## Cable_SCH
|  | Inverter Power (MW) | 1.64
Losses
| Start | Finish | Number of inverter | P(MW) | Distance (mm) | Distance (m) | FLA (A) | Conductor construction | Cable length (10% margin) | Cable size (mm2) | Type | Resistance (ohms/km) | P loss (kW) | P loss (%)
Feeder 1 | PCU1 | PCU2 | 3 | 4.92 | 13 | 300 | 86.0777 | 3C | 0.33 | 120 | Al | 0.325 | 2.384 | 0.04845%
| PCU2 | PCU3 | 6 | 9.84 | 12 | 300 | 172.1554 | 3C | 0.33 | 120 | Al | 0.325 | 9.5359 | 0.09691%
| PCU3 | PCU4 | 9 | 14.76 | 13 | 500 | 258.233 | 3C | 0.55 | 240 | Al | 0.161 | 17.7147 | 0.12%
| PCU4 | Sub | 9 | 14.76 | 130 | 900 | 258.233 | 3C | 0.99 | 500 | Al | 0.0815 | 16.1413 | 0.1094%
[9 empty] | 2.2 |  |  |  | 45.7758 | 0.3101%
Feeder 2 | PCU5 | PCU6 | 3 | 4.92 | 13 | 300 | 86.0777 | 3C | 0.33 | 120 | Al | 0.325 | 2.384 | 0.04845%
| PCU6 | PCU7 | 6 | 9.84 | 17 | 300 | 172.1554 | 3C | 0.33 | 120 | Al | 0.325 | 9.5359 | 0.09691%
| PCU7 | PCU8 | 9 | 14.76 | 35 | 300 | 258.233 | 3C | 0.33 | 185 | Al | 0.211 | 13.9297 | 0.09437%
| PCU8 | Sub | 9 | 14.76 | 60 | 1000 | 258.233 | 3C | 1.1 | 500 | Al | 0.0815 | 17.9347 | 0.1215%
[9 empty] | 2.09 |  |  |  | 43.7842 | 0.2966%
Feeder 3 | PCU9 | PCU10 | 3 | 4.92 | 19 | 300 | 86.0777 | 3C | 0.33 | 120 | Al | 0.325 | 2.384 | 0.04845%
| PCU10 | PCU11 | 6 | 9.84 | 12 | 300 | 172.1554 | 3C | 0.33 | 120 | Al | 0.325 | 9.5359 | 0.09691%
| PCU11 | PCU12 | 9 | 14.76 | 13 | 300 | 258.233 | 3C | 0.33 | 185 | Al | 0.211 | 13.9297 | 0.09437%
| PCU12 | Sub | 9 | 14.76 | 100 | 1000 | 258.233 | 3C | 1.1 | 500 | Al | 0.0815 | 17.9347 | 0.1215%
[9 empty] | 2.09 |  |  |  | 43.7842 | 0.2966%
Feeder 4 | PCU12 | PCU13 | 3 | 4.92 | 12 | 300 | 86.0777 | 3C | 0.33 | 120 | Al | 0.325 | 2.384 | 0.04845%
| PCU14 | PCU15 | 6 | 9.84 | 14 | 300 | 172.1554 | 3C | 0.33 | 120 | Al | 0.325 | 9.5359 | 0.09691%
| PCU15 | Sub | 6 | 9.84 | 25 | 1100 | 172.1554 | 3C | 1.21 | 500 | Al | 0.0815 | 8.7681 | 0.08911%
[9 empty] | 1.87 |  |  |  | 20.6879 | 0.2102%
Feeder 5 | PCU16 | PCU17 | 3 | 4.92 | 90 | 380 | 86.0777 | 3C | 0.418 | 120 | Al | 0.325 | 3.0197 | 0.06138%
| PCU17 | PCU18 | 6 | 9.84 | 25 | 380 | 172.1554 | 3C | 0.418 | 185 | Al | 0.211 | 7.8419 | 0.07969%
| PCU18 | Sub | 6 | 9.84 | 75 | 1200 | 172.1554 | 3C | 1.32 | 500 | Al | 0.0815 | 9.5652 | 0.09721%
[9 empty] | 2.156 |  |  |  | 20.4268 | 0.2076%
Outgoing Feeder | Sub | Tx |  | 88.56 |  | 50 | 1549.3982 | 6 x 3C | 0.055 | 630 | Al | 0.056 | 22.1819 | 0.02505%
[11 empty] | losses (kW) |  | 196.6408
[11 empty] | Total Power (MWac) |  | 88.56
[11 empty] | losses (%) |  | 0.222%
Conductor AC resistance @ 50Hz and 90°C
|  | Amp | Ω/km |  | size | length |  | termination
| 50 | 159 | 0.821 |  | 95 | 0 |  | 95 | 0
| 70 | 194 | 0.568 |  | 120 | 3.058 |  | 120 | 18
| 95 | 232 | 0.41 |  | 150 | 0 |  | 150 | 0
| 120 | 264 | 0.325 |  | 185 | 1.078 |  | 185 | 6
| 150 | 295 | 0.264 |  | 240 | 0.55 |  | 240 | 2
| 185 | 334 | 0.211 |  | 300 | 0 |  | 300 | 0
| 240 | 388 | 0.161 |  | 400 | 0 |  | 400 | 0
| 300 | 438 | 0.13 |  | 500 | 5.72 |  | 500 | 10
| 400 | 502 | 0.102 |  | 630 | 0 |  | 630 | 12
| 500 | 570 | 0.0815 |  |  | 10.406
| 630 | 622 | 0.056
[5 empty] | F1 | F2 | F3 | F4 | F5 | F6 | F7
|  |  |  | Trench 1 | 310 |  | 457 |  | 1551 | 1078 | 718 | 4114
|  |  |  | Trench 2 | F1: 1061; F3: 816; F6: 100 | 1977
|  |  |  | Trench 3 | F3: 130 | 130
[5 empty] | 1371 | 1061 | 1403 | 946 | 1681 | 1178 | 818 | 8458

## 33kV Cable Data
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35
19/33kV Three Core Ind. Screened & PVC Sheathed
Cu
Nominal Conductor area | Nominal Conductor Diameter | Nominal Insulation Thickness | Nominal Diameter Over Insulation | Nominal Screen Area | Number and nominal diameter of screen wires on each core | Nominal diameter over wire screen | Nominal overall diameter | Approximate mass | Product Code | [6 empty] | Fault Current Carrying Capacity for 1 second |  |  | Max pulling Tension | Min. Bending Radius During Pulling | Min. Bending Radius Set in Position | Nominal duct diameter |  | Maximum Conductor DC resistance @ 20oC | Conductor AC resistance @ 50Hz and 90oC | Inductive reactance at 50Hz | Insulation resistance at 20oC | Conductor to Screen Capacitance | Charging current per phase | Dielectric loos per phase | Maximum dielectric stress | DC resistance of screens @ 20oC | Zero Sequence resistance @ 20oC | Zero seq. react @ 50Hz
mm2 | mm | mm | mm | mm2 | No/mm | mm | mm | kg/100m |  |  | A | A | A | A | A | Cond kA | Screen kA |  | kN | mm | mm | mm |  | Ω/km | Ω/km | Ω/km | MΩ.km | μF/km | A/km | W/km | kV/mm | Ω/km | Ω/km | Ω/km
50 | 8 | 8 | 25.5 | 49.4 | 29/0.85 | 28.8 | 69.4 | 460 |  |  | 204 | 217 | 156 | 205 | 170 | 7.15 | 7.32 |  | 11 | 1250 | 830 | 100 |  | 0.387 | 0.494 | 0.147 | 18000 | 0.133 | 0.796 | 60.5 | 4.05 | 0.366 | 1.49 | 0.0988
70 | 9.6 | 8 | 27.1 | 68.1 | 40/0.85 | 30.4 | 73 | 560 |  |  | 252 | 269 | 198 | 250 | 213 | 10 | 10.1 |  | 15 | 1310 | 880 | 125 |  | 0.268 | 0.342 | 0.139 | 16000 | 0.148 | 0.883 | 67.1 | 3.82 | 0.265 | 1.06 | 0.0909
95 | 11.5 | 8 | 29 | 68.1 | 40/0.85 | 32.3 | 77.3 | 665 |  |  | 306 | 328 | 238 | 299 | 255 | 13.6 | 10.1 |  | 20 | 1390 | 930 | 125 |  | 0.193 | 0.247 | 0.128 | 15000 | 0.165 | 0.984 | 74.8 | 3.61 | 0.265 | 0.989 | 0.0807
120 | 13.1 | 8 | 30.6 | 68.1 | 40/0.85 | 33.9 | 81.1 | 765 |  |  | 352 | 377 | 271 | 341 | 290 | 17.1 | 10.1 |  | 25 | 1460 | 970 | 125 |  | 0.153 | 0.196 | 0.123 | 14000 | 0.179 | 1.07 | 81.1 | 3.48 | 0.265 | 0.949 | 0.0757
150 | 14.5 | 8 | 32 | 68.1 | 40/0.85 | 35.5 | 84.8 | 875 |  |  | 397 | 427 | 304 | 381 | 324 | 21.4 | 10.1 |  | 32 | 1530 | 1020 | 125 |  | 0.124 | 0.159 | 0.12 | 13000 | 0.191 | 1.14 | 86.8 | 3.38 | 0.266 | 0.922 | 0.0722
185 | 16.1 | 8 | 33.6 | 68.1 | 40/0.85 | 37.1 | 88.4 | 990 |  |  | 454 | 488 | 345 | 431 | 366 | 26.4 | 10.1 |  | 39 | 1590 | 1060 | 150 |  | 0.0991 | 0.128 | 0.116 | 12000 | 0.205 | 1.23 | 93.2 | 3.29 | 0.266 | 0.897 | 0.0685
240 | 18.5 | 8 | 36 | 68.1 | 40/0.85 | 39.5 | 94.1 | 1190 |  |  | 533 | 575 | 402 | 499 | 424 | 34.3 | 10.1 |  | 50 | 1690 | 1130 | 150 |  | 0.0754 | 0.0978 | 0.111 | 11000 | 0.227 | 1.35 | 103 | 3.17 | 0.265 | 0.872 | 0.0637
300 | 20.7 | 8 | 38.4 | 68.1 | 40/0.85 | 41.9 | 99.4 | 1410 |  |  | 609 | 658 | 456 | 563 | 478 | 42.9 | 10.1 |  | 63 | 1790 | 1190 | 150 |  | 0.0601 | 0.0788 | 0.107 | 9800 | 0.247 | 1.48 | 112 | 3.09 | 0.266 | 0.858 | 0.0605
400 | 23.6 | 8 | 41.3 | 68.1 | 40/0.85 | 44.8 | 106.2 | 1730 |  |  | 701 | 759 | 542 | 630 | 562 | 57.2 | 10.1 |  | 84 | 1910 | 1270 | 200 |  | 0.047 | 0.0628 | 0.102 | 8900 | 0.272 | 1.62 | 123 | 3 | 0.266 | 0.845 | 0.0557
500 | 26.5 | 8 | 44.2 | 68.1 | 40/0.85 | 47.7 | 112.9 | 2070 |  |  | 797 | 864 | 610 | 718 | 630 | 71.5 | 10.1 |  | 105 | 2030 | 1350 | 200 |  | 0.0373 | 0.0513 | 0.099 | 8100 | 0.297 | 1.77 | 135 | 2.93 | 0.265 | 0.835 | 0.0524
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45
19/33kV Single Core Ind. Screened & PVC Sheathed
Cu
Nominal Conductor area | Nominal Conductor Diameter | Nominal Insulation Thickness | Nominal Diameter Over Insulation | Nominal Screen Area on Each Core | Number and nominal diameter of screen wires | Nominal diameter over over wire screen | Nominal overall diameter | Approximate mass | Product Code | Max pulling Tension | Min. Bending Radius During Pulling | Min. Bending Radius Set in Position | Nominal duct diameter | Nominal duct diameter | [13 empty] | Fault Current Carrying Capacity for 1 second |  |  | Maximum Conductor DC resistance @ 20oC | Conductor AC resistance @ 50Hz & 90oC Trefoil or Flat Touching | Conductor AC resistance @ 50Hz & 90oC Flat Spaced | Inductive reactance at 50Hz & 90oC Trefoil | Inductive reactance at 50Hz & 90oC Flat Touching | Inductive reactance at 50Hz & 90oC Flat Spaced | Insulation resistance at 20oC | Conductor to Screen Capacitance | Charging current per phase | Dielectric loos per phase | Maximum dielectric stress | DC resistance of screens @ 20oC | Zero Sequence resistance @ 20oC | Zero seq. react @ 50Hz
mm2 | mm | mm | mm | mm2 | No/mm | mm | mm | kg/100m |  | kN | mm | mm | mm | mm |  | A | A | A | A | A | A | A | A | A | A | A | A | Cond kA | Screen kA |  | Ω/km | Ω/km | Ω/km | Ω/km | Ω/km | Ω/km | MΩ.km | μF/km | A/km | W/km | kV/mm | Ω/km | Ω/km | Ω/km
50 | 8 | 8 | 25.5 | 48.7 | 34/1.35 | 29.8 | 34.3 | 170 |  | 3.5 | 620 | 410 | 63 | 100 |  | 224 | 250 | 210 | 221 | 160 | 208 | 209 | 205 | 187 | 186 | 185 | 174 | 7.15 | 7.22 |  | 0.387 | 0.494 | 0.494 | 0.163 | 0.178 | 0.224 | 18000 | 0.133 | 0.796 | 60.5 | 4.05 | 0.372 | 0.759 | 0.0999
70 | 9.6 | 8 | 27.1 | 68.7 | 48/1.35 | 31.4 | 36.1 | 215 |  | 4.9 | 650 | 430 | 63 | 100 |  | 276 | 306 | 259 | 273 | 202 | 251 | 249 | 249 | 223 | 219 | 223 | 216 | 10 | 10.1 |  | 0.268 | 0.342 | 0.342 | 0.154 | 0.169 | 0.215 | 16000 | 0.148 | 0.883 | 67.1 | 3.82 | 0.263 | 0.531 | 0.0919
95 | 11.5 | 8 | 29 | 68.7 | 48/1.35 | 33.3 | 38 | 245 |  | 6.7 | 680 | 460 | 65 | 150 |  | 333 | 369 | 315 | 332 | 242 | 297 | 292 | 297 | 265 | 258 | 267 | 258 | 13.6 | 10.1 |  | 0.193 | 0.247 | 0.247 | 0.143 | 0.158 | 0.204 | 15000 | 0.165 | 0.984 | 74.8 | 3.61 | 0.263 | 0.457 | 0.0817
120 | 13.1 | 8 | 30.6 | 68.7 | 48/1.35 | 34.9 | 39.8 | 280 |  | 8.4 | 720 | 480 | 65 | 150 |  | 381 | 420 | 361 | 381 | 276 | 335 | 327 | 336 | 296 | 287 | 300 | 292 | 17.1 | 10.2 |  | 0.153 | 0.195 | 0.195 | 0.137 | 0.153 | 0.198 | 14000 | 0.179 | 1.07 | 81.1 | 3.48 | 0.263 | 0.416 | 0.0767
150 | 14.5 | 8 | 32 | 68.7 | 48/1.35 | 36.5 | 41.4 | 310 |  | 11 | 750 | 500 | 65 | 150 |  | 429 | 469 | 407 | 430 | 308 | 372 | 359 | 375 | 327 | 313 | 333 | 325 | 21.4 | 10.2 |  | 0.124 | 0.159 | 0.159 | 0.133 | 0.148 | 0.194 | 13000 | 0.191 | 1.14 | 86.8 | 3.38 | 0.264 | 0.389 | 0.0731
185 | 16.1 | 8 | 33.6 | 68.7 | 48/1.35 | 38.1 | 43.2 | 345 |  | 13 | 780 | 520 | 65 | 150 |  | 485 | 527 | 463 | 490 | 348 | 414 | 397 | 421 | 362 | 343 | 372 | 366 | 26.4 | 10.2 |  | 0.0991 | 0.127 | 0.127 | 0.129 | 0.144 | 0.19 | 12000 | 0.205 | 1.23 | 93.2 | 3.29 | 0.264 | 0.364 | 0.0693
240 | 18.5 | 8 | 36 | 68.7 | 48/1.35 | 40.5 | 45.9 | 410 |  | 17 | 830 | 550 | 65 | 150 |  | 563 | 605 | 542 | 574 | 402 | 471 | 444 | 485 | 408 | 382 | 425 | 420 | 34.4 | 10.2 |  | 0.0754 | 0.0976 | 0.0972 | 0.124 | 0.139 | 0.185 | 11000 | 0.227 | 1.35 | 103 | 3.17 | 0.263 | 0.34 | 0.0645
300 | 20.7 | 8 | 38.4 | 68.7 | 48/1.35 | 42.9 | 48.4 | 475 |  | 21 | 870 | 580 | 80 | 150 |  | 634 | 674 | 616 | 653 | 452 | 521 | 485 | 542 | 446 | 413 | 471 | 469 | 42.9 | 10.2 |  | 0.0601 | 0.0786 | 0.0779 | 0.12 | 0.135 | 0.181 | 9800 | 0.247 | 1.48 | 112 | 3.09 | 0.264 | 0.325 | 0.0612
400 | 23.6 | 8 | 41.3 | 68.7 | 48/1.35 | 45.8 | 51.5 | 575 |  | 28 | 930 | 620 | 80 | 150 |  | 719 | 756 | 706 | 750 | 533 | 579 | 531 | 610 | 492 | 449 | 526 | 547 | 57.2 | 10.2 |  | 0.047 | 0.0625 | 0.0616 | 0.115 | 0.13 | 0.176 | 8900 | 0.272 | 1.62 | 123 | 3 | 0.263 | 0.312 | 0.0564
500 | 26.5 | 8 | 44.2 | 68.7 | 48/1.35 | 48.7 | 54.9 | 685 |  | 35 | 990 | 660 | 80 | 200 |  | 807 | 837 | 803 | 854 | 600 | 637 | 574 | 682 | 539 | 484 | 585 | 611 | 71.5 | 10.2 |  | 0.0366 | 0.0499 | 0.0487 | 0.111 | 0.126 | 0.172 | 8100 | 0.297 | 1.77 | 135 | 2.93 | 0.263 | 0.302 | 0.0531
630 | 29.9 | 8 | 47.9 | 68.7 | 48/1.35 | 52.4 | 58.8 | 815 |  | 44 | 1060 | 710 | 100 | 200 |  | 902 | 924 | 911 | 969 | 672 | 697 | 619 | 759 | 576 | 513 | 635 | 680 | 90 | 10.2 |  | 0.0283 | 0.0403 | 0.0387 | 0.108 | 0.123 | 0.169 | 7300 | 0.329 | 1.96 | 149 | 2.86 | 0.263 | 0.294 | 0.0504
800 | 35.9 | 8 | 54 | 68.7 | 48/1.35 | 58.5 | 65.3 | 1020 |  | 56 | 1180 | 780 | 100 | 200 |  | 1012 | 1026 | 1036 | 1103 | 748 | 756 | 664 | 838 | 630 | 552 | 705 | 748 | 114 | 10.2 |  | 0.0221 | 0.0336 | 0.0315 | 0.102 | 0.117 | 0.163 | 6300 | 0.381 | 2.27 | 173 | 2.78 | 0.263 | 0.289 | 0.0452
1000 | 40.2 | 8 | 59.5 | 68.7 | 48/1.35 | 64 | 71 | 1220 |  | 70 | 1280 | 850 | 125 | 200 |  | 1160 | 1131 | 1219 | 1300 | 888 | 845 | 713 | 966 | 661 | 578 | 749 | 880 | 143 | 10.2 |  | 0.0182 | 0.0245 | 0.024 | 0.1 | 0.115 | 0.161 | 5600 | 0.427 | 2.55 | 194 | 2.72 | 0.263 | 0.282 | 0.0441
1200 | 43.8 | 8 | 63.5 | 68.7 | 48/1.35 | 68 | 75.2 | 1420 |  | 84 | 1350 | 900 | 125 | 200 |  | 1252 | 1204 | 1337 | 1426 | 963 | 896 | 745 | 1043 | 698 | 603 | 801 | 948 | 171 | 10.2 |  | 0.015 | 0.0207 | 0.0201 | 0.0984 | 0.114 | 0.159 | 5200 | 0.461 | 2.75 | 209 | 2.68 | 0.263 | 0.279 | 0.0426
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35
19/33kV Three Core Ind. Screened & PVC Sheathed
Al
Nominal Conductor area | Nominal Conductor Diameter | Nominal insulation thickness | Nominal diameter over insulation | Nominal screen area | Number and nominal diameter of screen wires on each core | Nominal diameter over wire screen | Nominal overall diameter | Approximate mass | Product Code | [6 empty] | Fault Current Carrying Capacity for 1 second |  |  | Max pulling Tension | Min. Bending Radius During Pulling | Min. Bending Radius Set in Position | Nominal duct diameter |  | Maximum Conductor DC resistance @ 20oC | Conductor AC resistance @ 50Hz and 90oC | Inductive reactance at 50Hz | Insulation resistance at 20oC | Conductor to Screen Capacitance | Charging current per phase | Dielectric loos per phase | Maximum dielectric stress | DC resistance of screens @ 20oC | Zero Sequence resistance @ 20oC | Zero seq. react @ 50Hz
mm2 | mm | mm | mm | mm2 | No/mm | mm | mm | kg/100m |  |  | A | A | A | A | A | Cond kA | Screen kA |  | kN | mm | mm | mm |  | Ω/km | Ω/km | Ω/km | MΩ.km | μF/km | A/km | W/km | kV/mm | Ω/km | Ω/km | Ω/km
50 | 8.1 | 8 | 25.6 | 32.3 | 19/0.85 | 28.9 | 69.5 | 355 |  |  | 158 | 168 | 121 | 159 | 132 | 4.73 | 4.8 |  | 7.5 | 1250 | 830 | 100 |  | 0.641 | 0.821 | 0.147 | 18000 | 0.134 | 0.798 | 60.7 | 4.04 | 0.559 | 2.32 | 0.0985
70 | 9.6 | 8 | 27.2 | 46 | 27/0.85 | 30.5 | 73.1 | 415 |  |  | 196 | 209 | 153 | 194 | 165 | 6.62 | 6.82 |  | 11 | 1320 | 880 | 125 |  | 0.443 | 0.568 | 0.136 | 16000 | 0.148 | 0.885 | 67.3 | 3.81 | 0.392 | 1.62 | 0.0879
95 | 11.4 | 8 | 28.9 | 61.3 | 36/0.85 | 32.2 | 77 | 480 |  |  | 237 | 254 | 184 | 232 | 197 | 8.99 | 9.09 |  | 14 | 1390 | 920 | 125 |  | 0.32 | 0.41 | 0.129 | 15000 | 0.164 | 0.977 | 74.3 | 3.62 | 0.294 | 1.2 | 0.0812
120 | 12.8 | 8 | 30.3 | 68.1 | 40/0.85 | 33.6 | 80.2 | 525 |  |  | 272 | 292 | 210 | 264 | 224 | 11.4 | 10.1 |  | 18 | 1440 | 960 | 125 |  | 0.253 | 0.325 | 0.124 | 14000 | 0.176 | 1.05 | 79.9 | 3.5 | 0.265 | 1.05 | 0.0766
150 | 14.2 | 8 | 31.7 | 68.1 | 40/0.85 | 35.2 | 83.9 | 580 |  |  | 307 | 330 | 236 | 295 | 251 | 14.2 | 10.1 |  | 23 | 1510 | 1010 | 125 |  | 0.206 | 0.264 | 0.12 | 13000 | 0.189 | 1.13 | 85.5 | 3.4 | 0.265 | 1 | 0.0731
185 | 15.7 | 8 | 33.2 | 68.1 | 40/0.85 | 36.7 | 87.3 | 635 |  |  | 351 | 378 | 268 | 334 | 284 | 17.5 | 10.1 |  | 28 | 1570 | 1050 | 125 |  | 0.164 | 0.211 | 0.117 | 12000 | 0.202 | 1.2 | 91.5 | 3.31 | 0.265 | 0.961 | 0.0694
240 | 18 | 8 | 35.5 | 68.1 | 40/0.85 | 39 | 92.9 | 730 |  |  | 413 | 445 | 312 | 388 | 330 | 22.7 | 10.1 |  | 36 | 1670 | 1110 | 150 |  | 0.125 | 0.161 | 0.112 | 11000 | 0.222 | 1.32 | 101 | 3.2 | 0.265 | 0.923 | 0.0647
300 | 20.1 | 8 | 37.8 | 68.1 | 40/0.85 | 41.3 | 98.1 | 820 |  |  | 472 | 509 | 354 | 438 | 372 | 28.4 | 10.1 |  | 45 | 1770 | 1180 | 150 |  | 0.1 | 0.13 | 0.108 | 10000 | 0.242 | 1.44 | 110 | 3.11 | 0.265 | 0.897 | 0.0614
400 | 23 | 8 | 40.7 | 68.1 | 40/0.85 | 44.2 | 104.8 | 955 |  |  | 548 | 593 | 424 | 502 | 440 | 37.8 | 10.1 |  | 60 | 1890 | 1260 | 200 |  | 0.0778 | 0.102 | 0.103 | 9100 | 0.267 | 1.59 | 121 | 3.02 | 0.265 | 0.874 | 0.0565
500 | 26.5 | 8 | 44.2 | 68.1 | 40/0.85 | 47.7 | 112.9 | 1120 |  |  | 632 | 686 | 484 | 570 | 499 | 47.3 | 10.1 |  | 75 | 2030 | 1350 | 200 |  | 0.0617 | 0.0815 | 0.099 | 8100 | 0.297 | 1.77 | 135 | 2.93 | 0.265 | 0.858 | 0.0524
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45
19/33kV Single Core Ind. Screened & PVC Sheathed
Al
Nominal Conductor area | Nominal Conductor Diameter | Nominal Insulation Thickness | Nominal Diameter Over Insulation | Nominal Screen Area on Each Core | Number and nominal diameter of screen wires | Nominal diameter over over wire screen | Nominal overall diameter | Approximate mass | Product Code | Max pulling Tension | Min. Bending Radius During Pulling | Min. Bending Radius Set in Position | Nominal duct diameter | Nominal duct diameter | [13 empty] | Fault Current Carrying Capacity for 1 second |  |  | Maximum Conductor DC resistance @ 20oC | Conductor AC resistance @ 50Hz & 90oC Trefoil or Flat Touching | Conductor AC resistance @ 50Hz & 90oC Flat Spaced | Inductive reactance at 50Hz & 90oC Trefoil | Inductive reactance at 50Hz & 90oC Flat Touching | Inductive reactance at 50Hz & 90oC Flat Spaced | Insulation resistance at 20oC | Conductor to Screen Capacitance | Charging current per phase | Dielectric loos per phase | Maximum dielectric stress | Screen DC resistance @ 20oC | Zero Sequence resistance @ 20oC | Zero seq. react @ 50Hz
mm2 | mm | mm | mm | mm2 | No/mm | mm | mm | kg/100m |  | kN | mm | mm | mm | mm |  | A | A | A | A | A | A | A | A | A | A | A | A | Cond kA | Screen kA |  | Ω/km | Ω/km | Ω/km | Ω/km | Ω/km | Ω/km | MΩ.km | μF/km | A/km | W/km | kV/mm | Ω/km | Ω/km | Ω/km
50 | 8.1 | 8 | 25.6 | 32.9 | 23/1.35 | 29.9 | 34.4 | 125 |  | 2.5 | 620 | 410 | 63 | 100 |  | 175 | 197 | 163 | 172 | 125 | 162 | 164 | 159 | 147 | 148 | 145 | 135 | 4.73 | 4.88 |  | 0.641 | 0.821 | 0.821 | 0.163 | 0.178 | 0.223 | 18000 | 0.134 | 0.798 | 60.7 | 4.04 | 0.55 | 1.19 | 0.0997
70 | 9.6 | 8 | 27.2 | 45.8 | 32/1.35 | 31.5 | 36.2 | 150 |  | 3.5 | 650 | 430 | 63 | 100 |  | 217 | 243 | 202 | 213 | 158 | 198 | 199 | 194 | 178 | 178 | 175 | 169 | 6.62 | 6.79 |  | 0.443 | 0.568 | 0.568 | 0.151 | 0.166 | 0.212 | 16000 | 0.148 | 0.885 | 67.3 | 3.81 | 0.394 | 0.838 | 0.089
95 | 11.4 | 8 | 28.9 | 61.5 | 43/1.35 | 33.2 | 37.9 | 180 |  | 4.8 | 680 | 450 | 63 | 150 |  | 262 | 292 | 245 | 258 | 189 | 234 | 234 | 232 | 209 | 207 | 208 | 201 | 8.99 | 9.13 |  | 0.32 | 0.41 | 0.41 | 0.143 | 0.159 | 0.204 | 15000 | 0.164 | 0.977 | 74.3 | 3.62 | 0.294 | 0.613 | 0.0822
120 | 12.8 | 8 | 30.3 | 68.7 | 48/1.35 | 34.6 | 39.5 | 200 |  | 6 | 710 | 470 | 65 | 150 |  | 299 | 332 | 281 | 296 | 215 | 264 | 262 | 262 | 237 | 233 | 237 | 228 | 11.4 | 10.2 |  | 0.253 | 0.325 | 0.325 | 0.138 | 0.154 | 0.199 | 14000 | 0.176 | 1.05 | 79.9 | 3.5 | 0.263 | 0.516 | 0.0776
150 | 14.2 | 8 | 31.7 | 68.7 | 48/1.35 | 36.2 | 41.1 | 215 |  | 7.5 | 740 | 490 | 65 | 150 |  | 337 | 374 | 317 | 335 | 241 | 294 | 290 | 293 | 263 | 257 | 264 | 254 | 14.2 | 10.2 |  | 0.206 | 0.264 | 0.264 | 0.134 | 0.149 | 0.195 | 13000 | 0.189 | 1.13 | 85.5 | 3.4 | 0.263 | 0.47 | 0.074
185 | 15.7 | 8 | 33.2 | 68.7 | 48/1.35 | 37.7 | 42.8 | 230 |  | 9.3 | 770 | 510 | 65 | 150 |  | 383 | 422 | 362 | 382 | 272 | 330 | 323 | 330 | 293 | 285 | 296 | 287 | 17.5 | 10.2 |  | 0.164 | 0.211 | 0.211 | 0.13 | 0.145 | 0.191 | 12000 | 0.202 | 1.2 | 91.5 | 3.31 | 0.263 | 0.428 | 0.0703
240 | 18 | 8 | 35.5 | 68.7 | 48/1.35 | 40 | 45.1 | 255 |  | 12 | 810 | 540 | 65 | 150 |  | 448 | 491 | 425 | 450 | 316 | 378 | 366 | 382 | 334 | 321 | 340 | 331 | 22.7 | 10.2 |  | 0.125 | 0.161 | 0.161 | 0.125 | 0.14 | 0.186 | 11000 | 0.222 | 1.32 | 101 | 3.2 | 0.263 | 0.388 | 0.0655
300 | 20.1 | 8 | 37.8 | 68.7 | 48/1.35 | 42.3 | 47.8 | 285 |  | 15 | 860 | 570 | 80 | 150 |  | 508 | 551 | 484 | 513 | 357 | 421 | 404 | 428 | 370 | 352 | 381 | 371 | 28.4 | 10.2 |  | 0.1 | 0.129 | 0.129 | 0.121 | 0.136 | 0.182 | 10000 | 0.242 | 1.44 | 110 | 3.11 | 0.263 | 0.364 | 0.0622
400 | 23 | 8 | 40.7 | 68.7 | 48/1.35 | 45.2 | 50.9 | 320 |  | 20 | 920 | 610 | 80 | 150 |  | 584 | 628 | 561 | 595 | 425 | 475 | 449 | 487 | 414 | 389 | 430 | 437 | 37.8 | 10.2 |  | 0.0778 | 0.101 | 0.101 | 0.116 | 0.131 | 0.177 | 9100 | 0.267 | 1.59 | 121 | 3.02 | 0.263 | 0.342 | 0.0573
500 | 26.5 | 8 | 44.2 | 68.7 | 48/1.35 | 48.7 | 54.6 | 370 |  | 25 | 980 | 660 | 80 | 200 |  | 671 | 714 | 651 | 691 | 487 | 533 | 497 | 554 | 462 | 428 | 486 | 497 | 47.3 | 10.2 |  | 0.0605 | 0.0797 | 0.0789 | 0.111 | 0.126 | 0.172 | 8100 | 0.297 | 1.77 | 135 | 2.93 | 0.263 | 0.325 | 0.0531
630 | 29.9 | 8 | 48 | 68.7 | 48/1.35 | 52.5 | 58.6 | 430 |  | 32 | 1050 | 700 | 100 | 200 |  | 764 | 802 | 748 | 795 | 553 | 593 | 545 | 625 | 507 | 464 | 541 | 560 | 59.6 | 10.2 |  | 0.0469 | 0.0629 | 0.0618 | 0.108 | 0.123 | 0.168 | 7300 | 0.329 | 1.96 | 149 | 2.86 | 0.263 | 0.312 | 0.0504
800 | 34.2 | 8 | 52.3 | 68.7 | 48/1.35 | 56.8 | 63.4 | 500 |  | 40 | 1140 | 760 | 100 | 200 |  | 862 | 895 | 855 | 910 | 623 | 654 | 591 | 699 | 556 | 501 | 602 | 625 | 75.7 | 10.2 |  | 0.0367 | 0.0507 | 0.0492 | 0.104 | 0.119 | 0.165 | 6600 | 0.366 | 2.19 | 166 | 2.8 | 0.263 | 0.301 | 0.047
1000 | 40.2 | 8 | 59.5 | 68.7 | 48/1.35 | 64 | 70.8 | 600 |  | 50 | 1270 | 850 | 100 | 200 |  | 997 | 1007 | 1006 | 1072 | 736 | 733 | 644 | 801 | 619 | 546 | 681 | 730 | 94.6 | 10.2 |  | 0.0298 | 0.039 | 0.0387 | 0.1 | 0.115 | 0.161 | 5600 | 0.427 | 2.55 | 194 | 2.72 | 0.263 | 0.293 | 0.0441
1200 | 43.8 | 8 | 63.5 | 68.7 | 48/1.35 | 68 | 75 | 680 |  | 60 | 1350 | 900 | 125 | 200 |  | 1089 | 1085 | 1113 | 1187 | 805 | 786 | 681 | 873 | 639 | 565 | 710 | 794 | 114 | 10.2 |  | 0.0247 | 0.0327 | 0.0323 | 0.0981 | 0.113 | 0.159 | 5200 | 0.461 | 2.75 | 209 | 2.68 | 0.263 | 0.289 | 0.0426