## ChangeLog
# | Date | Change | Description
1 | 2022-03-23 | Adop from Summerville Project | Original version for Lancaster SF
2 | 2022-03-24 | Update to version 0a | Update the setpoint tab: Separate General, PSSE specific and PSCAD specific sections
3 | 2022-03-30 | Update to version 1 | Include more setpoints in the Setpoints Tab
4 | 2022-04-04 | Update to version 2 | Update the setpoint tab and scenarios back to GLW typical

## SimulationSettings
ParamIdentifier | Value | unit
Batches | test1
Name of test run | script_upgrade
model(s) for PSSE network studies | LowLoad | folder name and path relative to relative to PSSE_sim\base_model | HighLoad, LowLoad
PSSE start offset | 0 | seconds
default_sim_duration PSSE | 15
default_sim_duration PSCAD | 15
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: define which test batches should be included in next test run
Note on A3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: name of test run used for labelling the output files
Note on A4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: list of folder names of one or more network cases, used in Network fault studies and voltge control studies carried out on the wider network in PSS/E.
Note on A5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: provide a negative number to delay the PSSE simulation [second]

## ProjectDetails
HighLevelParamName | ParamIdentifier | Value
Project Name | Name | Horsham Solar Farm
Project Name short | NameShrt | HORSFBESS
Developer | Dev | OX2 Australia
Abbreviation | Abbr
Type of Test | Type
Town | Town | Horsham
State | State | Victoria
Lot/DP | lot_dp | Multiple Lots
Address | addrs | Horsham-Lubeck Road, Riverside, VIC 3401
LGA | lga | Horsham Rural City Council
Network Service Provider | NSP | AEMO
POC Substation | Sub | Horsham Terminal Station
Connection type | contyp | direct
POC Feeder | poc_fdr | N/A
POC circuit | CCT | Horsham 220 kV
Short Circuit Ratios | SCRHigh
SCRLow
| SCRMVA | 119
Total Plant MW at POC | PlantMW | 119
Total Plant MW at terminals | GenMW | 121
Maximum Plant MVAr at terminals | GenMVArMax | 90.72
Minimum Plant MVAr at terminal | GenMVArMin | -90.72
Total Plant Maximum MVA at POC (base for per-unitisation) | TotalMVA | 119
Nominal POC voltage (kV) | VPOCkv | 220 | VLL | VLN
Normal POC voltage (p.u.) | VPOCpu | 1.03 | 226.6 | 130.8276
Nominal voltage at Bus where test source is connected (optional) | VbaseTestSrc | 220
Normal frequency at POC | Fbase | 50
Inverter/Plant Model | plnt_mdl
Number of generator aggregates in model | Gens | 1
Generators Per Site | genPerSite1 | 36
genPerSite2
Generator MVA | genMVA1 | 151.2
genMVA2
Generator terminal voltage in kV | VTERkv | 0.63
VTERkv2
| NomMW1 | 118.8
NomMW2
Pmax | Pmax | 1
Pmax_at_Qmax | PmaxQmax | 1
Pmax_at_Qmin | PmaxQmin | 1
Pmin | Pmin | 0
Pmin_at_Qmax | PminQmax | 0
Pmin_at_Qmin | PminQmin | 0
Note on B26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Lancaster, the Qmax for half of SF only
Note on B31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is in case the GridSource for automated testing is connected at a different point than the POC. If this entry is left empty, VPOCpu is assumed.

## ModelDetailsPSCAD
ParamIdentifier | Value
workspace_folder_path |  | This sheet lists all relevant information about the project file and PSCAD-specific setup
workspace_folder_name
Workspace File Name | HOR_PV.pswx
Projects | 1
Project1 | HOR_PV
DllPath
result_path
default_sim_duration | 15
disturbance_offset | 5
max_processes | 8
pscad version | PSCAD 5.0.1 (x64)
compiler | Intel Fortran One API v2021
compiler_short | if18_x86
create example cases | no
GridSourceID | 1927070795
GridSourceCanvas (optional)
Fprofile | 45171500
Vprofile | 394750131
PHprofile | 541663597
StpBlockID | 163769877
StpBlockCanvas (optional)
Vstp_profile | 7352230
Qstp_profile | 1650106288
PFstp_profile | 1487257830
Pstp_profile | 43564542
P1stp_profile | 977647848
AUX_profile | 1599255413
FaultBlockID | 1591544161
FaultBlockCanvas (optional)
plotStep_us | 5000
Note on B7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: contains the path to the dll files that must be copied to the directory containing the compiled files. Expressed relative to the "PSCAD_sim" directory.
Note on B18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This one needs to reflect the ending of the folders auto-created by PSCAD during compilation
Note on A19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: determines wether the test script generates an example case for each test. This can be handy for debugging or sharing the cases with third parties. However, it also takes up disk space.
Note on A23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Inside the GridSourceCanvas
Note on A28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This normally remain the same with StpBlockID for the tests.

## ModelDetailsPSSE
ParamIdentifier | Value |  |  | ChanAdd | Bus | ID | Model | Type | Order | Label | Legend |  | deviation | ChanAdd | Bus | ID | Model | Type | Order | Label | Legend
PSSEversion | PSS/E v34.5 |  |  | 1 | 367176 | 1 | WAUX | VAR | 2 | PPC1_L2 | f_ref(L+2) | INV VAR | 2 | 0 | 367176 | 1 | WGEN | VAR | 0 | VAR 2 | Active power reference for voltage control
savFileName | HOR_v0_8.sav |  |  | 2 | 367176 | 1 | WAUX | VAR | 18 | PPC1_HVRT |  |  | 2 | 0 | 367176 | 1 | WGEN | VAR | 1 | VAR 3 | Active power reduction
dyrFileName | HOR_v0_8.dyr |  |  | 3 | 367176 | 1 | WAUX | STATE | 3 | PPC1_K3 | f_grid(K+3) |  | 2 | 0 | 367176 | 1 | WGEN | VAR | 2 | VAR 4 | Reactive power reference
dll1 | SMAHYCF_G13_349_IVF150.dll |  |  | 4 | 367176 | 1 | WGEN | VAR | 15 | INV1_L15 | VDdetection |  | 2 | 0 | 367176 | 1 | WGEN | VAR | 5 | VAR 7 | Voltage reference
dll2 | SMASC_G185_349_IVF150.dll |  |  | 5 | 367176 | 1 | WGEN | VAR | 27 | INV1_L27 | Trip signal |  | 2 | 0 | 367176 | 1 | WGEN | VAR | 7 | VAR 9 | P command
|  |  |  | 6 | 367176 | 1 | WGEN | VAR | 28 | INV1_L28 | Vol Flag (L+28) |  | 2 | 0 | 367176 | 1 | WGEN | VAR | 8 | VAR 10 | Q command
|  |  |  | 7 | 367176 | 1 | WGEN | VAR | 29 | INV1_L29 | Freq Flag (L+29) |  | 2 | 0 | 367176 | 1 | WGEN | VAR | 9 | VAR 11 | Id ref
|  |  |  | 8 | 367176 | 1 | WGEN | STATE | 0 | INV1_K0 | Pgrid_measured |  | 2 | 0 | 367176 | 1 | WGEN | VAR | 10 | VAR 12 | Iq ref
savFileHigh | 20210720-180037-SubTrans-SystemNormal.sav |  |  | 9 | 367176 | 1 | WGEN | STATE | 2 | INV1_K2 | Vgrid_measured |  | 2 | 0 | 367176 | 1 | WGEN | VAR | 15 | VAR 17 | Voltage Disturbance Detection
dyrFileHigh | [12 empty] | 2 | 0 | 367176 | 1 | WGEN | VAR | 28 | VAR 30 | Voltage Event Detection Flag
savFileLow | [12 empty] | 2 | 0 | 367176 | 1 | WGEN | VAR | 29 | VAR 31 | Frequency Event Detection Flag
dyrFileLow | [12 empty] | 2 | 0 | 367176 | 1 | WGEN | VAR | 46 | VAR 48 | Grid side Id
[13 empty] | 2 | 0 | 367176 | 1 | WGEN | VAR | 47 | VAR 49 | Grid side Iq
default_sim_duration | 15
start_offset | 0 | [10 empty] | INV STATE | 2 | 0 | 367176 | 1 | WGEN | STATE | 10 | STATE 12 | Active power setpoint filtered
[13 empty] | 2 | 0 | 367176 | 1 | WGEN | STATE | 11 | STATE 13 | Reactive power setpoint filtered
InfiniteBus | 1
FaultBus | 2 | [10 empty] | PPC VAR | 112 | 0
DummyTxBus | 10 | [11 empty] | 112 | 0 | 367176 | 1 | WAUX | VAR | 7 | VAR 119 | P flow1 (MW)
POC | 334081 | [11 empty] | 112 | 0 | 367176 | 1 | WAUX | VAR | 12 | VAR 124 | P PV available
Generator1 | 334095 | [11 empty] | 112 | 0 | 367176 | 1 | WAUX | VAR | 13 | VAR 125 | P reference unlimited
[13 empty] | 112 | 0 | 367176 | 1 | WAUX | VAR | 14 | VAR 126 | Memory active power change ramp limit
POCfromBus1 | 334081 | [11 empty] | 112 | 0 | 367176 | 1 | WAUX | VAR | 15 | VAR 127 | P reference P Control
POCtoBus1 | 334090 | [11 empty] | 112 | 0 | 367176 | 1 | WAUX | VAR | 16 | VAR 128 | P command
POCmeasBus1 | 334081 | [11 empty] | 112 | 0 | 367176 | 1 | WAUX | VAR | 17 | VAR 129 | Pred command
HVfromBus1 | 2 | INF bus | [10 empty] | 112 | 0 | 367176 | 1 | WAUX | VAR | 20 | VAR 132 | Q reference unlimited
HVtoBus1 | 1 | INF bus | [10 empty] | 112 | 0 | 367176 | 1 | WAUX | VAR | 21 | VAR 133 | Q reference Q Control
HVmeasBus1 | 1 | INF bus | [10 empty] | 112 | 0 | 367176 | 1 | WAUX | VAR | 22 | VAR 134 | Q command
MVfromBus1 | 334092 | [10 empty] | PPC STATE
MVtoBus1 | 334091
MVmeasBus1 | 334092 | [11 empty] | 54 | 0 | 367176 | 1 | WAUX | STATE | 0 | STATE 54 | Measured active power (Pgrid)
LVfromBus1 | 334094 | [11 empty] | 54 | 0 | 367176 | 1 | WAUX | STATE | 1 | STATE 55 | Measured reactive power (Qgrid)
LVtoBus1 | 334092 | [11 empty] | 54 | 0 | 367176 | 1 | WAUX | STATE | 2 | STATE 56 | Measured voltage (Vgrid)
LVmeasBus1 | 334094 | [11 empty] | 54 | 0 | 367176 | 1 | WAUX | STATE | 3 | STATE 57 | Measured frequency (Fgrid)
MVfromBus2 | 334093 | [11 empty] | 54 | 0 | 367176 | 1 | WAUX | STATE | 4 | STATE 58 | Pref filtered
MVtoBus2 | 334091 | [11 empty] | 54 | 0 | 367176 | 1 | WAUX | STATE | 5 | STATE 59 | Qref filtered
MVmeasBus2 | 334093 | [11 empty] | 54 | 0 | 367176 | 1 | WAUX | STATE | 6 | STATE 60 | Vref filtered
LVfromBus2 | 334095 | [11 empty] | 54 | 0 | 367176 | 1 | WAUX | STATE | 8 | STATE 62 | PvsF Setpoint Filter
LVtoBus2 | 334093 | [11 empty] | 54 | 0 | 367176 | 1 | WAUX | STATE | 9 | STATE 63 | Qmax filtered
LVmeasBus2 | 334095 | [11 empty] | 54 | 0 | 367176 | 1 | WAUX | STATE | 10 | STATE 64 | Qmin filtered
[13 empty] | 54 | 0 | 367176 | 1 | WAUX | STATE | 11 | STATE 65 | P control PI regulator
Vset1_bus | 334090 | [11 empty] | 54 | 0 | 367176 | 1 | WAUX | STATE | 12 | STATE 66 | Q control PI regulator
Vset1_mac | 1 | [11 empty] | 54 | 0 | 367176 | 1 | WAUX | STATE | 16 | STATE 70 | Qcmd command
Vset1_var | 16
Vset1_model | SMAHYCF13
Vset1_type | OTHER
Pset1_bus | 334090 | THIS SETPOINT IS THE COMBINED SETPOINT AND NOT TRUE PV SETPOINT. NEED TO ACCOUNT FOR THIS.
Pset1_mac | 1
Pset1_var | 18
Pset1_model | SMAHYCF13
Pset1_type | OTHER
Pprim1_bus | 334095
Pprim1_mac | 1
Pprim1_con | 0
Pprim1_model | SMASC185
Pprim1_type | GEN
Qset1_bus | 334090
Qset1_mac | 1
Qset1_var | 14
Qset1_model | SMAHYCF13
Qset1_type | OTHER
PFset1_bus | 334090
PFset1_mac | 1
PFset1_var | 15
PFset1_model | SMAHYCF13
PFset1_type | OTHER
Plot Channels
from bus | tobus | item | label
Note on A16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: start_offset is to delay the start of Dynamic simulation in PSSE compared to PSCAD
Note on A18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This has been fixed to 1 in run_simulation script - line805
Note on A19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This has been fixed to 2 in run_simulation script - line805
Note on A20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is dummy bus inserted for including a dummy transformer for Vangle testing purposes DUM_TR_POC (default value: 10 line 483 in run_simulation script)
Note on A21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: POC_To bus
Note on A24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The numbering of these must match the Generator numbers
Note on C24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: by default the voltages and angles will alwaye be read at the toBus. But for example for the LV it may be preferred to read at the fromBus.
Note on A43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: for the setpoints common ways are adjusting variables or writing to VREF
Note on A49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Active Power setpoint to HyCon

## ModelDetailsPF
ParamIdentifier | Value
PF Version | DigSILENT PowerFactory 2023
Project Name | HSFBESS PQ Model
DPL_Z Loci | HSFBESS_Z_Loci
Study Case | Base Model
Grid ID | 220kV_EQ
PoC ID | 220kV_PoC
POC Feeder ID | 220kV Feeder
DPL_Switch off Grid | SwitchOff_Grid
DPL_Switch on Grid | SwitchOn_Grid
DPL_Switch off PoC Feeder | SwitchOff_PoC Feeder
DPL_Switch on PoC Feeder | SwitchOn_PoC Feeder
DPL_BESS Charge Characteristic | BESS Charge Characteristic
DPL_BESS Discharge Characteristic | BESS Discharge Characteristic
DPL_Q at Night Characteristic | PV Q at Night Characteristic
DPL_+10%BoP | plus10_BoP
DPL_-10%BoP | minus10_BoP
DPL_Emissions off | Inverter Emissions off
DPL_Reset Variations | Reset Variations

## LargeDist
Description: For every fault, specify the impedance in Ohms and the X/R ratio. For 3-phase faults, a residual voltage can be set, instead of the fault impedance and X/R. In that case, the fault impedance will be calculated so that the voltage initially dips to the value specified under 'Vresidual'. It is important that Vpoc and SCR as well as X/R are correctly defined for this to work. If both an impedance and 'Vresidual' are defined, only the impedance value is used in the simulation. For Multifault-sequences there are two option: 1) define define the first fault as a regular fault, subsequently define all other faults of the Multifault sequence for any fault belonging to the series, do not set caseID, it will then be interpreted as belonging to the multifaul sequence. 2) select one of the pre-defined multifault sequences under "fault type". The other fault parameters (impedance, fault X_R, residual voltage, and duration will then be ignored). The "Ftime" will be interpreted as the start time of the multifault sequence.
608
38
PSSE-specific settings
CaseNr | Test Type | Ftype | Ftime | Fduration | F_Impedance | Vresidual | Fault X_R | Vpoc | Active Power | Reactive Power | SCR | X_R | SCL_post | X_R_post | setpoint ID | init_help | TimeStep | AccFactor | run in PSCAD? | run in PSS/E? | Comment/Corresponding DMAT case | test group | simulation batch
1 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 25 | 0 | 1 | 0.2 | no | no | 1 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
2 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 27 | 0 | 1 | 0.2 | no | no | 2 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
3 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 26 | 0 | 1 | 0.2 | no | no | 3 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
4 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 4 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
5 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no | 5 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
6 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 20 | 0 | 1 | 0.2 | no | no | 6 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
7 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 1 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
8 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 9 | 0 | 1 | 0.2 | no | no | 2 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
9 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 3 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
10 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 4 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
11 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 5 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
12 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 6 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
13 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 28 | 0 | 1 | 0.2 | no | no | 7 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
14 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 30 | 0 | 1 | 0.2 | no | no | 8 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
15 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 29 | 0 | 1 | 0.2 | no | no | 9 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
16 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 10 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
17 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 24 | 0 | 1 | 0.2 | no | no | 11 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
18 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 23 | 0 | 1 | 0.2 | no | no | 12 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
19 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 10 | 0 | 1 | 0.2 | no | no | 7 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
20 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 8 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
21 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 9 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
22 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 4 | 0 | 1 | 0.2 | no | no | 10 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
23 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 11 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
24 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 5 | 0 | 1 | 0.2 | no | no | 12 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
25 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 25 | 0 | 1 | 0.2 | no | no | 13 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
26 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 27 | 0 | 1 | 0.2 | no | no | 14 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
27 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 26 | 0 | 1 | 0.2 | no | no | 15 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
28 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 16 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
29 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no | 17 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
30 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 20 | 0 | 1 | 0.2 | no | no | 18 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
31 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 13 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
32 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 9 | 0 | 1 | 0.2 | no | no | 14 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
33 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 15 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
34 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 16 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
35 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 17 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
36 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 18 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
37 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 28 | 0 | 1 | 0.2 | no | no | 19 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
38 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 30 | 0 | 1 | 0.2 | no | no | 20 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
39 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 29 | 0 | 1 | 0.2 | no | no | 21 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
40 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 22 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
41 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 24 | 0 | 1 | 0.2 | no | no | 23 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
42 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 23 | 0 | 1 | 0.2 | no | no | 24 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
43 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 10 | 0 | 1 | 0.2 | no | no | 19 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
44 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 20 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
45 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 21 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
46 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 4 | 0 | 1 | 0.2 | no | no | 22 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
47 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 23 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
48 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 5 | 0 | 1 | 0.2 | no | no | 24 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
49 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 25 | 0 | 1 | 0.2 | no | no | 25 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
50 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 27 | 0 | 1 | 0.2 | no | no | 26 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
51 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 26 | 0 | 1 | 0.2 | no | no | 27 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
52 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 28 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
53 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no | 29 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
54 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 20 | 0 | 1 | 0.2 | no | no | 30 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
55 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 25 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
56 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 9 | 0 | 1 | 0.2 | no | no | 26 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
57 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 27 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
58 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 28 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
59 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 29 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
60 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 30 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
61 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 28 | 0 | 1 | 0.2 | no | no | 31 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
62 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 30 | 0 | 1 | 0.2 | no | no | 32 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
63 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 29 | 0 | 1 | 0.2 | no | no | 33 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
64 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 34 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
65 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 24 | 0 | 1 | 0.2 | no | no | 35 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
66 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 23 | 0 | 1 | 0.2 | no | no | 36 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
67 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 10 | 0 | 1 | 0.2 | no | no | 31 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
68 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 32 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
69 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 33 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
70 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 4 | 0 | 1 | 0.2 | no | no | 34 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
71 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 35 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
72 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 5 | 0 | 1 | 0.2 | no | no | 36 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
73 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | no | 37 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT_SELF_ALL
74 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 27 | 0 | 1 | 0.2 | no | no | 38 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
75 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 26 | 0 | 1 | 0.2 | no | no | 39 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
76 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 40 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
77 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no | 41 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
78 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 20 | 0 | 1 | 0.2 | no | no | 42 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
79 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 66 | 0 | 1 | 0.2 | no | no | 37 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT_SELF_BESS
80 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 9 | 0 | 1 | 0.2 | no | no | 38 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
81 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 39 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
82 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 40 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
83 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 41 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
84 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 42 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
85 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 41 | 0 | 1 | 0.2 | yes | no | 43 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT_SELF_ALL
86 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 30 | 0 | 1 | 0.2 | no | no | 44 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
87 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 29 | 0 | 1 | 0.2 | no | no | 45 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
88 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 46 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
89 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 24 | 0 | 1 | 0.2 | no | no | 47 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
90 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 23 | 0 | 1 | 0.2 | no | no | 48 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
91 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 71 | 0 | 1 | 0.2 | no | no | 43 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT_SELF_BESS
92 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 44 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
93 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 45 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
94 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 4 | 0 | 1 | 0.2 | no | no | 46 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
95 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 47 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
96 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 5 | 0 | 1 | 0.2 | no | no | 48 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
97 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | no | 49 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT_SELF_ALL
98 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 27 | 0 | 1 | 0.2 | no | no | 50 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
99 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 26 | 0 | 1 | 0.2 | no | no | 51 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
100 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 52 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
101 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no | 53 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
102 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 20 | 0 | 1 | 0.2 | no | no | 54 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
103 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 66 | 0 | 1 | 0.2 | no | no | 49 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT_SELF_BESS
104 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 9 | 0 | 1 | 0.2 | no | no | 50 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
105 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 51 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
106 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 52 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
107 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 53 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
108 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 54 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
109 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 41 | 0 | 1 | 0.2 | yes | no | 55 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT_SELF_ALL
110 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 30 | 0 | 1 | 0.2 | no | no | 56 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
111 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 29 | 0 | 1 | 0.2 | no | no | 57 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
112 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 58 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
113 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 24 | 0 | 1 | 0.2 | no | no | 59 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
114 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 23 | 0 | 1 | 0.2 | no | no | 60 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
115 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 71 | 0 | 1 | 0.2 | no | no | 55 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT_SELF_BESS
116 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 56 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
117 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 57 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
118 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 4 | 0 | 1 | 0.2 | no | no | 58 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
119 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 59 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
120 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 5 | 0 | 1 | 0.2 | no | no | 60 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
121 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | no | 61 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT_SELF_ALL
122 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 27 | 0 | 1 | 0.2 | no | no | 62 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
123 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 26 | 0 | 1 | 0.2 | no | no | 63 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
124 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 64 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
125 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no | 65 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
126 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 20 | 0 | 1 | 0.2 | no | no | 66 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
127 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 66 | 0 | 1 | 0.2 | no | no | 61 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT_SELF_BESS
128 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 9 | 0 | 1 | 0.2 | no | no | 62 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
129 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 63 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
130 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 64 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
131 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 65 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
132 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 66 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
133 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 41 | 0 | 1 | 0.2 | yes | no | 67 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT_SELF_ALL
134 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 30 | 0 | 1 | 0.2 | no | no | 68 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
135 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 29 | 0 | 1 | 0.2 | no | no | 69 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
136 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 70 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
137 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 24 | 0 | 1 | 0.2 | no | no | 71 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
138 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 23 | 0 | 1 | 0.2 | no | no | 72 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
139 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 71 | 0 | 1 | 0.2 | no | no | 67 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT_SELF_BESS
140 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 68 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
141 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 69 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
142 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 4 | 0 | 1 | 0.2 | no | no | 70 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
143 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 71 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
144 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 5 | 0 | 1 | 0.2 | no | no | 72 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
145 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | no | 73 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT_SELF_ALL
146 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 27 | 0 | 1 | 0.2 | no | no | 74 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
147 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 26 | 0 | 1 | 0.2 | no | no | 75 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
148 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 76 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
149 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no | 77 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
150 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 20 | 0 | 1 | 0.2 | no | no | 78 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
151 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 66 | 0 | 1 | 0.2 | no | no | 73 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT_SELF_BESS
152 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 9 | 0 | 1 | 0.2 | no | no | 74 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
153 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 75 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
154 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 76 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
155 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 77 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
156 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 78 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
157 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 41 | 0 | 1 | 0.2 | yes | no | 79 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT_SELF_ALL
158 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 30 | 0 | 1 | 0.2 | no | no | 80 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
159 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 29 | 0 | 1 | 0.2 | no | no | 81 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
160 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 82 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
161 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 24 | 0 | 1 | 0.2 | no | no | 83 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
162 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 23 | 0 | 1 | 0.2 | no | no | 84 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
163 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 71 | 0 | 1 | 0.2 | no | no | 79 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT_SELF_BESS
164 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 80 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
165 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 81 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
166 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 4 | 0 | 1 | 0.2 | no | no | 82 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
167 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 83 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
168 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 5 | 0 | 1 | 0.2 | no | no | 84 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
169 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | no | 85 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT_SELF_ALL
170 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 27 | 0 | 1 | 0.2 | no | no | 86 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
171 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 26 | 0 | 1 | 0.2 | no | no | 87 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
172 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 88 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
173 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no | 89 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
174 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 20 | 0 | 1 | 0.2 | no | no | 90 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
175 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 66 | 0 | 1 | 0.2 | no | no | 85 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT_SELF_BESS
176 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 9 | 0 | 1 | 0.2 | no | no | 86 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
177 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 87 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
178 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 88 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
179 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 89 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
180 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 90 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
181 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 41 | 0 | 1 | 0.2 | yes | no | 91 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT_SELF_ALL
182 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 30 | 0 | 1 | 0.2 | no | no | 92 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
183 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 29 | 0 | 1 | 0.2 | no | no | 93 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
184 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 94 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
185 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 24 | 0 | 1 | 0.2 | no | no | 95 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
186 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 23 | 0 | 1 | 0.2 | no | no | 96 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
187 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 71 | 0 | 1 | 0.2 | no | no | 91 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT_SELF_BESS
188 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 92 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
189 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 93 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
190 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 4 | 0 | 1 | 0.2 | no | no | 94 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
191 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 95 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
192 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 5 | 0 | 1 | 0.2 | no | no | 96 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
193 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 25 | 0 | 1 | 0.2 | no | no | 97 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
194 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 27 | 0 | 1 | 0.2 | no | no | 98 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
195 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 26 | 0 | 1 | 0.2 | no | no | 99 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
196 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 100 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
197 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no | 101 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
198 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 20 | 0 | 1 | 0.2 | no | no | 102 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
199 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 97 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
200 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 9 | 0 | 1 | 0.2 | no | no | 98 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
201 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 99 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
202 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 100 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
203 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 101 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
204 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 102 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
205 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 28 | 0 | 1 | 0.2 | no | no | 103 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
206 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 30 | 0 | 1 | 0.2 | no | no | 104 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
207 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 29 | 0 | 1 | 0.2 | no | no | 105 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
208 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 106 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
209 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 24 | 0 | 1 | 0.2 | no | no | 107 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
210 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 23 | 0 | 1 | 0.2 | no | no | 108 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
211 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 10 | 0 | 1 | 0.2 | no | no | 103 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
212 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 104 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
213 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 105 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
214 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 4 | 0 | 1 | 0.2 | no | no | 106 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
215 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 107 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
216 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 5 | 0 | 1 | 0.2 | no | no | 108 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
217 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 25 | 0 | 1 | 0.2 | no | no | 97 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
218 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 27 | 0 | 1 | 0.2 | no | no | 98 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
219 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 26 | 0 | 1 | 0.2 | no | no | 99 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
220 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 100 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
221 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no | 101 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
222 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 20 | 0 | 1 | 0.2 | no | no | 102 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
223 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 97 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
224 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 9 | 0 | 1 | 0.2 | no | no | 98 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
225 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 99 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
226 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 100 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
227 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 101 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
228 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 102 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
229 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 28 | 0 | 1 | 0.2 | no | no | 103 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
230 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 30 | 0 | 1 | 0.2 | no | no | 104 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
231 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 29 | 0 | 1 | 0.2 | no | no | 105 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
232 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 106 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
233 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 24 | 0 | 1 | 0.2 | no | no | 107 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
234 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 23 | 0 | 1 | 0.2 | no | no | 108 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
235 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 10 | 0 | 1 | 0.2 | no | no | 103 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
236 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 104 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
237 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 105 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
238 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 4 | 0 | 1 | 0.2 | no | no | 106 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
239 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 107 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
240 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 5 | 0 | 1 | 0.2 | no | no | 108 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
241 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 25 | 0 | 1 | 0.2 | no | no | 97 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
242 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 27 | 0 | 1 | 0.2 | no | no | 98 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
243 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 26 | 0 | 1 | 0.2 | no | no | 99 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
244 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 100 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
245 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no | 101 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
246 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 20 | 0 | 1 | 0.2 | no | no | 102 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
247 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 97 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
248 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 9 | 0 | 1 | 0.2 | no | no | 98 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
249 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 99 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
250 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 100 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
251 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 101 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
252 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 102 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
253 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 28 | 0 | 1 | 0.2 | no | no | 103 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
254 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 30 | 0 | 1 | 0.2 | no | no | 104 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
255 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 29 | 0 | 1 | 0.2 | no | no | 105 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
256 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 106 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
257 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 24 | 0 | 1 | 0.2 | no | no | 107 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
258 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 23 | 0 | 1 | 0.2 | no | no | 108 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
259 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 10 | 0 | 1 | 0.2 | no | no | 103 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
260 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 104 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
261 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 105 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
262 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 4 | 0 | 1 | 0.2 | no | no | 106 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
263 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 107 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
264 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 5 | 0 | 1 | 0.2 | no | no | 108 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
265 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 25 | 0 | 1 | 0.2 | no | no | 109 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
266 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 27 | 0 | 1 | 0.2 | no | no | 110 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
267 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 26 | 0 | 1 | 0.2 | no | no | 111 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
268 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 112 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
269 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no | 113 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
270 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 20 | 0 | 1 | 0.2 | no | no | 114 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
271 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 109 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
272 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 9 | 0 | 1 | 0.2 | no | no | 110 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
273 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 111 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
274 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 112 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
275 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 113 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
276 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 114 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
277 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 28 | 0 | 1 | 0.2 | no | no | 115 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
278 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 30 | 0 | 1 | 0.2 | no | no | 116 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
279 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 29 | 0 | 1 | 0.2 | no | no | 117 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
280 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 118 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
281 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 24 | 0 | 1 | 0.2 | no | no | 119 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
282 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 23 | 0 | 1 | 0.2 | no | no | 120 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
283 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 10 | 0 | 1 | 0.2 | no | no | 115 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
284 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 116 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
285 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 117 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
286 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 4 | 0 | 1 | 0.2 | no | no | 118 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
287 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 119 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
288 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 5 | 0 | 1 | 0.2 | no | no | 120 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
289 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 25 | 0 | 1 | 0.2 | no | no | 109 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
290 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 27 | 0 | 1 | 0.2 | no | no | 110 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
291 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 26 | 0 | 1 | 0.2 | no | no | 111 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
292 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 112 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
293 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no | 113 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
294 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 20 | 0 | 1 | 0.2 | no | no | 114 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
295 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 109 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
296 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 9 | 0 | 1 | 0.2 | no | no | 110 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
297 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 111 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
298 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 112 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
299 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 113 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
300 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 114 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
301 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 28 | 0 | 1 | 0.2 | no | no | 115 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
302 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 30 | 0 | 1 | 0.2 | no | no | 116 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
303 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 29 | 0 | 1 | 0.2 | no | no | 117 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
304 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 118 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
305 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 24 | 0 | 1 | 0.2 | no | no | 119 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
306 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 23 | 0 | 1 | 0.2 | no | no | 120 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
307 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 10 | 0 | 1 | 0.2 | no | no | 115 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
308 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 116 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
309 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 117 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
310 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 4 | 0 | 1 | 0.2 | no | no | 118 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
311 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 119 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
312 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 5 | 0 | 1 | 0.2 | no | no | 120 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
313 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 25 | 0 | 1 | 0.2 | no | no | 109 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
314 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 27 | 0 | 1 | 0.2 | no | no | 110 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
315 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 26 | 0 | 1 | 0.2 | no | no | 111 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
316 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 112 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
317 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no | 113 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
318 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 20 | 0 | 1 | 0.2 | no | no | 114 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
319 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 109 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
320 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 9 | 0 | 1 | 0.2 | no | no | 110 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
321 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 111 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
322 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 112 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
323 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 113 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
324 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 114 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
325 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 28 | 0 | 1 | 0.2 | no | no | 115 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
326 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 30 | 0 | 1 | 0.2 | no | no | 116 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
327 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 29 | 0 | 1 | 0.2 | no | no | 117 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
328 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 118 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
329 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 24 | 0 | 1 | 0.2 | no | no | 119 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
330 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 23 | 0 | 1 | 0.2 | no | no | 120 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
331 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 10 | 0 | 1 | 0.2 | no | no | 115 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
332 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 116 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
333 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 117 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
334 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 4 | 0 | 1 | 0.2 | no | no | 118 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
335 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 119 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
336 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 5 | 0 | 1 | 0.2 | no | no | 120 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
337 | Multifault | 3PHG | 5 | 0.1 |  | 0.2 | 1.13 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | no | 121 | Multiple Fault Ride Through (MFRT) test [PSCAD/EMTDC models] | DMAT_SELF_ALL
|  | 3PHG | 5.25 | 0.1 |  | 0.2 | 1.13 | [9 empty] | 1 |  | yes | no |  |  | DMAT_SELF_ALL
|  | 3PHG | 5.5 | 0.1 |  | 0.2 | 1.13 | [9 empty] | 1 |  | yes | no |  |  | DMAT_SELF_ALL
|  | 2PHG | 8 | 0.1 |  | 0.2 | 1.13 | [9 empty] | 1 |  | yes | no |  |  | DMAT_SELF_ALL
|  | 2PHG | 11 | 0.1 |  | 0.2 | 1.13 | [9 empty] | 1 |  | yes | no |  |  | DMAT_SELF_ALL
|  | 2PHG | 13 | 0.1 |  | 0.2 | 1.13 | [9 empty] | 1 |  | yes | no |  |  | DMAT_SELF_ALL
338 | Multifault_random |  | 5 | [11 empty] | 36 | 0 | 1 | 0.2 | yes | no | 122 | Multiple Fault Ride Through (MFRT) test [PSCAD/EMTDC models] | DMAT_SELF_ALL
339 | Multifault | 3PHG | 5 | 0.1 |  | 0.2 | 1.13 | [7 empty] | 66 | 0 | 1 | 0.2 | no | no | 121 | Multiple Fault Ride Through (MFRT) test [PSCAD/EMTDC models] | DMAT_SELF_BESS
|  | 3PHG | 5.25 | 0.1 |  | 0.2 | 1.13 | [9 empty] | 1 |  | no | no |  |  | DMAT_SELF_BESS
|  | 3PHG | 5.5 | 0.1 |  | 0.2 | 1.13 | [9 empty] | 1 |  | no | no |  |  | DMAT_SELF_BESS
|  | 2PHG | 8 | 0.1 |  | 0.2 | 1.13 | [9 empty] | 1 |  | no | no |  |  | DMAT_SELF_BESS
|  | 2PHG | 11 | 0.1 |  | 0.2 | 1.13 | [9 empty] | 1 |  | no | no |  |  | DMAT_SELF_BESS
|  | 2PHG | 13 | 0.1 |  | 0.2 | 1.13 | [9 empty] | 1 |  | no | no |  |  | DMAT_SELF_BESS
340 | Multifault_random |  | 5 | [11 empty] | 66 | 0 | 1 | 0.2 | no | no | 122 | Multiple Fault Ride Through (MFRT) test [PSCAD/EMTDC models] | DMAT_SELF_BESS
341 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | no | 123 | Multiple Fault Ride Through (MFRT) test [PSCAD/EMTDC models] | DMAT
342 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | no | 124 | Multiple Fault Ride Through (MFRT) test [PSCAD/EMTDC models] | DMAT
343 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | no | 125 | Multiple Fault Ride Through (MFRT) test [PSCAD/EMTDC models] | DMAT
344 | Multifault_random |  | 5 | [11 empty] | 36 | 0 | 1 | 0.2 | no | yes | 126 | MFRT Test [PSS®E models] | DMAT_SELF_ALL
345 | Multifault_random |  | 5 | [11 empty] | 36 | 0 | 1 | 0.2 | no | yes | 127 | MFRT Test [PSS®E models] | DMAT_SELF_ALL
346 | Multifault_random |  | 5 | [11 empty] | 66 | 0 | 1 | 0.2 | no | no | 126 | MFRT Test [PSS®E models] | DMAT_SELF_BESS
347 | Multifault_random |  | 5 | [11 empty] | 66 | 0 | 1 | 0.2 | no | no | 127 | MFRT Test [PSS®E models] | DMAT_SELF_BESS
348 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | no | 128 | MFRT Test [PSS®E models] | DMAT
349 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | no | 129 | MFRT Test [PSS®E models] | DMAT
350 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | no | 130 | MFRT Test [PSS®E models] | DMAT
351 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 118.8 | 14 | 424 | 0 | 1 | 0.2 | yes | yes | 200 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
352 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 118.8 | 3 | 426 | 0 | 1 | 0.2 | yes | yes | 200 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
353 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 118.8 | 14 | 415 | 0 | 1 | 0.2 | no | no | 200 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
354 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 118.8 | 3 | 417 | 0 | 1 | 0.2 | no | no | 200 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
355 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 118.8 | 14 | 69 | 0 | 1 | 0.2 | no | no | 201 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
356 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 118.8 | 14 | 16 | 0 | 1 | 0.2 | no | no | 202 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
357 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 118.8 | 14 | 424 | 0 | 1 | 0.2 | yes | yes | 203 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
358 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 118.8 | 3 | 426 | 0 | 1 | 0.2 | yes | yes | 203 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
357 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 118.8 | 14 | 415 | 0 | 1 | 0.2 | no | no | 203 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
358 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 118.8 | 3 | 417 | 0 | 1 | 0.2 | no | no | 203 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
359 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 118.8 | 14 | 69 | 0 | 1 | 0.2 | no | no | 204 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
360 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 118.8 | 14 | 16 | 0 | 1 | 0.2 | no | no | 205 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
361 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 118.8 | 3 | 414 | 0 | 1 | 0.2 | no | no | 200 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
362 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 118.8 | 3 | 416 | 0 | 1 | 0.2 | no | no | 200 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
363 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 118.8 | 3 | 415 | 0 | 1 | 0.2 | no | no | 200 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
364 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 118.8 | 3 | 417 | 0 | 1 | 0.2 | no | no | 200 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
365 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 118.8 | 3 | 70 | 0 | 1 | 0.2 | no | no | 201 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
366 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 118.8 | 3 | 22 | 0 | 1 | 0.2 | no | no | 202 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
365 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 118.8 | 3 | 414 | 0 | 1 | 0.2 | no | no | 203 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
366 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 118.8 | 3 | 416 | 0 | 1 | 0.2 | no | no | 203 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
367 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 118.8 | 3 | 415 | 0 | 1 | 0.2 | no | no | 203 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
368 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 118.8 | 3 | 417 | 0 | 1 | 0.2 | no | no | 203 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
369 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 118.8 | 3 | 70 | 0 | 1 | 0.2 | no | no | 204 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
370 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 118.8 | 3 | 22 | 0 | 1 | 0.2 | no | no | 205 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
371 | Fault | 3PHG | 5 | 0.43 |  | 0 | [8 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 206 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL | prelim_fault_ALL
372 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | [8 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 207 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
373 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | [8 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 208 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
374 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | [8 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 209 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL_DBG
375 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | [8 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 210 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
376 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | [8 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 211 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
377 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | [8 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 212 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
378 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | [8 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 213 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
379 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [8 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 214 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
380 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | [8 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 215 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
381 | Fault | 3PHG | 5 | 0.43 |  | 0 | [8 empty] | 418 | 0 | 1 | 0.2 | yes | yes | 216 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
382 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | [8 empty] | 418 | 0 | 1 | 0.2 | yes | yes | 217 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
383 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | [8 empty] | 418 | 0 | 1 | 0.2 | yes | yes | 218 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
384 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | [8 empty] | 418 | 0 | 1 | 0.2 | yes | yes | 219 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
385 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | [8 empty] | 418 | 0 | 1 | 0.2 | yes | yes | 220 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
386 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | [8 empty] | 418 | 0 | 1 | 0.2 | yes | yes | 221 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
387 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | [8 empty] | 418 | 0 | 1 | 0.2 | yes | yes | 222 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
388 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | [8 empty] | 418 | 0 | 1 | 0.2 | yes | yes | 223 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
389 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [8 empty] | 418 | 0 | 1 | 0.2 | yes | yes | 224 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
390 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | [8 empty] | 418 | 0 | 1 | 0.2 | yes | yes | 225 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
391 | Fault | 3PHG | 5 | 0.43 |  | 0 | [8 empty] | 21 | 0 | 1 | 0.2 | no | no | 206 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS | prelim_fault_BESS
392 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | [8 empty] | 21 | 0 | 1 | 0.2 | no | no | 207 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
393 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | [8 empty] | 21 | 0 | 1 | 0.2 | no | no | 208 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
394 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | [8 empty] | 21 | 0 | 1 | 0.2 | no | no | 209 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
395 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | [8 empty] | 21 | 0 | 1 | 0.2 | no | no | 210 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
396 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | [8 empty] | 21 | 0 | 1 | 0.2 | no | no | 211 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
397 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | [8 empty] | 21 | 0 | 1 | 0.2 | no | no | 212 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
398 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | [8 empty] | 21 | 0 | 1 | 0.2 | no | no | 213 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
399 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [8 empty] | 21 | 0 | 1 | 0.2 | no | no | 214 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
400 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | [8 empty] | 21 | 0 | 1 | 0.2 | no | no | 215 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
401 | Fault | 3PHG | 5 | 0.43 |  | 0 | [8 empty] | 407 | 0 | 1 | 0.2 | no | no | 216 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
402 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | [8 empty] | 407 | 0 | 1 | 0.2 | no | no | 217 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
403 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | [8 empty] | 407 | 0 | 1 | 0.2 | no | no | 218 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
404 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | [8 empty] | 407 | 0 | 1 | 0.2 | no | no | 219 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
405 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | [8 empty] | 407 | 0 | 1 | 0.2 | no | no | 220 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
406 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | [8 empty] | 407 | 0 | 1 | 0.2 | no | no | 221 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
407 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | [8 empty] | 407 | 0 | 1 | 0.2 | no | no | 222 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
408 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | [8 empty] | 407 | 0 | 1 | 0.2 | no | no | 223 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
409 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [8 empty] | 407 | 0 | 1 | 0.2 | no | no | 224 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
410 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | [8 empty] | 407 | 0 | 1 | 0.2 | no | no | 225 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
411 | Fault | 3PHG | 5 | 0.43 |  | 0.85 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL | Min SCR Q0
412 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
413 | Fault | 3PHG | 5 | 0.43 |  | 0.25 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
414 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
415 | Fault | 3PHG | 5 | 0.43 |  | 0.85 | 3 | [7 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL | Max SCR Q0
416 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
417 | Fault | 3PHG | 5 | 0.43 |  | 0.25 | 3 | [7 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
418 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
419 | Fault | 3PHG | 5 | 0.12 |  | 0.8 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS | Min SCR Q0
420 | Fault | 3PHG | 5 | 0.12 |  | 0.5 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
421 | Fault | 3PHG | 5 | 0.12 |  | 0.25 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
422 | Fault | 3PHG | 5 | 0.12 |  | 0 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
423 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 66 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS | Max SCR Q0
424 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 66 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
425 | Fault | 3PHG | 5 | 0.43 |  | 0.25 | 3 | [7 empty] | 66 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
426 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 66 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
427 | Multifault | 3PHG | 5 | 0.22 |  | 0.4 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  | Multiple Fault Ride Through (MFRT) test [PSCAD/EMTDC models] | S5255_MULTI_ALL
|  | 2PHG | 5.32 | 0.43 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no
|  | 1PHG | 5.85 | 0.49 |  | 0.85 | 3 | [9 empty] | 1 |  | no | no
|  | 3PHG | 6.44 | 0.22 |  | 0.4 | 3 | [9 empty] | 1 |  | no | no
|  | 2PHG | 7.66 | 0.12 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no
|  | 2PHG | 7.88 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no
|  | 2PHG | 10.1 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no
|  | 2PHG | 10.82 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no
|  | 2PHG | 11.54 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no
|  | 2PHG | 11.86 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no
|  | 2PHG | 12.13 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no
|  | 2PHG | 14.35 | 0.12 |  | 0.85 | 3 | [9 empty] | 1 |  | no | no
|  | 1PHG | 16.47 | 0.12 |  | 0.85 | 3 | [9 empty] | 1 |  | no | no
|  | 1PHG | 21.59 | 0.22 |  | 0.85 | 3 | [9 empty] | 1 |  | no | no
|  | 2PHG | 22.81 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no
428 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL
429 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL
430 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL
431 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL
432 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL
433 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL
434 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL
435 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL
436 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL
437 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL
438 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL
439 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL
440 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL
441 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL
442 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL
443 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL
444 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL
445 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL
446 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL
447 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | 3 | [7 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL
448 | Multifault | 3PHG | 5 | 0.22 |  | 0.4 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no |  | Multiple Fault Ride Through (MFRT) test [PSCAD/EMTDC models] | S5255_BESS
|  | 2PHG | 5.32 | 0.43 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no
|  | 1PHG | 5.85 | 0.49 |  | 0.85 | 3 | [9 empty] | 1 |  | no | no
|  | 3PHG | 6.44 | 0.22 |  | 0.4 | 3 | [9 empty] | 1 |  | no | no
|  | 2PHG | 7.66 | 0.12 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no
|  | 2PHG | 7.88 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no
|  | 2PHG | 10.1 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no
|  | 2PHG | 10.82 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no
|  | 2PHG | 11.54 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no
|  | 2PHG | 11.86 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no
|  | 2PHG | 12.13 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no
|  | 2PHG | 14.35 | 0.12 |  | 0.85 | 3 | [9 empty] | 1 |  | no | no
|  | 1PHG | 16.47 | 0.12 |  | 0.85 | 3 | [9 empty] | 1 |  | no | no
|  | 1PHG | 21.59 | 0.22 |  | 0.85 | 3 | [9 empty] | 1 |  | no | no
|  | 2PHG | 22.81 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no
449 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_BESS
450 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_BESS
451 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_BESS
452 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_BESS
453 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_BESS
454 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_BESS
455 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_BESS
456 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_BESS
457 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_BESS
458 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | 3 | [7 empty] | 21 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_BESS
459 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 66 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_BESS
460 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 66 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_BESS
461 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 66 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_BESS
462 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 66 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_BESS
463 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 66 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_BESS
464 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 66 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_BESS
465 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 66 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_BESS
466 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 66 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_BESS
467 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 66 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_BESS
468 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | 3 | [7 empty] | 66 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_BESS
469 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 84 | 1 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_IQ_ALL
470 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 84 | 1 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_IQ_ALL
471 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 84 | 1 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_IQ_ALL
472 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 84 | 1 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_IQ_ALL
473 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 84 | 1 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_IQ_ALL
472 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 84 | 1 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_IQ_ALL
473 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 84 | 1 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_IQ_ALL
474 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 84 | 1 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_IQ_ALL
475 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 84 | 1 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_IQ_ALL
476 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 69 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_IQ_BESS
477 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 69 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_IQ_BESS
478 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 69 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_IQ_BESS
479 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 69 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_IQ_BESS
480 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 69 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_IQ_BESS
481 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 69 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_IQ_BESS
482 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 69 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_IQ_BESS
483 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 69 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_IQ_BESS
484 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 69 | 0 | 1 | 0.2 | no | no |  | Iq rise/settling time and P recovery assessment | S5255_IQ_BESS
485 | Fault | 3PHG | 5 | 0.43 |  | 0 | [8 empty] | 36 | 0 | 1 | 0.2 | no | no | 206 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_PV
486 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | [8 empty] | 36 | 0 | 1 | 0.2 | no | no | 207 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_PV
487 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | [8 empty] | 36 | 0 | 1 | 0.2 | no | no | 208 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_PV
488 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | [8 empty] | 36 | 0 | 1 | 0.2 | no | no | 209 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_PV
489 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | [8 empty] | 36 | 0 | 1 | 0.2 | no | no | 210 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_PV
490 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | [8 empty] | 36 | 0 | 1 | 0.2 | no | no | 211 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_PV
491 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | [8 empty] | 36 | 0 | 1 | 0.2 | no | no | 212 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_PV
492 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | [8 empty] | 36 | 0 | 1 | 0.2 | no | no | 213 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_PV
493 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [8 empty] | 36 | 0 | 1 | 0.2 | no | no | 214 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_PV
494 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | [8 empty] | 36 | 0 | 1 | 0.2 | no | no | 215 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_PV
495 | Fault | 3PHG | 5 | 0.43 |  | 0 | [8 empty] | 21 | 0 | 1 | 0.2 | no | no | 206 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_BESS
496 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | [8 empty] | 21 | 0 | 1 | 0.2 | no | no | 207 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_BESS
497 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | [8 empty] | 21 | 0 | 1 | 0.2 | no | no | 208 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_BESS
498 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | [8 empty] | 21 | 0 | 1 | 0.2 | no | no | 209 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_BESS
499 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | [8 empty] | 21 | 0 | 1 | 0.2 | no | no | 210 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_BESS
500 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | [8 empty] | 21 | 0 | 1 | 0.2 | no | no | 211 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_BESS
501 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | [8 empty] | 21 | 0 | 1 | 0.2 | no | no | 212 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_BESS
502 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | [8 empty] | 21 | 0 | 1 | 0.2 | no | no | 213 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_BESS
503 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [8 empty] | 21 | 0 | 1 | 0.2 | no | no | 214 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_BESS
504 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | [8 empty] | 21 | 0 | 1 | 0.2 | no | no | 215 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_BESS
505 | Fault | 3PHG | 5 | 0.43 |  | 0 | [8 empty] | 1 | 0 | 1 | 0.2 | no | no | 206 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_ALL
506 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | [8 empty] | 1 | 0 | 1 | 0.2 | no | no | 207 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_ALL
507 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | [8 empty] | 1 | 0 | 1 | 0.2 | no | no | 208 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_ALL
508 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | [8 empty] | 1 | 0 | 1 | 0.2 | no | no | 209 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_ALL
509 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | [8 empty] | 1 | 0 | 1 | 0.2 | no | no | 210 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_ALL
510 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | [8 empty] | 1 | 0 | 1 | 0.2 | no | no | 211 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_ALL
511 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | [8 empty] | 1 | 0 | 1 | 0.2 | no | no | 212 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_ALL
512 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | [8 empty] | 1 | 0 | 1 | 0.2 | no | no | 213 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_ALL
513 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [8 empty] | 1 | 0 | 1 | 0.2 | no | no | 214 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_ALL
514 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | [8 empty] | 1 | 0 | 1 | 0.2 | no | no | 215 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | P_DROP_DEBUG_ALL
515 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 39 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
516 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 39 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
517 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 39 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
518 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 39 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
519 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 39 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
520 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 39 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
521 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 39 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
522 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 39 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
523 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 39 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
524 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | 3 | [7 empty] | 39 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
525 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 84 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
526 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 84 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
527 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 84 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
528 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 84 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
529 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 84 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
530 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 84 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
531 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 84 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
532 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 84 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
533 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 84 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
534 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | 3 | [7 empty] | 84 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
535 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 40 | 0 | 1 | 0.2 | yes | no |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
536 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 40 | 0 | 1 | 0.2 | yes | no |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
537 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 40 | 0 | 1 | 0.2 | yes | no |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
538 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 40 | 0 | 1 | 0.2 | yes | no |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
539 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 40 | 0 | 1 | 0.2 | yes | no |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
540 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 40 | 0 | 1 | 0.2 | yes | no |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
541 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 40 | 0 | 1 | 0.2 | yes | no |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
542 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 40 | 0 | 1 | 0.2 | yes | no |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
543 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 40 | 0 | 1 | 0.2 | yes | no |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
544 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | 3 | [7 empty] | 40 | 0 | 1 | 0.2 | yes | no |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
545 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 85 | 0 | 1 | 0.2 | yes | no |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
546 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 85 | 0 | 1 | 0.2 | yes | no |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
547 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 85 | 0 | 1 | 0.2 | yes | no |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
548 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 85 | 0 | 1 | 0.2 | yes | no |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
549 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 85 | 0 | 1 | 0.2 | yes | no |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
550 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 85 | 0 | 1 | 0.2 | yes | no |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
551 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 85 | 0 | 1 | 0.2 | yes | no |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
552 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 85 | 0 | 1 | 0.2 | yes | no |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
553 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 85 | 0 | 1 | 0.2 | yes | no |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
554 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | 3 | [7 empty] | 85 | 0 | 1 | 0.2 | yes | no |  | Iq rise/settling time and P recovery assessment | S5255_ALL_Qextr
555 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | no |  | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | S5255_unbalanced
556 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 81 | 0 | 1 | 0.2 | yes | no |  | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | S5255_unbalanced
557 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | no |  | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | S5255_unbalanced
558 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 81 | 0 | 1 | 0.2 | yes | no |  | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | S5255_unbalanced
559 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | no |  | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | S5255_unbalanced
560 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 81 | 0 | 1 | 0.2 | yes | no |  | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | S5255_unbalanced
561 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | no |  | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | S5255_unbalanced
562 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 81 | 0 | 1 | 0.2 | yes | no |  | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | S5255_unbalanced
563 | Fault | L-L | 5 | 0.43 |  | 0 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | no |  | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | S5255_unbalanced
564 | Fault | L-L | 5 | 0.43 |  | 0 | 3 | [7 empty] | 81 | 0 | 1 | 0.2 | yes | no |  | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | S5255_unbalanced
565 | Fault | L-L | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | yes | no |  | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | S5255_unbalanced
566 | Fault | L-L | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 81 | 0 | 1 | 0.2 | yes | no |  | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | S5255_unbalanced
Note on C6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Multifault, include a few sequences that are hard-coded. In case a multifault sequence is chosen, The Fault X_R, Impedance, residual voltage, duration and application time are ignored.
Note on A7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MAT
Note on A31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MAT
Note on A55: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MAT

## SmallDist
When defining the SmallDist tests, make sure the initial values of the profiles do not contradict the Initialisation parameters in the Setpoints tab, as they will overwrite the parameters form the "Setpoints" sheet, where applicable. E.G.: When running S5.2.5.4 on an inifinite grid, and the selected initial setpoint defined in the "PSCAD setpoint ID" inisilises to 1.04pu at the POC, then the test profile selected under "Test profile" and defined in the "Profiles" sheet, should also start with 1.04pu to ensure smooth intialisation. If the profile starts at a different voltage, it might for example lead to different power flows at the POC and an incoherent transformer tap. (In the future a routine could be added that scales or offsets the profile to match the initial valuye of the profile, and notifies the user). Grid SCR and Grid X/R refer to the point where the grid source is attached, which may be differnet from the POC. For example in the case of Mulwala the grid source is connected at 132 kV level, (which is where the plant controls the voltage) but the POC is at 22 kV level. | [10 empty] | PSSE-specific settings
CaseNr | Test Type | Test profile | Vpoc | ActivePower | ReactivePower | Secondary SCL time | Secondary SCL | Secondary X_R | setpoint ID | init_help | TimeStep | AccFactor | run in PSCAD? | run in PSS/E? | comment | test group | simulation batch | more comment | additional comment | framwork changes required
1 | V_profile | FLAT_RUN_5 | [6 empty] | 36 | 0 | 1 | 0.2 | yes | no | 0.1 | Pre-requisite tests – single machine infinite bus (SMIB) flat run [PSCAD/EMTDC models] | DMAT_SELF_ALL |  | normally 300s
2 | V_profile | FLAT_RUN_5 | [6 empty] | 36 | 0 | 1 | 0.2 | yes | no | 0.2 | Pre-requisite tests – single machine infinite bus (SMIB) flat run [PSCAD/EMTDC models] | DMAT_SELF_ALL |  | normally 300s
3 | V_profile | FLAT_RUN_5 | [6 empty] | 41 | 0 | 1 | 0.2 | yes | no | 0.3 | Pre-requisite tests – single machine infinite bus (SMIB) flat run [PSCAD/EMTDC models] | DMAT_SELF_ALL |  | normally 300s
4 | V_profile | FLAT_RUN_5 | [6 empty] | 36 | 0 | 1 | 0.2 | yes | no | 0.4 | Pre-requisite tests – single machine infinite bus (SMIB) flat run [PSCAD/EMTDC models] | DMAT_SELF_ALL
5 | V_profile | FLAT_RUN_5 | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 0.1 | Pre-requisite tests – single machine infinite bus (SMIB) flat run [PSCAD/EMTDC models] | DMAT_SELF_BESS |  | normally 300s
6 | V_profile | FLAT_RUN_5 | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 0.2 | Pre-requisite tests – single machine infinite bus (SMIB) flat run [PSCAD/EMTDC models] | DMAT_SELF_BESS |  | normally 300s
7 | V_profile | FLAT_RUN_5 | [6 empty] | 71 | 0 | 1 | 0.2 | no | no | 0.3 | Pre-requisite tests – single machine infinite bus (SMIB) flat run [PSCAD/EMTDC models] | DMAT_SELF_BESS |  | normally 300s
8 | V_profile | FLAT_RUN_5 | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 0.4 | Pre-requisite tests – single machine infinite bus (SMIB) flat run [PSCAD/EMTDC models] | DMAT_SELF_BESS
9 | V_profile | FLAT_RUN_5 | [6 empty] | 37 | 0 | 1 | 0.2 | no | no | 0.5 | Pre-requisite tests – single machine infinite bus (SMIB) flat run [PSCAD/EMTDC models] | DMAT
10 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 25 | 0 | 1 | 0.2 | no | no | 149 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | ScriptTest
11 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 149 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
12 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 28 | 0 | 1 | 0.2 | no | no | 150 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
13 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 34 | 0 | 1 | 0.2 | no | no | 150 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
14 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 13 | 0 | 1 | 0.2 | no | no | 151 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
15 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 19 | 0 | 1 | 0.2 | no | no | 151 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
16 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 16 | 0 | 1 | 0.2 | no | no | 152 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
17 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 22 | 0 | 1 | 0.2 | no | no | 152 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
18 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 153 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
19 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 153 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
20 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 10 | 0 | 1 | 0.2 | no | no | 154 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
21 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 4 | 0 | 1 | 0.2 | no | no | 154 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
22 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 25 | 0 | 1 | 0.2 | no | no | 155 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
23 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 155 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
24 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 28 | 0 | 1 | 0.2 | no | no | 156 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
25 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 34 | 0 | 1 | 0.2 | no | no | 156 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
26 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 13 | 0 | 1 | 0.2 | no | no | 157 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
27 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 19 | 0 | 1 | 0.2 | no | no | 157 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
28 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 16 | 0 | 1 | 0.2 | no | no | 158 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
29 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 22 | 0 | 1 | 0.2 | no | no | 158 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
30 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 159 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
31 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 1 | 0 | 1 | 0.2 | no | no | 160 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
32 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 159 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
33 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 4 | 0 | 1 | 0.2 | no | no | 160 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
34 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 99 | 0 | 1 | 0.2 | no | no | 161 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
35 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 105 | 0 | 1 | 0.2 | no | no | 161 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
36 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 102 | 0 | 1 | 0.2 | no | no | 162 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
37 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 108 | 0 | 1 | 0.2 | no | no | 162 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
38 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 87 | 0 | 1 | 0.2 | no | no | 163 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
39 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 93 | 0 | 1 | 0.2 | no | no | 163 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
40 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 90 | 0 | 1 | 0.2 | no | no | 164 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
41 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 96 | 0 | 1 | 0.2 | no | no | 164 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
42 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 171 | 0 | 1 | 0.2 | yes | yes | 165 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
43 | Q1_stp_profile | MAT_QREF_STEP_Fig4_BESS | [6 empty] | 156 | 0 | 1 | 0.2 | no | no | 165 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS |  |  | make sure Q1_stp_profile and other setpoint profiles are available in PSS/E and understood
44 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 84 | 0 | 1 | 0.2 | no | no | 166 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
45 | Q_stp_profile | MAT_QREF_STEP_Fig4.1 | [6 empty] | 78 | 0 | 1 | 0.2 | no | no | 166 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
46 | P_stp_profile | MAT_P_STEP_Fig5 | [6 empty] | 25 | 0 | 1 | 0.2 | no | no | 167 | Active Power Controller Reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
47 | P_stp_profile | MAT_P_STEP_Fig5 | [6 empty] | 13 | 0 | 1 | 0.2 | no | no | 168 | Active Power Controller Reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
48 | P_stp_profile | MAT_P_STEP_Fig5 | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 169 | Active Power Controller Reference step change [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
49 | P1_stp_profile | MAT_P_STEP_Fig5_BESS | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 169 | Active Power Controller Reference step change [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
50 | F_profile | F_PROFILE_Fig6_1 | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 170 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
51 | F_profile | F_PROFILE_Fig6_2 | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 170 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
52 | F_profile | F_PROFILE_Fig6_3 | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 170 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
53 | F_profile | F_PROFILE_Fig6_4 | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 170 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
54 | F_profile | F_PROFILE_Fig6_1 | [6 empty] | 418 | 0 | 1 | 0.2 | yes | yes | 171 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
55 | F_profile | F_PROFILE_Fig6_2 | [6 empty] | 418 | 0 | 1 | 0.2 | yes | yes | 171 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
56 | F_profile | F_PROFILE_Fig6_3 | [6 empty] | 418 | 0 | 1 | 0.2 | yes | yes | 171 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
57 | F_profile | F_PROFILE_Fig6_4 | [6 empty] | 418 | 0 | 1 | 0.2 | yes | yes | 171 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
58 | F_profile | F_PROFILE_Fig6_1 | [6 empty] | 408 | 0 | 1 | 0.2 | no | no | 172 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
59 | F_profile | F_PROFILE_Fig6_2 | [6 empty] | 408 | 0 | 1 | 0.2 | no | no | 172 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
60 | F_profile | F_PROFILE_Fig6_3 | [6 empty] | 408 | 0 | 1 | 0.2 | no | no | 172 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
61 | F_profile | F_PROFILE_Fig6_4 | [6 empty] | 408 | 0 | 1 | 0.2 | no | no | 172 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
62 | F_profile | F_PROFILE_Fig6_1 | [6 empty] | 41 | 0 | 1 | 0.2 | yes | yes | 173 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
63 | F_profile | F_PROFILE_Fig6_2 | [6 empty] | 41 | 0 | 1 | 0.2 | yes | yes | 173 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
64 | F_profile | F_PROFILE_Fig6_3 | [6 empty] | 41 | 0 | 1 | 0.2 | yes | yes | 173 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
65 | F_profile | F_PROFILE_Fig6_4 | [6 empty] | 41 | 0 | 1 | 0.2 | yes | yes | 173 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
66 | F_profile | F_PROFILE_Fig7_1 | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 174 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
67 | F_profile | F_PROFILE_Fig7_2 | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 174 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
68 | F_profile | F_PROFILE_Fig7_1 | [6 empty] | 418 | 0 | 1 | 0.2 | yes | yes | 175 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
69 | F_profile | F_PROFILE_Fig7_2 | [6 empty] | 418 | 0 | 1 | 0.2 | yes | yes | 175 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
70 | F_profile | F_PROFILE_Fig7_1 | [6 empty] | 408 | 0 | 1 | 0.2 | no | no | 176 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
71 | F_profile | F_PROFILE_Fig7_2 | [6 empty] | 408 | 0 | 1 | 0.2 | no | no | 176 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
72 | F_profile | F_PROFILE_Fig7_1 | [6 empty] | 41 | 0 | 1 | 0.2 | yes | yes | 177 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
73 | F_profile | F_PROFILE_Fig7_2 | [6 empty] | 41 | 0 | 1 | 0.2 | yes | yes | 177 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
74 | F_profile | F_PROFILE_Fig6_1 | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 170 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
75 | F_profile | F_PROFILE_Fig6_2 | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 170 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
76 | F_profile | F_PROFILE_Fig6_3 | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 170 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
77 | F_profile | F_PROFILE_Fig6_4 | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 170 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
78 | F_profile | F_PROFILE_Fig6_1 | [6 empty] | 407 | 0 | 1 | 0.2 | no | no | 171 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
79 | F_profile | F_PROFILE_Fig6_2 | [6 empty] | 407 | 0 | 1 | 0.2 | no | no | 171 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
80 | F_profile | F_PROFILE_Fig6_3 | [6 empty] | 407 | 0 | 1 | 0.2 | no | no | 171 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
81 | F_profile | F_PROFILE_Fig6_4 | [6 empty] | 407 | 0 | 1 | 0.2 | no | no | 171 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
82 | F_profile | F_PROFILE_Fig6_1 | [6 empty] | P=0.5 | 0 | 1 | 0.2 | no | no | 172 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
83 | F_profile | F_PROFILE_Fig6_2 | [6 empty] | P=0.5 | 0 | 1 | 0.2 | no | no | 172 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
84 | F_profile | F_PROFILE_Fig6_3 | [6 empty] | P=0.5 | 0 | 1 | 0.2 | no | no | 172 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
85 | F_profile | F_PROFILE_Fig6_4 | [6 empty] | P=0.5 | 0 | 1 | 0.2 | no | no | 172 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
86 | F_profile | F_PROFILE_Fig6_1 | [6 empty] | 71 | 0 | 1 | 0.2 | no | no | 173 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
87 | F_profile | F_PROFILE_Fig6_2 | [6 empty] | 71 | 0 | 1 | 0.2 | no | no | 173 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
88 | F_profile | F_PROFILE_Fig6_3 | [6 empty] | 71 | 0 | 1 | 0.2 | no | no | 173 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
89 | F_profile | F_PROFILE_Fig6_4 | [6 empty] | 71 | 0 | 1 | 0.2 | no | no | 173 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
90 | F_profile | F_PROFILE_Fig7_1 | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 174 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
91 | F_profile | F_PROFILE_Fig7_2 | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 174 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
92 | F_profile | F_PROFILE_Fig7_1 | [6 empty] | 407 | 0 | 1 | 0.2 | no | no | 175 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
93 | F_profile | F_PROFILE_Fig7_2 | [6 empty] | 407 | 0 | 1 | 0.2 | no | no | 175 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
94 | F_profile | F_PROFILE_Fig7_1 | [6 empty] | P=0.5 | 0 | 1 | 0.2 | no | no | 176 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
95 | F_profile | F_PROFILE_Fig7_2 | [6 empty] | P=0.5 | 0 | 1 | 0.2 | no | no | 176 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
96 | F_profile | F_PROFILE_Fig7_1 | [6 empty] | 71 | 0 | 1 | 0.2 | no | no | 177 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
97 | F_profile | F_PROFILE_Fig7_2 | [6 empty] | 71 | 0 | 1 | 0.2 | no | no | 177 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS | Need to initialise with High P, then reduce to low level before applying Frequency Disturbance
98 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 25 | 0 | 1 | 0.2 | no | no | 178 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
99 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 178 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
100 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 13 | 0 | 1 | 0.2 | no | no | 179 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
101 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 180 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
102 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 418 | 0 | 1 | 0.2 | yes | yes | 181 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
103 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 180 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
104 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 407 | 0 | 1 | 0.2 | no | no | 181 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
105 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 68 | 0 | 1 | 0.2 | no | no | 181 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
106 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 25 | 0 | 1 | 0.2 | no | no | 182 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
107 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 182 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
108 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 13 | 0 | 1 | 0.2 | no | no | 183 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
109 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 19 | 0 | 1 | 0.2 | no | no | 183 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
110 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 184 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
111 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 41 | 0 | 1 | 0.2 | yes | yes | 185 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
112 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 184 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
113 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 71 | 0 | 1 | 0.2 | no | no | 185 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
114 | V_profile | MAT_V_STEP_Fig10.1 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 25 | 0 | 1 | 0.2 | no | no | 186 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
115 | V_profile | MAT_V_STEP_Fig10.1 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 186 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
116 | V_profile | MAT_V_STEP_Fig10.1 | [6 empty] | 13 | 0 | 1 | 0.2 | no | no | 187 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
117 | V_profile | MAT_V_STEP_Fig10.1 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 19 | 0 | 1 | 0.2 | no | no | 187 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
118 | V_profile | MAT_V_STEP_Fig10.1 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 36 | 0 | 1 | 0.2 | yes | yes | 188 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
119 | V_profile | MAT_V_STEP_Fig10.1 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 41 | 0 | 1 | 0.2 | yes | yes | 189 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
120 | V_profile | MAT_V_STEP_Fig10.1 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 66 | 0 | 1 | 0.2 | no | no | 188 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
121 | V_profile | MAT_V_STEP_Fig10.1 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 71 | 0 | 1 | 0.2 | no | no | 189 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
122 | V_profile | MAT_V_STEP_Fig10.2 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 25 | 0 | 1 | 0.2 | no | no | 186 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
123 | V_profile | MAT_V_STEP_Fig10.2 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 186 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
124 | V_profile | MAT_V_STEP_Fig10.2 | [6 empty] | 13 | 0 | 1 | 0.2 | no | no | 187 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
125 | V_profile | MAT_V_STEP_Fig10.2 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 19 | 0 | 1 | 0.2 | no | no | 187 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
126 | V_profile | MAT_V_STEP_Fig10.2 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 7 | 0 | 1 | 0.2 | no | no | 188 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
127 | V_profile | MAT_V_STEP_Fig10.2 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 67 | 0 | 1 | 0.2 | no | no | 188 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
128 | V_profile | MAT_V_STEP_Fig10.2 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 1 | 0 | 1 | 0.2 | no | no | 189 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
129 | V_profile | MAT_V_STEP_Fig10.2 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 68 | 0 | 1 | 0.2 | no | no | 189 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
130 | V_profile | MAT_V_STEP_Fig10.3 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 25 | 0 | 1 | 0.2 | no | no | 186 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
131 | V_profile | MAT_V_STEP_Fig10.3 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 186 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
132 | V_profile | MAT_V_STEP_Fig10.3 | [6 empty] | 13 | 0 | 1 | 0.2 | no | no | 187 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
133 | V_profile | MAT_V_STEP_Fig10.3 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 19 | 0 | 1 | 0.2 | no | no | 187 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
134 | V_profile | MAT_V_STEP_Fig10.3 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 7 | 0 | 1 | 0.2 | no | no | 188 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
135 | V_profile | MAT_V_STEP_Fig10.3 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 67 | 0 | 1 | 0.2 | no | no | 188 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
136 | V_profile | MAT_V_STEP_Fig10.3 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 1 | 0 | 1 | 0.2 | no | no | 189 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
137 | V_profile | MAT_V_STEP_Fig10.3 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 68 | 0 | 1 | 0.2 | no | no | 189 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
138 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 25 | 0 | 1 | 0.2 | no | no | 193 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
139 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 193 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
140 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 28 | 0 | 1 | 0.2 | no | no | 194 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
141 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 34 | 0 | 1 | 0.2 | no | no | 194 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
142 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 13 | 0 | 1 | 0.2 | no | no | 195 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
143 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 19 | 0 | 1 | 0.2 | no | no | 195 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
144 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 16 | 0 | 1 | 0.2 | no | no | 196 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
145 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 22 | 0 | 1 | 0.2 | no | no | 196 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
146 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 197 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
147 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 197 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
148 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 4 | 0 | 1 | 0.2 | no | no | 198 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
149 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 10 | 0 | 1 | 0.2 | no | no | 198 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
150 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 25 | 0 | 1 | 0.2 | no | no | 193 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
151 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 193 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
152 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 28 | 0 | 1 | 0.2 | no | no | 194 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
153 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 34 | 0 | 1 | 0.2 | no | no | 194 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
154 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 13 | 0 | 1 | 0.2 | no | no | 195 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
155 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 19 | 0 | 1 | 0.2 | no | no | 195 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
156 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 16 | 0 | 1 | 0.2 | no | no | 196 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
157 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 22 | 0 | 1 | 0.2 | no | no | 196 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
158 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes | 197 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
159 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 197 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
160 | P_stp_profile | MAT_P_STEP_Fig12 | [6 empty] | 420 | 0 | 1 | 0.2 | yes | yes | 199 | POC SCR = 1 Active Power reference change test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
161 | P_stp_profile | MAT_P_STEP_Fig12 | [6 empty] | 422 | 0 | 1 | 0.2 | yes | yes | 199 | POC SCR = 1 Active Power reference change test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
162 | P1_stp_profile | MAT_P_STEP_Fig12_BESS | [6 empty] | 411 | 0 | 1 | 0.2 | no | no | 199 | POC SCR = 1 Active Power reference change test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
163 | P1_stp_profile | MAT_P_STEP_Fig12_BESS | [6 empty] | 413 | 0 | 1 | 0.2 | no | no | 199 | POC SCR = 1 Active Power reference change test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
164 | Auxiliary_profile | AVAIL_P_-20% | [6 empty] | 428 | 0 | 1 | 0.2 | yes | yes | 226 | Input power source step change test | DMAT_SELF_ALL | no relevance for BESS alone, because no limit
165 | Auxiliary_profile | AVAIL_P_-20% | [6 empty] | 1 | 0 | 1 | 0.2 | no | no | 227 | Input power source step change test | DMAT
166 | Auxiliary_profile | AVAIL_P_+20% | [6 empty] | 418 | 0 | 1 | 0.2 | yes | yes | 228 | Input power source step change test | DMAT_SELF_ALL | no relevance for BESS alone, because no limit. Increase Pavail and show that no increase.
167 | Auxiliary_profile | AVAIL_P_+20% | [6 empty] | 68 | 0 | 1 | 0.2 | no | no | 229 | Input power source step change test | DMAT
168 | V_stp_profile | S52513_V0+/-5% | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
169 | V_stp_profile | S52513_V0+/-5% | [6 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
170 | Q_stp_profile | S52513_Q0+/-15 | [6 empty] | 306 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
171 | Q_stp_profile | S52513_Q0+/-15 | [6 empty] | 351 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
172 | PF_stp_profile | S52513_PF0+/-1% | [6 empty] | 396 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
173 | PF_stp_profile | S52513_PF0+/-1% | [6 empty] | 216 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
174 | V_profile | V_STEP_+/-5% | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
175 | V_profile | V_STEP_+/-5% | [6 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
176 | P_stp_profile | S52514_-/+50% | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
177 | P_stp_profile | S52514_-/+50% | [6 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
178 | F_profile | S52511_+/-1Hz | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
179 | F_profile | S52511_+/-1Hz | [6 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
180 | ANG_profile | MAT_ANG_STEP | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
181 | ANG_profile | MAT_ANG_STEP | [6 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
182 | Auxiliary_profile | AVAIL_P_-20% | [6 empty] | 428 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
183 | Auxiliary_profile | AVAIL_P_-20% | [6 empty] | 429 | 0 | 1 | 0.2 | yes | yes |  |  | BENCHMARKING_ALL
184 | V_stp_profile | S52513_V0+/-5% | [6 empty] | 21 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
185 | V_stp_profile | S52513_V0+/-5% | [6 empty] | 66 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
186 | Q_stp_profile | S52513_Q0+/-15BM | [6 empty] | 291 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
187 | Q_stp_profile | S52513_Q0+/-15BM | [6 empty] | 336 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
188 | PF_stp_profile | S52513_PF0+/-2% | [6 empty] | 381 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
189 | PF_stp_profile | S52513_PF0+/-2% | [6 empty] | 201 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
190 | V_profile | V_STEP_+/-5% | [6 empty] | 21 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
191 | V_profile | V_STEP_+/-5% | [6 empty] | 66 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
192 | P_stp_profile | S52514_-/+50% | [6 empty] | 21 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
193 | P_stp_profile | S52514_-/+50% | [6 empty] | 66 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
194 | F_profile | S52511_+/-1Hz | [6 empty] | 21 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
195 | F_profile | S52511_+/-1Hz | [6 empty] | 66 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
196 | ANG_profile | MAT_ANG_STEP | [6 empty] | 21 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
197 | ANG_profile | MAT_ANG_STEP | [6 empty] | 66 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
198 | Auxiliary_profile | AVAIL_P_-20% | [6 empty] | 21 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
199 | Auxiliary_profile | AVAIL_P_-20% | [6 empty] | 66 | 0 | 1 | 0.2 | no | no |  |  | BENCHMARKING_BESS
200 | F_profile | S5253_UF_short | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5253_ALL | Min SCR PmaxQ0 _BESS=0
201 | F_profile | S5253_OF_short | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5253_ALL | Min SCR PmaxQ0_BESS=0
202 | F_profile | S5253_UF_short | [6 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5253_ALL | Max SCR PmaxQ0 _BESS=0
203 | F_profile | S5253_OF_short | [6 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5253_ALL | Max SCR PmaxQ0_BESS=0
204 | F_profile | S5253_UF_short | [6 empty] | 6 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253_ALL | Min SCR PmaxQ0_BESS=50
205 | F_profile | S5253_OF_short | [6 empty] | 6 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253_ALL | Min SCR PmaxQ0_BESS=50
206 | F_profile | S5253_UF_short | [6 empty] | 51 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253_ALL | Max SCR PmaxQ0_BESS=50
207 | F_profile | S5253_OF_short | [6 empty] | 51 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253_ALL | Max SCR PmaxQ0_BESS=50
208 | F_profile | S5253_UF | [6 empty] | 271 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253_ALL | Min SCR PmaxQ0 _BESS=0
209 | F_profile | S5253_OF | [6 empty] | 271 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253_ALL | Min SCR PmaxQ0_BESS=0
210 | F_profile | S5253_UF | [6 empty] | 316 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253_ALL | Max SCR PmaxQ0 _BESS=0
211 | F_profile | S5253_OF | [6 empty] | 316 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253_ALL | Max SCR PmaxQ0_BESS=0
212 | F_profile | S5253_UF | [6 empty] | 276 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253_ALL | Min SCR PmaxQ0_BESS=50
213 | F_profile | S5253_OF | [6 empty] | 276 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253_ALL | Min SCR PmaxQ0_BESS=50
214 | F_profile | S5253_UF | [6 empty] | 321 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253_ALL | Max SCR PmaxQ0_BESS=50
215 | F_profile | S5253_OF | [6 empty] | 321 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253_ALL | Max SCR PmaxQ0_BESS=50
216 | F_profile | S5253_UF | [6 empty] | 361 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253_ALL | Min SCR PmaxQ0 _BESS=0
217 | F_profile | S5253_OF | [6 empty] | 361 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253_ALL | Min SCR PmaxQ0_BESS=0
218 | F_profile | S5253_UF | [6 empty] | 181 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253_ALL | Max SCR PmaxQ0 _BESS=0
219 | F_profile | S5253_OF | [6 empty] | 181 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253_ALL | Max SCR PmaxQ0_BESS=0
220 | F_profile | S5253_UF | [6 empty] | 366 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253_ALL | Min SCR PmaxQ0_BESS=50
221 | F_profile | S5253_OF | [6 empty] | 366 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253_ALL | Min SCR PmaxQ0_BESS=50
222 | F_profile | S5253_UF | [6 empty] | 186 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253_ALL | Max SCR PmaxQ0_BESS=50
223 | F_profile | S5253_OF | [6 empty] | 186 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253_ALL | Max SCR PmaxQ0_BESS=50
224 | F_profile | S5253_UF_short | [6 empty] | 21 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253_BESS | Min SCR, PmaxQ0
225 | F_profile | S5253_OF_short | [6 empty] | 21 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253_BESS | Min SCR, PmaxQ0
226 | F_profile | S5253_UF_short | [6 empty] | 66 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253_BESS | Max SCR, PmaxQ0
227 | F_profile | S5253_OF_short | [6 empty] | 66 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253_BESS | Max SCR, PmaxQ0
228 | F_profile | S5253_UF | [6 empty] | 155 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253_BESS
229 | F_profile | S5253_OF | [6 empty] | 155 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253_BESS
230 | F_profile | S5253_UF | [6 empty] | 161 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253_BESS
231 | F_profile | S5253_OF | [6 empty] | 161 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253_BESS
232 | F_profile | S5253_UF | [6 empty] | 167 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253_BESS
233 | F_profile | S5253_OF | [6 empty] | 167 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253_BESS
234 | F_profile | S5253_UF | [6 empty] | 173 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253_BESS
235 | F_profile | S5253_OF | [6 empty] | 173 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253_BESS
236 | F_profile | S5253_UF_short | [6 empty] | 31 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253_BESS | Min SCR, PminQ0, charging
237 | F_profile | S5253_OF_short | [6 empty] | 31 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253_BESS | Min SCR, PminQ0, charging
238 | F_profile | S5253_UF_short | [6 empty] | 76 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253_BESS | Max SCR, PminQ0, charging
239 | F_profile | S5253_OF_short | [6 empty] | 76 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253_BESS | Max SCR, PminQ0, charging
240 | F_profile | S5253_UF | [6 empty] | 155 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253_BESS
241 | F_profile | S5253_OF | [6 empty] | 155 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253_BESS
242 | F_profile | S5253_UF | [6 empty] | 161 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253_BESS
243 | F_profile | S5253_OF | [6 empty] | 161 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253_BESS
244 | F_profile | S5253_UF | [6 empty] | 167 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253_BESS
245 | F_profile | S5253_OF | [6 empty] | 167 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253_BESS
246 | F_profile | S5253_UF | [6 empty] | 173 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253_BESS
247 | F_profile | S5253_OF | [6 empty] | 173 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253_BESS
248 | V_profile | S5254_LVRT | [6 empty] | 130 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5254_ALL | inf Grid PmaxQmin; Bes=0
249 | V_profile | S5254_HVRT | [6 empty] | 129 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5254_ALL | inf Grid PmaxQmax Bes=0
250 | V_profile | S5254_LVRT | [6 empty] | 100 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254_ALL | inf Grid PmaxQmin; Bes=50
251 | V_profile | S5254_HVRT | [6 empty] | 99 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254_ALL | inf Grid PmaxQmax Bes=50
252 | V_profile | S5254_LVRT_REL | [6 empty] | 40 | 1 | 1 | 0.2 | yes | yes |  | V control mode | S5254_ALLdbg | min SCR PmaxQmin; Bes=0
253 | V_profile | S5254_HVRT_REL | [6 empty] | 39 | 1 | 1 | 0.2 | yes | yes |  | V control mode | S5254_ALLdbg | min SCR Grid PmaxQmax Bes=0
254 | V_profile | S5254_LVRT_REL | [6 empty] | 10 | 1 | 1 | 0.2 | no | no |  | V control mode | S5254_ALL | min Grid PmaxQmin; Bes=50
255 | V_profile | S5254_HVRT_REL | [6 empty] | 9 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254_ALL | min Grid PmaxQmax Bes=50
256 | V_profile | S5254_LVRT | [6 empty] | 265 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S5254_ALL | inf Grid PmaxQmin; Bes=0
257 | V_profile | S5254_HVRT | [6 empty] | 264 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S5254_ALL | inf Grid PmaxQmax Bes=0
258 | V_profile | S5254_LVRT | [6 empty] | 235 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254_ALL | inf Grid PmaxQmin; Bes=50
259 | V_profile | S5254_HVRT | [6 empty] | 234 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254_ALL | inf Grid PmaxQmax Bes=50
260 | V_profile | S5254_LVRT_REL | [6 empty] | 310 | 1 | 1 | 0.2 | yes | yes |  | Q control mode | S5254_ALLdbg | min SCR PmaxQmin; Bes=0
261 | V_profile | S5254_HVRT_REL | [6 empty] | 309 | 1 | 1 | 0.2 | yes | yes |  | Q control mode | S5254_ALLdbg | min SCR Grid PmaxQmax Bes=0
262 | V_profile | S5254_LVRT_REL | [6 empty] | 280 | 1 | 1 | 0.2 | no | no |  | Q control mode | S5254_ALL | min Grid PmaxQmin; Bes=50
263 | V_profile | S5254_HVRT_REL | [6 empty] | 279 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254_ALL | min Grid PmaxQmax Bes=50
264 | V_profile | S5254_110_CUO | [6 empty] | 130 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5254_ALL | inf Grid PmaxQmax; Bes=0
265 | V_profile | S5254_090_CUO | [6 empty] | 129 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5254_ALL | inf Grid PmaxQmin Bes=0
266 | V_profile | S5254_110_CUO | [6 empty] | 99 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254_ALL | inf Grid PmaxQmax; Bes=50
267 | V_profile | S5254_090_CUO | [6 empty] | 100 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254_ALL | inf Grid PmaxQmin Bes=50
268 | V_profile | S5254_110_CUO | [6 empty] | 265 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S5254_ALL | inf Grid PmaxQmax; Bes=0
269 | V_profile | S5254_090_CUO | [6 empty] | 264 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S5254_ALL | inf Grid PmaxQmin Bes=0
270 | V_profile | S5254_110_CUO | [6 empty] | 234 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254_ALL | inf Grid PmaxQmax; Bes=50
271 | V_profile | S5254_090_CUO | [6 empty] | 235 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254_ALL | inf Grid PmaxQmin Bes=50
272 | V_profile | S5254_LVRT | [6 empty] | 115 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254_BESS | inf Grid PmaxQmin
273 | V_profile | S5254_HVRT | [6 empty] | 114 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254_BESS | inf Grid PmaxQmax
274 | V_profile | S5254_LVRT_REL | [6 empty] | 25 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254_BESS_DBG | min SCR PmaxQmin
275 | V_profile | S5254_HVRT_REL | [6 empty] | 24 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254_BESS_DBG | min SCR PmaxQmax
276 | V_profile | S5254_LVRT | [6 empty] | 250 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254_BESS | inf Grid PmaxQmin
277 | V_profile | S5254_HVRT | [6 empty] | 249 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254_BESS | inf Grid PmaxQmax
278 | V_profile | S5254_LVRT_REL | [6 empty] | 295 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254_BESS_DBG | min SCR PmaxQmin
279 | V_profile | S5254_HVRT_REL | [6 empty] | 294 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254_BESS_DBG | min SCR PmaxQmax
280 | V_profile | S5254_110_CUO | [6 empty] | 114 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254_BESS | inf Grid PmaxQmax
281 | V_profile | S5254_090_CUO | [6 empty] | 115 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254_BESS | inf Grid PmaxQmin
282 | V_profile | S5254_110_CUO | [6 empty] | 249 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254_BESS | inf Grid PmaxQmax
283 | V_profile | S5254_090_CUO | [6 empty] | 250 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254_BESS | inf Grid PmaxQmin
284 | V_profile | S5254_LVRT | [6 empty] | 125 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254_BESS | inf Grid PminQmin, charging
285 | V_profile | S5254_HVRT | [6 empty] | 124 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254_BESS | inf Grid PminQmax, charging
286 | V_profile | S5254_LVRT_REL | [6 empty] | 35 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254_BESS_DBG | min SCR PminQmin, charging
287 | V_profile | S5254_HVRT_REL | [6 empty] | 34 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254_BESS_DBG | min SCR PminQmax, charging
288 | V_profile | S5254_LVRT | [6 empty] | 260 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254_BESS | inf Grid PminQmin, charging
289 | V_profile | S5254_HVRT | [6 empty] | 259 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254_BESS | inf Grid PminQmax, charging
290 | V_profile | S5254_LVRT_REL | [6 empty] | 305 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254_BESS_DBG | min SCR PminQmin, charging
291 | V_profile | S5254_HVRT_REL | [6 empty] | 304 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254_BESS_DBG | min SCR PminQmax, charging
292 | V_profile | S5254_110_CUO | [6 empty] | 124 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254_BESS | inf Grid PminQmax, charging
293 | V_profile | S5254_090_CUO | [6 empty] | 125 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254_BESS | inf Grid PminQmin, charging
294 | V_profile | S5254_110_CUO | [6 empty] | 159 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254_BESS | inf Grid PminQmax, charging
295 | V_profile | S5254_090_CUO | [6 empty] | 260 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254_BESS | inf Grid PminQmin, charging
296 | F_profile | S5257_OF_ShedLoad | [6 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  | V control mode. | S5257_ALL | nom SCR PmaxQ0 Bes=0
297 | F_profile | S5257_OF_ShedLoad | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5257_ALL | min SCR PmaxQ0 Bes=0
298 | F_profile | S5257_OF_ShedLoad | [6 empty] | 51 | 0 | 1 | 0.2 | no | no |  | V control mode | S5257_ALL | nom SCR PmaxQ0 Bes=50
299 | F_profile | S5257_OF_ShedLoad | [6 empty] | 6 | 0 | 1 | 0.2 | no | no |  | V control mode | S5257_ALL | min SCR PmqxQ0 Bes=50
300 | F_profile | S5257_OF_ShedLoad | [6 empty] | 66 | 0 | 1 | 0.2 | no | no |  | V control mode. | S5257_BESS | nom SCR PmaxQ0 | This is about reducing output, so no need to test in load mode
301 | F_profile | S5257_OF_ShedLoad | [6 empty] | 21 | 0 | 1 | 0.2 | no | no |  | V control mode | S5257_BESS | min SCR PmaxQ0
302 | F_profile | S5257_OF_ShedLoad | [6 empty] | 143 | 0 | 1 | 0.2 | no | no |  | V control mode | S5257_BESS | nom SCR PmaxQ0 Bes=-50, charging
303 | F_profile | S5257_OF_ShedLoad | [6 empty] | 149 | 0 | 1 | 0.2 | no | no |  | V control mode | S5257_BESS | min SCR PmqxQ0 Bes=-50, charging
304 | F_profile | UF_TRIP | [6 empty] | 126 | 0 | 1 | 0.2 | yes | yes |  |  | S5258_ALL | INF grid PmaxQ0, bes=0
305 | F_profile | OF_TRIP | [6 empty] | 126 | 0 | 1 | 0.2 | yes | yes |  |  | S5258_ALL | INF grid PmaxQ0, bes=0
306 | V_profile | LV_TRIP | [6 empty] | 126 | 0 | 1 | 0.2 | yes | yes |  |  | S5258_ALL | INF grid PmaxQ0, bes=0
307 | V_profile | HV_TRIP | [6 empty] | 126 | 0 | 1 | 0.2 | yes | yes |  |  | S5258_ALL | INF grid PmaxQ0, bes=0
308 | F_profile | UF_TRIP | [6 empty] | 6 | 0 |  |  | no | no |  |  | S5258_BESS | INF grid, PmaxQ0, bes only
309 | F_profile | OF_TRIP | [6 empty] | 111 | 0 |  |  | no | no |  |  | S5258_BESS | INF grid, PmaxQ0, bes only
310 | V_profile | LV_TRIP | [6 empty] | 111 | 0 |  |  | no | no |  |  | S5258_BESS | INF grid, PmaxQ0, bes only
311 | V_profile | HV_TRIP | [6 empty] | 111 | 0 |  |  | no | no |  |  | S5258_BESS | INF grid, PmaxQ0, bes only
312 | F_profile | S52511_F_db | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52511_ALL | Min SCR, pmaxQ0, Bes=0 | Because we are not messing with voltage the control mode is not that important
313 | F_profile | S52511_+/-1Hz | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52511_ALL | Min SCR, pmaxQ0, Bes=0
314 | F_profile | S52511_F_db | [6 empty] | 6 | 0 | 1 | 0.2 | no | no |  | V control mode | S52511_ALL | Min SCR, PmaxQ0, Bes=50
315 | F_profile | S52511_+/-1Hz | [6 empty] | 6 | 0 | 1 | 0.2 | no | no |  | V control mode | S52511_ALL | Min SCR, PmaxQ0, Bes=50
316 | F_profile | S52511_F_db | [6 empty] | 41 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52511_ALL | Min SCR, P0Q0, Bes=0
317 | F_profile | S52511_+/-1Hz | [6 empty] | 41 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52511_ALL | Min SCR, P0Q0, Bes=0
318 | F_profile | S52511_F_db | [6 empty] | 16 | 0 | 1 | 0.2 | no | no |  | V control mode | S52511_ALL | Min SCR, PminQ0, Bes=-50
319 | F_profile | S52511_+/-1Hz | [6 empty] | 16 | 0 | 1 | 0.2 | no | no |  | V control mode | S52511_ALL | Min SCR, PminQ0, Bes=-50
320 | F_profile | S52511_F_db | [6 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52511_ALL | Max SCR, pmaxQ0, Bes=0
321 | F_profile | S52511_+/-1Hz | [6 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52511_ALL | Max SCR, pmaxQ0, Bes=0
322 | F_profile | S52511_F_db | [6 empty] | 51 | 0 | 1 | 0.2 | no | no |  | V control mode | S52511_ALL | Max SCR, PmaxQ0, Bes=50
323 | F_profile | S52511_+/-1Hz | [6 empty] | 51 | 0 | 1 | 0.2 | no | no |  | V control mode | S52511_ALL | Max SCR, PmaxQ0, Bes=50
324 | F_profile | S52511_F_db | [6 empty] | 86 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52511_ALL | Max SCR, P0Q0, Bes=0
325 | F_profile | S52511_+/-1Hz | [6 empty] | 86 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52511_ALL | Max SCR, P0Q0, Bes=0
326 | F_profile | S52511_F_db | [6 empty] | 61 | 0 | 1 | 0.2 | no | no |  | V control mode | S52511_ALL | Max SCR, PminQ0, Bes=-50
327 | F_profile | S52511_+/-1Hz | [6 empty] | 61 | 0 | 1 | 0.2 | no | no |  | V control mode | S52511_ALL | Max SCR, PminQ0, Bes=-50
328 | F_profile | S52511_F_db | [6 empty] | 21 | 0 | 1 | 0.2 | no | no |  | V control mode | S52511_BESS | Min SCR, pmaxQ0, Bes=50
329 | F_profile | S52511_+/-1Hz | [6 empty] | 21 | 0 | 1 | 0.2 | no | no |  | V control mode | S52511_BESS | Min SCR, pmaxQ0, Bes=50
330 | F_profile | S52511_F_db | [6 empty] | 31 | 0 | 1 | 0.2 | no | no |  | V control mode | S52511_BESS | Min SCR, PminQ0, Bes=-50
331 | F_profile | S52511_+/-1Hz | [6 empty] | 31 | 0 | 1 | 0.2 | no | no |  | V control mode | S52511_BESS | Min SCR, PminQ0, Bes=-50
332 | F_profile | S52511_F_db | [6 empty] | 66 | 0 | 1 | 0.2 | no | no |  | V control mode | S52511_BESS | Max SCR, pmaxQ0, Bes=50
333 | F_profile | S52511_+/-1Hz | [6 empty] | 66 | 0 | 1 | 0.2 | no | no |  | V control mode | S52511_BESS | Max SCR, pmaxQ0, Bes=50
334 | F_profile | S52511_F_db | [6 empty] | 76 | 0 | 1 | 0.2 | no | no |  | V control mode | S52511_BESS | Max SCR, PminQ0, Bes=-50
335 | F_profile | S52511_+/-1Hz | [6 empty] | 76 | 0 | 1 | 0.2 | no | no |  | V control mode | S52511_BESS | Max SCR, PminQ0, Bes=-50
336 | V_stp_profile | S52513_V0+/-5% | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  |  | S52513_ALL | Min SCR, PmaxQ0, Bes=0
337 | V_stp_profile | S52513_Vmax-2.5%/+5% | [6 empty] | 39 | 1 | 1 | 0.2 | yes | yes |  | reducing setpoint and then driving plant into upper Q limit | S52513_ALL | Min SCR, PmaxQmax, bes=0
338 | V_stp_profile | S52513_Vmin+2.5%/-5% | [6 empty] | 40 | 1 | 1 | 0.2 | yes | yes |  | increasing setpoitn and then stepping down, driving plant into lower limit | S52513_ALL | Min SCR, PmaxQmin, bes=0
339 | V_stp_profile | S52513_V0+/-5% | [6 empty] | 6 | 0 | 1 | 0.2 | no | no |  |  | S52513_ALL | Min SCR, PmaxQ0, Bes=50
340 | V_stp_profile | S52513_Vmax-2.5%/+5% | [6 empty] | 9 | 0 | 1 | 0.2 | no | no |  |  | S52513_ALL | Min SCR, PmaxQmax, bes=50
341 | V_stp_profile | S52513_Vmin+2.5%/-5% | [6 empty] | 10 | 0 | 1 | 0.2 | no | no |  |  | S52513_ALL | Min SCR, PmaxQmin, bes=50
342 | V_stp_profile | S52513_V0+/-5% | [6 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  |  | S52513_ALL | Max SCR, PmaxQ0, Bes=0
343 | V_stp_profile | S52513_Vmax-2.5%/+5% | [6 empty] | 84 | 1 | 1 | 0.2 | yes | yes |  | reducing setpoint and then driving plant into upper Q limit | S52513_ALL | Max SCR, PmaxQmax, bes=0
344 | V_stp_profile | S52513_Vmin+2.5%/-5% | [6 empty] | 85 | 1 | 1 | 0.2 | yes | yes |  | increasing setpoitn and then stepping down, driving plant into lower limit | S52513_ALL | Max SCR, PmaxQmin, bes=0
345 | V_stp_profile | S52513_V0+/-5% | [6 empty] | 51 | 0 | 1 | 0.2 | no | no |  |  | S52513_ALL | Max SCR, PmaxQ0, Bes=50
346 | V_stp_profile | S52513_Vmax-2.5%/+5% | [6 empty] | 54 | 0 | 1 | 0.2 | no | no |  |  | S52513_ALL | Max SCR, PmaxQmax, bes=50
347 | V_stp_profile | S52513_Vmin+2.5%/-5% | [6 empty] | 55 | 0 | 1 | 0.2 | no | no |  |  | S52513_ALL | Max SCR, PmaxQmin, bes=50
348 | Q_stp_profile | S52513_Q0+/-15 | [6 empty] | 306 | 0 | 1 | 0.2 | yes | yes |  | Qctrl | S52513_ALL | Min SCR, PmaxQ0, Bes=0 | step only PV profiles
349 | Q_stp_profile | S52513_Qmax-10/+20 | [6 empty] | 309 | 1 | 1 | 0.2 | yes | yes |  | Qctrl | S52513_ALL | Min SCR, PmaxQmax, bes=0
350 | Q_stp_profile | S52513_Qmin+10/-20 | [6 empty] | 310 | 1 | 1 | 0.2 | yes | yes |  | Qctrl | S52513_ALL | Min SCR, PmaxQmin, bes=0
351 | Q_stp_profile | S52513_Q0+/-15 | [6 empty] | 276 | 0 | 1 | 0.2 | no | no |  | Qctrl | S52513_ALL | Min SCR, PmaxQ0, Bes=50
352 | Q_stp_profile | S52513_Qmax-10/+20 | [6 empty] | 279 | 1 | 1 | 0.2 | no | no |  | Qctrl | S52513_ALL | Min SCR, PmaxQmax, bes=50
353 | Q_stp_profile | S52513_Qmin+10/-20 | [6 empty] | 280 | 1 | 1 | 0.2 | no | no |  | Qctrl | S52513_ALL | Min SCR, PmaxQmin, bes=50
354 | Q_stp_profile | S52513_Q0+/-15 | [6 empty] | 171 | 0 | 1 | 0.2 | yes | yes |  | Qctrl | S52513_ALL | Max SCR, PmaxQ0, Bes=0
355 | Q_stp_profile | S52513_Qmax-10/+20 | [6 empty] | 174 | 1 | 1 | 0.2 | yes | yes |  | Qctrl | S52513_ALL | Max SCR, PmaxQmax, bes=0
356 | Q_stp_profile | S52513_Qmin+10/-20 | [6 empty] | 175 | 1 | 1 | 0.2 | yes | yes |  | Qctrl | S52513_ALL | Max SCR, PmaxQmin, bes=0
357 | Q_stp_profile | S52513_Q0+/-15 | [6 empty] | 141 | 0 | 1 | 0.2 | no | no |  | Qctrl | S52513_ALL | Max SCR, PmaxQ0, Bes=50
358 | Q_stp_profile | S52513_Qmax-10/+20 | [6 empty] | 144 | 0 | 1 | 0.2 | no | no |  | Qctrl | S52513_ALL | Max SCR, PmaxQmax, bes=50
359 | Q_stp_profile | S52513_Qmin+10/-20 | [6 empty] | 145 | 0 | 1 | 0.2 | no | no |  | Qctrl | S52513_ALL | Max SCR, PmaxQmin, bes=50
360 | PF_stp_profile | S52513_PF0+/-1% | [6 empty] | 396 | 0 | 1 | 0.2 | yes | yes |  | PfCtrl | S52513_ALL | Min SCR, PmaxQ0, Bes=0
361 | PF_stp_profile | S52513_PFMax-0.5%/+1.5% | [6 empty] | 399 | 1 | 1 | 0.2 | yes | yes |  | PfCtrl | S52513_ALL | Min SCR, PmaxQmax, bes=0
362 | PF_stp_profile | S52513_PFMin+0.5%/-1.5% | [6 empty] | 400 | 1 | 1 | 0.2 | yes | yes |  | PfCtrl | S52513_ALL | Min SCR, PmaxQmin, bes=0
363 | PF_stp_profile | S52513_PF0+/-1% | [6 empty] | 366 | 0 | 1 | 0.2 | no | no |  | PfCtrl | S52513_ALL | Min SCR, PmaxQ0, Bes=50
364 | PF_stp_profile | S52513_PFMax-0.5%/+1.5% | [6 empty] | 369 | 0 | 1 | 0.2 | no | no |  | PfCtrl | S52513_ALL | Min SCR, PmaxQmax, bes=50
365 | PF_stp_profile | S52513_PFMin+0.5%/-1.5% | [6 empty] | 370 | 0 | 1 | 0.2 | no | no |  | PfCtrl | S52513_ALL | Min SCR, PmaxQmin, bes=50
366 | PF_stp_profile | S52513_PF0+/-1% | [6 empty] | 216 | 0 | 1 | 0.2 | yes | yes |  | PfCtrl | S52513_ALL | Max SCR, PmaxQ0, Bes=0
367 | PF_stp_profile | S52513_PFMax-0.5%/+1.5% | [6 empty] | 219 | 1 | 1 | 0.2 | yes | yes |  | PfCtrl | S52513_ALL | Max SCR, PmaxQmax, bes=0
368 | PF_stp_profile | S52513_PFMin+0.5%/-1.5% | [6 empty] | 220 | 1 | 1 | 0.2 | yes | yes |  | PfCtrl | S52513_ALL | Max SCR, PmaxQmin, bes=0
369 | PF_stp_profile | S52513_PF0+/-1% | [6 empty] | 186 | 0 | 1 | 0.2 | no | no |  | PfCtrl | S52513_ALL | Max SCR, PmaxQ0, Bes=50
370 | PF_stp_profile | S52513_PFMax-0.5%/+1.5% | [6 empty] | 189 | 0 | 1 | 0.2 | no | no |  | PfCtrl | S52513_ALL | Max SCR, PmaxQmax, bes=50
371 | PF_stp_profile | S52513_PFMin+0.5%/-1.5% | [6 empty] | 190 | 0 | 1 | 0.2 | no | no |  | PfCtrl | S52513_ALL | Max SCR, PmaxQmin, bes=50
372 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 36 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52513_ALL | Min SCR, PmaxQ0, bes=0
373 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 6 | 0 | 1 | 0.2 | no | no |  | V control mode | S52513_ALL | Min SCR, PmaxQ0, bes=50
374 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 81 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52513_ALL | Max SCR, PmaxQ0, bes=0
375 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 51 | 0 | 1 | 0.2 | no | no |  | V control mode | S52513_ALL | Max SCR, PmaxQ0, bes=50
376 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 41 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52513_ALL | Min SCR, P0Q0, bes=0
377 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 86 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52513_ALL | Max SCR, P0Q0, bes=0
378 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 306 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S52513_ALL | Min SCR, PmaxQ0, bes=0
379 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 276 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52513_ALL | Min SCR, PmaxQ0, bes=50
380 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 171 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S52513_ALL | Max SCR, PmaxQ0, bes=0
381 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 141 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52513_ALL | Max SCR, PmaxQ0, bes=50
382 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 311 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S52513_ALL | Min SCR, P0Q0, bes=0
383 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 176 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S52513_ALL | Max SCR, P0Q0, bes=0
384 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 361 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52513_ALL | Min SCR, PmaxQ0, bes=0
385 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 366 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52513_ALL | Min SCR, PmaxQ0, bes=50
386 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 181 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52513_ALL | Max SCR, PmaxQ0, bes=0
387 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 186 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52513_ALL | Max SCR, PmaxQ0, bes=50
388 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 371 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52513_ALL | Min SCR, P0Q0, bes=0
389 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 191 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52513_ALL | Max SCR, P0Q0, bes=0
390 | V_stp_profile | S52513_V0+/-5% | [6 empty] | 21 | 0 | 1 | 0.2 | no | no |  |  | S52513_BESS | Min SCR, PmaxQ0, Bes=50 |  | Ability to make a single voltage profile apply to two variables in PSS/E
391 | V_stp_profile | S52513_Vmax-2.5%/+5% | [6 empty] | 24 | 0 | 1 | 0.2 | no | no |  | reducing setpoint and then driving plant into upper Q limit | S52513_BESS | Min SCR, PmaxQmax, bes=50
392 | V_stp_profile | S52513_Vmin+2.5%/-5% | [6 empty] | 25 | 0 | 1 | 0.2 | no | no |  | increasing setpoitn and then stepping down, driving plant into lower limit | S52513_BESS | Min SCR, PmaxQmin, bes=50
393 | V_stp_profile | S52513_V0+/-5% | [6 empty] | 31 | 0 | 1 | 0.2 | no | no |  |  | S52513_BESS | Min SCR, PminQ0, Bes=-50
394 | V_stp_profile | S52513_Vmax-2.5%/+5% | [6 empty] | 34 | 0 | 1 | 0.2 | no | no |  |  | S52513_BESS | Min SCR, PmminQmax, bes=-50
395 | V_stp_profile | S52513_Vmin+2.5%/-5% | [6 empty] | 35 | 0 | 1 | 0.2 | no | no |  |  | S52513_BESS | Min SCR, PminQmin, bes=-50
396 | V_stp_profile | S52513_V0+/-5% | [6 empty] | 66 | 0 | 1 | 0.2 | no | no |  |  | S52513_BESS | Max SCR, PmaxQ0, Bes=50
397 | V_stp_profile | S52513_Vmax-2.5%/+5% | [6 empty] | 69 | 0 | 1 | 0.2 | no | no |  | reducing setpoint and then driving plant into upper Q limit | S52513_BESS | Max SCR, PmaxQmax, bes=50
398 | V_stp_profile | S52513_Vmin+2.5%/-5% | [6 empty] | 70 | 0 | 1 | 0.2 | no | no |  | increasing setpoitn and then stepping down, driving plant into lower limit | S52513_BESS | Max SCR, PmaxQmin, bes=50
399 | V_stp_profile | S52513_V0+/-5% | [6 empty] | 76 | 0 | 1 | 0.2 | no | no |  |  | S52513_BESS | Max SCR, PminQ0, Bes=-50
400 | V_stp_profile | S52513_Vmax-2.5%/+5% | [6 empty] | 79 | 0 | 1 | 0.2 | no | no |  |  | S52513_BESS | Max SCR, PmminQmax, bes=-50
401 | V_stp_profile | S52513_Vmin+2.5%/-5% | [6 empty] | 80 | 0 | 1 | 0.2 | no | no |  |  | S52513_BESS | Max SCR, PminQmin, bes=-50
402 | Q1_stp_profile | S52513_Q0+/-5 | [6 empty] | 291 | 0 | 1 | 0.2 | no | no |  | Qctrl | S52513_BESS | Min SCR, PmaxQ0, Bes=50
403 | Q1_stp_profile | S52513_Qmax-10/+20 | [6 empty] | 294 | 0 | 1 | 0.2 | no | no |  | Qctrl | S52513_BESS | Min SCR, PmaxQmax, bes=50
404 | Q1_stp_profile | S52513_Qmin+10/-20 | [6 empty] | 295 | 0 | 1 | 0.2 | no | no |  | Qctrl | S52513_BESS | Min SCR, PmaxQmin, bes=50
405 | Q1_stp_profile | S52513_Q0+/-5 | [6 empty] | 301 | 0 | 1 | 0.2 | no | no |  | Qctrl | S52513_BESS | Min SCR, PminQ0, Bes=-50
406 | Q1_stp_profile | S52513_Qmax-10/+20 | [6 empty] | 304 | 0 | 1 | 0.2 | no | no |  | Qctrl | S52513_BESS | Min SCR, PmminQmax, bes=-50
407 | Q1_stp_profile | S52513_Qmin+10/-20 | [6 empty] | 305 | 0 | 1 | 0.2 | no | no |  | Qctrl | S52513_BESS | Min SCR, PminQmin, bes=-50
408 | Q1_stp_profile | S52513_Q0+/-5 | [6 empty] | 336 | 0 | 1 | 0.2 | no | no |  | Qctrl | S52513_BESS | Max SCR, PmaxQ0, Bes=50
409 | Q1_stp_profile | S52513_Qmax-10/+20 | [6 empty] | 339 | 0 | 1 | 0.2 | no | no |  | Qctrl | S52513_BESS | Max SCR, PmaxQmax, bes=50
410 | Q1_stp_profile | S52513_Qmin+10/-20 | [6 empty] | 340 | 0 | 1 | 0.2 | no | no |  | Qctrl | S52513_BESS | Max SCR, PmaxQmin, bes=50
411 | Q1_stp_profile | S52513_Q0+/-5 | [6 empty] | 346 | 0 | 1 | 0.2 | no | no |  | Qctrl | S52513_BESS | Max SCR, PminQ0, Bes=-50
412 | Q1_stp_profile | S52513_Qmax-10/+20 | [6 empty] | 349 | 0 | 1 | 0.2 | no | no |  | Qctrl | S52513_BESS | Max SCR, PmminQmax, bes=-50
413 | Q1_stp_profile | S52513_Qmin+10/-20 | [6 empty] | 350 | 0 | 1 | 0.2 | no | no |  | Qctrl | S52513_BESS | Max SCR, PminQmin, bes=-50
414 | PF1_stp_profile | S52513_PF0+/-1% | [6 empty] | 381 | 0 | 1 | 0.2 | no | no |  | PfCtrl | S52513_BESS | Min SCR, PmaxQ0, Bes=50
415 | PF1_stp_profile | S52513_PFMax-0.5%/+1.5% | [6 empty] | 384 | 0 | 1 | 0.2 | no | no |  | PfCtrl | S52513_BESS | Min SCR, PmaxQmax, bes=50
416 | PF1_stp_profile | S52513_PFMin+0.5%/-1.5% | [6 empty] | 385 | 0 | 1 | 0.2 | no | no |  | PfCtrl | S52513_BESS | Min SCR, PmaxQmin, bes=50
417 | PF1_stp_profile | S52513_PF0+/-1% | [6 empty] | 391 | 0 | 1 | 0.2 | no | no |  | PfCtrl | S52513_BESS | Min SCR, PminQ0, Bes=-50
418 | PF1_stp_profile | S52513_PFMax-0.5%/+1.5% | [6 empty] | 394 | 0 | 1 | 0.2 | no | no |  | PfCtrl | S52513_BESS | Min SCR, PmminQmax, bes=-50
419 | PF1_stp_profile | S52513_PFMin+0.5%/-1.5% | [6 empty] | 395 | 0 | 1 | 0.2 | no | no |  | PfCtrl | S52513_BESS | Min SCR, PminQmin, bes=-50
420 | PF1_stp_profile | S52513_PF0+/-1% | [6 empty] | 201 | 0 | 1 | 0.2 | no | no |  | PfCtrl | S52513_BESS | Max SCR, PmaxQ0, Bes=50
421 | PF1_stp_profile | S52513_PFMax-0.5%/+1.5% | [6 empty] | 204 | 0 | 1 | 0.2 | no | no |  | PfCtrl | S52513_BESS | Max SCR, PmaxQmax, bes=50
422 | PF1_stp_profile | S52513_PFMin+0.5%/-1.5% | [6 empty] | 205 | 0 | 1 | 0.2 | no | no |  | PfCtrl | S52513_BESS | Max SCR, PmaxQmin, bes=50
423 | PF1_stp_profile | S52513_PF0+/-1% | [6 empty] | 211 | 0 | 1 | 0.2 | no | no |  | PfCtrl | S52513_BESS | Max SCR, PminQ0, Bes=-50
424 | PF1_stp_profile | S52513_PFMax-0.5%/+1.5% | [6 empty] | 214 | 0 | 1 | 0.2 | no | no |  | PfCtrl | S52513_BESS | Max SCR, PmminQmax, bes=-50
425 | PF1_stp_profile | S52513_PFMin+0.5%/-1.5% | [6 empty] | 215 | 0 | 1 | 0.2 | no | no |  | PfCtrl | S52513_BESS | Max SCR, PminQmin, bes=-50
426 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 21 | 0 | 1 | 0.2 | no | no |  | V control mode | S52513_BESS | Min SCR, PmaxQ0, bes=50
427 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 66 | 0 | 1 | 0.2 | no | no |  | V control mode | S52513_BESS | Max SCR, PmaxQ0, bes=50
428 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 31 | 0 | 1 | 0.2 | no | no |  | V control mode | S52513_BESS | Min SCR, PminQ0, bes=-50
429 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 76 | 0 | 1 | 0.2 | no | no |  | V control mode | S52513_BESS | Max SCR, PminQ0, bes=-50
430 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 291 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52513_BESS | Min SCR, PmaxQ0, bes=50
431 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 156 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52513_BESS | Max SCR, PmaxQ0, bes=50
432 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 301 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52513_BESS | Min SCR, PminQ0, bes=-50
433 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 166 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52513_BESS | Max SCR, PminQ0, bes=-50
434 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 381 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52513_BESS | Min SCR, PmaxQ0, bes=50
435 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 201 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52513_BESS | Max SCR, PmaxQ0, bes=50
436 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 391 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52513_BESS | Min SCR, PminQ0, bes=-50
437 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 211 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52513_BESS | Max SCR, PminQ0, bes=-50
438 | P_stp_profile | S52514_-/+50% | [6 empty] | 126 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52514_ALL | Inf Grid, PmaxQ0, bes=0 | focus here is on Solar farm, Bess ability to follow setpoints is sufficiently demonstrated in BESS only test.
439 | P_stp_profile | S52514_-/+50% | [6 empty] | 129 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52514_ALL | Inf Grid, PmaxQmax, bes=0
440 | P_stp_profile | S52514_-/+50% | [6 empty] | 130 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52514_ALL | Inf Grid, PmaxQmin, bes=0
441 | P_stp_profile | S52514_-/+50% | [6 empty] | 155 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52514_ALL
442 | P_stp_profile | S52514_-/+50% | [6 empty] | 156 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52514_ALL
443 | P_stp_profile | S52514_-/+50% | [6 empty] | 157 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52514_ALL
444 | P_stp_profile | S52514_-/+50% | [6 empty] | 167 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52514_ALL
445 | P_stp_profile | S52514_-/+50% | [6 empty] | 168 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52514_ALL
446 | P_stp_profile | S52514_-/+50% | [6 empty] | 169 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52514_ALL
447 | P1_stp_profile | S52514_-/+50% | [6 empty] | 96 | 0 | 1 | 0.2 | no | no |  | V control mode | S52514_BESS | Inf Grid, PmaxQ0, bes=50 | focus here is on Solar farm, Bess ability to follow setpoints is sufficiently demonstrated in BESS only test.
448 | P1_stp_profile | S52514_-/+50% | [6 empty] | 99 | 0 | 1 | 0.2 | no | no |  | V control mode | S52514_BESS | Inf Grid, PmaxQmax, bes=50
449 | P1_stp_profile | S52514_-/+50% | [6 empty] | 100 | 0 | 1 | 0.2 | no | no |  | V control mode | S52514_BESS | Inf Grid, PmaxQmin, bes=50
450 | P1_stp_profile | S52514_-/+50% | [6 empty] | 155 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52514_BESS
451 | P1_stp_profile | S52514_-/+50% | [6 empty] | 156 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52514_BESS
452 | P1_stp_profile | S52514_-/+50% | [6 empty] | 157 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52514_BESS
453 | P1_stp_profile | S52514_-/+50% | [6 empty] | 167 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52514_BESS
454 | P1_stp_profile | S52514_-/+50% | [6 empty] | 168 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52514_BESS
455 | P1_stp_profile | S52514_-/+50% | [6 empty] | 169 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52514_BESS
456 | V_profile | S5255_85 | [6 empty] | 129 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255_IQ_ALL_INF
457 | V_profile | S5255_80 | [6 empty] | 129 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255_IQ_ALL_INF
458 | V_profile | S5255_75 | [6 empty] | 129 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255_IQ_ALL_INF
459 | V_profile | S5255_70 | [6 empty] | 129 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255_IQ_ALL_INF
460 | V_profile | S5255_60 | [6 empty] | 129 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255_IQ_ALL_INF
461 | V_profile | S5255_50 | [6 empty] | 129 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255_IQ_ALL_INF
462 | V_profile | S5255_40 | [6 empty] | 129 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255_IQ_ALL_INF
463 | V_profile | S5255_30 | [6 empty] | 129 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255_IQ_ALL_INF
464 | V_profile | S5255_115 | [6 empty] | 130 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255_IQ_ALL_INF
465 | V_profile | S5255_120 | [6 empty] | 130 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255_IQ_ALL_INF
466 | V_profile | S5255_125 | [6 empty] | 130 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255_IQ_ALL_INF
467 | V_profile | S5255_130 | [6 empty] | 130 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255_IQ_ALL_INF
468 | V_profile | S5255_135 | [6 empty] | 130 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255_IQ_ALL_INF
469 | V_profile | S5255_140 | [6 empty] | 130 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255_IQ_ALL_INF
470 | V_profile | S5255_85 | [6 empty] | 114 | 0 | 1 | 0.2 | no | no |  | V control mode | S5255_IQ_BESS
471 | V_profile | S5255_80 | [6 empty] | 114 | 0 | 1 | 0.2 | no | no |  | V control mode | S5255_IQ_BESS
472 | V_profile | S5255_75 | [6 empty] | 114 | 0 | 1 | 0.2 | no | no |  | V control mode | S5255_IQ_BESS
473 | V_profile | S5255_70 | [6 empty] | 114 | 0 | 1 | 0.2 | no | no |  | V control mode | S5255_IQ_BESS
474 | V_profile | S5255_60 | [6 empty] | 114 | 0 | 1 | 0.2 | no | no |  | V control mode | S5255_IQ_BESS
475 | V_profile | S5255_50 | [6 empty] | 114 | 0 | 1 | 0.2 | no | no |  | V control mode | S5255_IQ_BESS
476 | V_profile | S5255_115 | [6 empty] | 115 | 0 | 1 | 0.2 | no | no |  | V control mode | S5255_IQ_BESS
477 | V_profile | S5255_120 | [6 empty] | 115 | 0 | 1 | 0.2 | no | no |  | V control mode | S5255_IQ_BESS
478 | V_profile | S5255_125 | [6 empty] | 115 | 0 | 1 | 0.2 | no | no |  | V control mode | S5255_IQ_BESS
479 | V_profile | S5255_130 | [6 empty] | 115 | 0 | 1 | 0.2 | no | no |  | V control mode | S5255_IQ_BESS
480 | V_profile | S5255_135 | [6 empty] | 115 | 0 | 1 | 0.2 | no | no |  | V control mode | S5255_IQ_BESS
481 | V_profile | S5255_140 | [6 empty] | 115 | 0 | 1 | 0.2 | no | no |  | V control mode | S5255_IQ_BESS
482 | V_profile | FLAT_RUN_20 | [6 empty] | 36 | 0 | 1 | 0.2 | no | yes |  |  | CORNER_CASES
483 | V_profile | FLAT_RUN_20 | [6 empty] | 37 | 1 | 1 | 0.2 | no | no |  |  | INIT
484 | V_profile | FLAT_RUN_20 | [6 empty] | 38 | 1 | 1 | 0.2 | no | no |  |  | INIT
485 | V_profile | FLAT_RUN_20 | [6 empty] | 39 | 1 | 1 | 0.2 | no | yes |  |  | CORNER_CASES | 1
486 | V_profile | FLAT_RUN_20 | [6 empty] | 40 | 1 | 1 | 0.2 | no | yes |  |  | CORNER_CASES | 0
487 | V_profile | FLAT_RUN_20 | [6 empty] | 41 | 0 | 1 | 0.2 | no | no |  |  | INIT | 0
488 | V_profile | FLAT_RUN_20 | [6 empty] | 42 | 1 | 1 | 0.2 | no | no |  |  | INIT | 1
489 | V_profile | FLAT_RUN_20 | [6 empty] | 43 | 1 | 1 | 0.2 | no | no |  |  | INIT | 0
490 | V_profile | FLAT_RUN_20 | [6 empty] | 44 | 1 | 1 | 0.2 | no | no |  |  | INIT | 1
491 | V_profile | FLAT_RUN_20 | [6 empty] | 45 | 1 | 1 | 0.2 | no | no |  |  | INIT | 0
492 | V_profile | FLAT_RUN_20 | [6 empty] | 81 | 0 | 1 | 0.2 | no | yes |  |  | CORNER_CASES | 0
493 | V_profile | FLAT_RUN_20 | [6 empty] | 84 | 1 | 1 | 0.2 | no | yes |  |  | CORNER_CASES | 1
494 | V_profile | FLAT_RUN_20 | [6 empty] | 85 | 1 | 1 | 0.2 | no | yes |  |  | CORNER_CASES | 0
495 | V_profile | FLAT_RUN_20 | [6 empty] | 86 | 1 | 1 | 0.2 | no | no |  |  | INIT | 1
496 | V_profile | FLAT_RUN_20 | [6 empty] | 87 | 1 | 1 | 0.2 | no | no |  |  | INIT | 0
497 | V_profile | FLAT_RUN_20 | [6 empty] | 88 | 0 | 1 | 0.2 | no | no |  |  | INIT | 0
498 | V_profile | FLAT_RUN_20 | [6 empty] | 89 | 1 | 1 | 0.2 | no | no |  |  | INIT | 0
499 | V_profile | FLAT_RUN_20 | [6 empty] | 90 | 1 | 1 | 0.2 | no | no |  |  | INIT | 1
500 | V_profile | FLAT_RUN_20 | [6 empty] | 91 | 1 | 1 | 0.2 | no | no |  |  | INIT
501 | V_profile | FLAT_RUN_20 | [6 empty] | 92 | 1 | 1 | 0.2 | no | no |  |  | INIT
502 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 39 | 1 | 1 | 0.2 | yes | yes |  | V control mode | S52513_ALL
503 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 40 | 1 | 1 | 0.2 | yes | yes |  | V control mode | S52513_ALL
504 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 84 | 1 | 1 | 0.2 | yes | yes |  | V control mode | S52513_ALL
505 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 85 | 1 | 1 | 0.2 | yes | yes |  | V control mode | S52513_ALL
506 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 309 | 1 | 1 | 0.2 | yes | yes |  | Q control mode | S52513_ALL
507 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 310 | 1 | 1 | 0.2 | yes | yes |  | Q control mode | S52513_ALL
508 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 174 | 1 | 1 | 0.2 | yes | yes |  | Q control mode | S52513_ALL
509 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 175 | 1 | 1 | 0.2 | yes | yes |  | Q control mode | S52513_ALL
510 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 399 | 1 | 1 | 0.2 | yes | yes |  | PF control mode | S52513_ALL
511 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 400 | 1 | 1 | 0.2 | yes | yes |  | PF control mode | S52513_ALL
512 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 219 | 1 | 1 | 0.2 | yes | yes |  | PF control mode | S52513_ALL
513 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 220 | 1 | 1 | 0.2 | yes | yes |  | PF control mode | S52513_ALL
514 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 39 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52513_ALL_dbg
515 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 40 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52513_ALL_dbg
516 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 84 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52513_ALL_dbg
517 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 85 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52513_ALL_dbg
518 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 309 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S52513_ALL_dbg
519 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 310 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S52513_ALL_dbg
520 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 174 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S52513_ALL_dbg
521 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 175 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S52513_ALL_dbg
522 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 399 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S52513_ALL_dbg
523 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 400 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S52513_ALL_dbg
524 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 219 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S52513_ALL_dbg
525 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 220 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S52513_ALL_dbg
Note on A3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: review
Note on J44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Make sure Plant in Qref mode.
Note on A52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: to be revisited - available P vs. setpoint --> how to adjust in model?
Note on J60: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: here the available energy from solar needs to be limited --> not sure if model can do it. And if so, how.
Note on A76: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: to be revisited - available P vs. setpoint --> how to adjust in model?
Note on J105: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not fully correct, MAT asks for P=0.5, which is not available in the setpoints at the moment
Note on J172: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Q-control mode
Note on J174: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pf-control mode
Note on J210: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Same SCR and Power flow as the listed setpoints, but Q-ctrl
Note on J218: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Same SCR and Power flow as the listed setpoints, but Pf-ctrl
Note on J234: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: why setpoint 2 and 3? Should it be at Qmax and Qmin instead of 0.3pu of Q like in DMAT?
Note on J246: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: why setpoint 2 and 3? Should it be at Qmax and Qmin instead of 0.3pu of Q like in DMAT?
Note on Q265: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pf control mode not relevant. Q testing adequate as it allows to reach pos and neg limits.
Note on J268: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: again, setpoint 100 is not with max Q, but 0.3pu
Note on B350: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Step only the PV command. Both Solar and PV in Q cmd mode
Note on B362: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Step only PV profile. Both PV and BESS in Pf command mode
Note on C449: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This profile will need to be battery-specific. Same as other BESS profiles.

## ORT
PSSE-specific settings
CaseNr | Test Type | time | Disturbance Frequency | Disturbance Magnitude | Vbase | PhaseOsc Magnitude | ActivePower | ReactivePower | Grid SCR | Grid X_R | setpoint ID | TimeStep | AccFactor | run in PSCAD? | run in PSS/E? | Comment/Corresponding DMAT case | test group | simulation batch
1 | ORT | 5 | 0.1 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
2 | ORT | 5 | 0.2 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
3 | ORT | 5 | 0.3 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
4 | ORT | 5 | 0.4 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
5 | ORT | 5 | 0.5 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
6 | ORT | 5 | 0.6 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
7 | ORT | 5 | 0.7 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
8 | ORT | 5 | 0.8 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
9 | ORT | 5 | 0.9 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
10 | ORT | 5 | 1 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
11 | ORT | 5 | 2 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
12 | ORT | 5 | 3 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
13 | ORT | 5 | 4 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
14 | ORT | 5 | 5 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
15 | ORT | 5 | 6 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
16 | ORT | 5 | 7 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
17 | ORT | 5 | 8 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
18 | ORT | 5 | 9 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
19 | ORT | 5 | 10 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
20 | ORT | 5 | 11 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
21 | ORT | 5 | 12 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
22 | ORT | 5 | 13 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
23 | ORT | 5 | 14 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
24 | ORT | 5 | 15 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
25 | ORT | 5 | 16 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
26 | ORT | 5 | 17 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
27 | ORT | 5 | 18 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
28 | ORT | 5 | 19 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
29 | ORT | 5 | 20 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
30 | ORT | 5 | 21 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
31 | ORT | 5 | 22 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
32 | ORT | 5 | 23 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
33 | ORT | 5 | 24 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
34 | ORT | 5 | 25 | 0.005 |  | 0 |  |  |  |  | 36 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_ALL
35 | ORT | 5 | 0.1 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
36 | ORT | 5 | 0.2 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
37 | ORT | 5 | 0.3 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
38 | ORT | 5 | 0.4 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
39 | ORT | 5 | 0.5 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
40 | ORT | 5 | 0.6 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
41 | ORT | 5 | 0.7 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
42 | ORT | 5 | 0.8 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
43 | ORT | 5 | 0.9 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
44 | ORT | 5 | 1 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
45 | ORT | 5 | 2 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
46 | ORT | 5 | 3 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
47 | ORT | 5 | 4 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
48 | ORT | 5 | 5 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
49 | ORT | 5 | 6 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
50 | ORT | 5 | 7 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
51 | ORT | 5 | 8 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
52 | ORT | 5 | 9 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
53 | ORT | 5 | 10 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
54 | ORT | 5 | 11 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
55 | ORT | 5 | 12 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
56 | ORT | 5 | 13 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
57 | ORT | 5 | 14 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
58 | ORT | 5 | 15 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
59 | ORT | 5 | 16 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
60 | ORT | 5 | 17 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
61 | ORT | 5 | 18 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
62 | ORT | 5 | 19 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
63 | ORT | 5 | 20 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
64 | ORT | 5 | 21 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
65 | ORT | 5 | 22 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
66 | ORT | 5 | 23 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
67 | ORT | 5 | 24 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
68 | ORT | 5 | 25 | 0.005 |  | 0 |  |  |  |  | 66 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT_SELF_BESS
69 | ORT | 5 | 26 | 0.005 |  | 0 |  |  |  |  | 7 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
70 | ORT | 5 | 27 | 0.005 |  | 0 |  |  |  |  | 7 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
71 | ORT | 5 | 28 | 0.005 |  | 0 |  |  |  |  | 7 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
72 | ORT | 5 | 29 | 0.005 |  | 0 |  |  |  |  | 7 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
73 | ORT | 5 | 30 | 0.005 |  | 0 |  |  |  |  | 7 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
74 | ORT | 5 | 31 | 0.005 |  | 0 |  |  |  |  | 7 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
75 | ORT | 5 | 32 | 0.005 |  | 0 |  |  |  |  | 7 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
76 | ORT | 5 | 33 | 0.005 |  | 0 |  |  |  |  | 7 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
77 | ORT | 5 | 34 | 0.005 |  | 0 |  |  |  |  | 7 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
78 | ORT | 5 | 35 | 0.005 |  | 0 |  |  |  |  | 7 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
79 | ORT | 5 | 36 | 0.005 |  | 0 |  |  |  |  | 7 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
80 | ORT | 5 | 37 | 0.005 |  | 0 |  |  |  |  | 7 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
81 | ORT | 5 | 38 | 0.005 |  | 0 |  |  |  |  | 7 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
82 | ORT | 5 | 39 | 0.005 |  | 0 |  |  |  |  | 7 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
83 | ORT | 5 | 40 | 0.005 |  | 0 |  |  |  |  | 7 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
84 | ORT | 5 | 41 | 0.005 |  | 0 |  |  |  |  | 7 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
85 | ORT | 5 | 42 | 0.005 |  | 0 |  |  |  |  | 7 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
86 | ORT | 5 | 43 | 0.005 |  | 0 |  |  |  |  | 7 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
87 | ORT | 5 | 44 | 0.005 |  | 0 |  |  |  |  | 7 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
88 | ORT | 5 | 45 | 0.005 |  | 0 |  |  |  |  | 7 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
55 | ORT | 5 | 0.1 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
56 | ORT | 5 | 0.2 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
57 | ORT | 5 | 0.3 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
58 | ORT | 5 | 0.4 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
59 | ORT | 5 | 0.5 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
60 | ORT | 5 | 0.6 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
61 | ORT | 5 | 0.7 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
62 | ORT | 5 | 0.8 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
63 | ORT | 5 | 0.9 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
64 | ORT | 5 | 1 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
65 | ORT | 5 | 2 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
66 | ORT | 5 | 3 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
67 | ORT | 5 | 4 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
68 | ORT | 5 | 5 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
69 | ORT | 5 | 6 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
70 | ORT | 5 | 7 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
71 | ORT | 5 | 8 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
72 | ORT | 5 | 9 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
73 | ORT | 5 | 10 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
74 | ORT | 5 | 11 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
75 | ORT | 5 | 12 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
76 | ORT | 5 | 13 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
77 | ORT | 5 | 14 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
78 | ORT | 5 | 15 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
79 | ORT | 5 | 16 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
80 | ORT | 5 | 17 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
81 | ORT | 5 | 18 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
82 | ORT | 5 | 19 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
83 | ORT | 5 | 20 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
84 | ORT | 5 | 21 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
85 | ORT | 5 | 22 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
86 | ORT | 5 | 23 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
87 | ORT | 5 | 24 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
88 | ORT | 5 | 25 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
89 | ORT | 5 | 26 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
90 | ORT | 5 | 27 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
91 | ORT | 5 | 28 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
92 | ORT | 5 | 29 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
93 | ORT | 5 | 30 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
94 | ORT | 5 | 31 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
95 | ORT | 5 | 32 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
96 | ORT | 5 | 33 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
97 | ORT | 5 | 34 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
98 | ORT | 5 | 35 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
99 | ORT | 5 | 36 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
100 | ORT | 5 | 37 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
101 | ORT | 5 | 38 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
102 | ORT | 5 | 39 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
103 | ORT | 5 | 40 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
104 | ORT | 5 | 41 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
105 | ORT | 5 | 42 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
106 | ORT | 5 | 43 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
107 | ORT | 5 | 44 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
108 | ORT | 5 | 45 | 0.005 |  | 2 |  |  |  |  | 7 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
Note on F2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: if not specified, just modulate in proportion to Vth voltage dictated by setpoint

## TOV
Overvoltage tests. Overvoltage condition is created by connecting a suitably-sized capacitor at the Connection point. The calculation is designed to take into account the power flows at POC
PSSE-specific settings
CaseNr | Test Type | time | Fduration | Capacity(F) | Vresidual | SCL_post | X_R_post | setpoint ID | init_help | TimeStep | AccFactor | run in PSCAD? | run in PSS/E? | Comment/Corresponding DMAT case | test group | simulation batch
1 | TOV | 5 | 0.9 |  | 1.15 |  |  | 25 | 0 | 1 | 0.2 | no | no | 131 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
2 | TOV | 5 | 0.9 |  | 1.15 |  |  | 27 | 0 | 1 | 0.2 | no | no | 132 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
3 | TOV | 5 | 0.9 |  | 1.15 |  |  | 26 | 0 | 1 | 0.2 | no | no | 133 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
4 | TOV | 5 | 0.9 |  | 1.15 |  |  | 13 | 0 | 1 | 0.2 | no | no | 134 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
5 | TOV | 5 | 0.9 |  | 1.15 |  |  | 21 | 0 | 1 | 0.2 | no | no | 135 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
6 | TOV | 5 | 0.9 |  | 1.15 |  |  | 20 | 0 | 1 | 0.2 | no | no | 136 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
7 | TOV | 5 | 0.9 |  | 1.15 |  |  | 36 | 0 | 1 | 0.2 | yes | yes | 137 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
8 | TOV | 5 | 0.9 |  | 1.15 |  |  | 66 | 0 | 1 | 0.2 | no | no | 137 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
9 | TOV | 5 | 0.9 |  | 1.15 |  |  | 9 | 0 | 1 | 0.2 | no | no | 138 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
10 | TOV | 5 | 0.9 |  | 1.15 |  |  | 8 | 0 | 1 | 0.2 | no | no | 139 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
11 | TOV | 5 | 0.9 |  | 1.15 |  |  | 1 | 0 | 1 | 0.2 | no | no | 137 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
12 | TOV | 5 | 0.9 |  | 1.15 |  |  | 3 | 0 | 1 | 0.2 | no | no | 138 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
13 | TOV | 5 | 0.9 |  | 1.15 |  |  | 2 | 0 | 1 | 0.2 | no | no | 139 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
14 | TOV | 5 | 0.1 |  | 1.2 |  |  | 25 | 0 | 1 | 0.2 | no | no | 140 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
15 | TOV | 5 | 0.1 |  | 1.2 |  |  | 27 | 0 | 1 | 0.2 | no | no | 141 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
16 | TOV | 5 | 0.1 |  | 1.2 |  |  | 26 | 0 | 1 | 0.2 | no | no | 142 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
17 | TOV | 5 | 0.1 |  | 1.2 |  |  | 13 | 0 | 1 | 0.2 | no | no | 143 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
18 | TOV | 5 | 0.1 |  | 1.2 |  |  | 21 | 0 | 1 | 0.2 | no | no | 144 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
19 | TOV | 5 | 0.1 |  | 1.2 |  |  | 20 | 0 | 1 | 0.2 | no | no | 145 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
20 | TOV | 5 | 0.1 |  | 1.2 |  |  | 7 | 0 | 1 | 0.2 | no | no | 146 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
21 | TOV | 5 | 0.1 |  | 1.2 |  |  | 9 | 0 | 1 | 0.2 | no | no | 147 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
22 | TOV | 5 | 0.1 |  | 1.2 |  |  | 8 | 0 | 1 | 0.2 | no | no | 148 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
22 | TOV | 5 | 0.1 |  | 1.2 |  |  | 36 | 0 | 1 | 0.2 | yes | yes | 146 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_ALL
23 | TOV | 5 | 0.1 |  | 1.2 |  |  | 66 | 0 | 1 | 0.2 | no | no | 146 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT_SELF_BESS
24 | TOV | 5 | 0.1 |  | 1.2 |  |  | 3 | 0 | 1 | 0.2 | no | no | 147 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
25 | TOV | 5 | 0.1 |  | 1.2 |  |  | 2 | 0 | 1 | 0.2 | no | no | 148 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
26 | TOV | 5 | 20 |  | 1.2 |  |  | 1 | 0 | 1 | 0.2 | no | no | 137 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | Benchmarking-5.3.9
27 | TOV | 5 | 2 |  | 1.25 |  |  | 1 | 0 | 1 | 0.2 | no | no | 136 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | Benchmarking-5.3.9
28 | TOV | 5 | 0.5 |  | 1.2 |  |  | 85 | 1 | 1 | 0.2 | yes | yes |  |  | S5255_IQ_ALL
29 | TOV | 5 | 0.5 |  | 1.25 |  |  | 85 | 1 | 1 | 0.2 | yes | yes |  |  | S5255_IQ_ALL
30 | TOV | 5 | 0.5 |  | 1.3 |  |  | 85 | 1 | 1 | 0.2 | yes | yes |  |  | S5255_IQ_ALL
31 | TOV | 5 | 0.5 |  | 1.35 |  |  | 85 | 1 | 1 | 0.2 | yes | yes |  |  | S5255_IQ_ALL
32 | TOV | 5 | 0.5 |  | 1.4 |  |  | 85 | 1 | 1 | 0.2 | yes | yes |  |  | S5255_IQ_ALL
33 | TOV | 5 | 0.5 |  | 1.45 |  |  | 85 | 1 | 1 | 0.2 | yes | yes |  |  | S5255_IQ_ALL
34 | TOV | 5 | 0.5 |  | 1.5 |  |  | 85 | 1 | 1 | 0.2 | yes | yes |  |  | S5255_IQ_ALL
35 | TOV | 5 | 0.5 |  | 1.55 |  |  | 85 | 1 | 1 | 0.2 | yes | yes |  |  | S5255_IQ_ALL
36 | TOV | 5 | 0.5 |  | 1.6 |  |  | 85 | 1 | 1 | 0.2 | yes | yes |  |  | S5255_IQ_ALL
37 | TOV | 5 | 0.5 |  | 1.65 |  |  | 85 | 1 | 1 | 0.2 | yes | yes |  |  | S5255_IQ_ALL
38 | TOV | 5 | 0.5 |  | 1.7 |  |  | 85 | 1 | 1 | 0.2 | yes | yes |  |  | S5255_IQ_ALL
39 | TOV | 5 | 0.5 |  | 1.2 |  |  | 70 | 0 | 1 | 0.2 | no | no |  |  | S5255_IQ_BESS
40 | TOV | 5 | 0.5 |  | 1.25 |  |  | 70 | 0 | 1 | 0.2 | no | no |  |  | S5255_IQ_BESS
41 | TOV | 5 | 0.5 |  | 1.3 |  |  | 70 | 0 | 1 | 0.2 | no | no |  |  | S5255_IQ_BESS
42 | TOV | 5 | 0.5 |  | 1.35 |  |  | 70 | 0 | 1 | 0.2 | no | no |  |  | S5255_IQ_BESS
43 | TOV | 5 | 0.5 |  | 1.4 |  |  | 70 | 0 | 1 | 0.2 | no | no |  |  | S5255_IQ_BESS
44 | TOV | 5 | 0.5 |  | 1.45 |  |  | 70 | 0 | 1 | 0.2 | no | no |  |  | S5255_IQ_BESS
45 | TOV | 5 | 0.5 |  | 1.5 |  |  | 70 | 0 | 1 | 0.2 | no | no |  |  | S5255_IQ_BESS
46 | TOV | 5 | 0.5 |  | 1.55 |  |  | 70 | 0 | 1 | 0.2 | no | no |  |  | S5255_IQ_BESS
47 | TOV | 5 | 0.5 |  | 1.6 |  |  | 70 | 0 | 1 | 0.2 | no | no |  |  | S5255_IQ_BESS
48 | TOV | 5 | 0.5 |  | 1.65 |  |  | 70 | 0 | 1 | 0.2 | no | no |  |  | S5255_IQ_BESS
49 | TOV | 5 | 0.5 |  | 1.7 |  |  | 70 | 0 | 1 | 0.2 | no | no |  |  | S5255_IQ_BESS
50 | TOV | 5 | 2 |  | 1.25 |  |  | 36 | 0 | 1 | 0.2 | yes | yes | 136 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | S5254_DBG
51 | TOV | 5 | 2 |  | 1.25 |  |  | 39 | 1 | 1 | 0.2 | yes | yes | 136 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | S5254_DBG
52 | TOV | 5 | 2 |  | 1.25 |  |  | 40 | 1 | 1 | 0.2 | yes | yes | 136 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | S5254_DBG
53 | TOV | 5 | 2 |  | 1.25 |  |  | 81 | 0 | 1 | 0.2 | yes | yes | 136 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | S5254_DBG
54 | TOV | 5 | 2 |  | 1.25 |  |  | 84 | 1 | 1 | 0.2 | yes | yes | 136 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | S5254_DBG
55 | TOV | 5 | 2 |  | 1.25 |  |  | 85 | 1 | 1 | 0.2 | yes | yes | 136 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | S5254_DBG
Note on A7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MAT

## NetworkFaults
For the contingency comes along with the runback scheme: + Define the contingency with the CaseNr as normal + In the following row, change the option Runback? To 1
CaseNr | TestType | Runback? | Ftype | Ftime | Fault_Element | F resistance | F reactance | i_bus | j_bus | k_bus | id | location | trip_near | trip_far | arc_time | arc_success | base_kV | run in PSS/E? | CaseDescription | Case_Code
1 | Fault |  | 3PHG | 3 | Line |  |  | 32700 | 32230 |  | 1 |  | 0.12 | 0.22 | 3 | -1 | 220 | yes | Line fault SHTS - FVTS -- 3PHG | SHTS_FVTS
|  | 1 | 3PHG | 3.22 | Line |  |  | 32230 | 32080 |  | 1 |  | 0 | 0 |  |  | 220 | yes | - Runback Trip FVTS - BETS -- 3PHG | FVTS_BETS
2 | Fault |  | 3PHG | 3 | Line |  |  | 32700 | 32240 |  | 1 |  | 0.12 | 0.22 | 3 | -1 | 220 | yes | Line fault SHTS - GNTS1 -- 3PHG | SHTS_GNTS1
3 | Fault |  | 3PHG | 3 | Line |  |  | 32700 | 32180 |  | 1 |  | 0.12 | 0.22 | 3 | -1 | 220 | yes | Line fault SHTS - DDTS -- 3PHG | SHTS_DDTS
4 | Fault |  | 2PHG | 3 | Line |  |  | 32940 | 32641 |  | 1 |  | 0.12 | 0.22 | 3 | -1 | 220 | no | Line fault YPS - ROTS_A -- 2PHG | YPS_ROTS_A
5 | Fault |  | 2PHG | 3 | Line |  |  | 32851 | 32680 |  | 1 |  | 0.12 | 0.22 | 3 | -1 | 220 | no | Line fault TTS - RWTS -- 2PHG | TTS_RWTS
6 | Fault |  | 2PHG | 3 | Line |  |  | 32090 | 32040 |  | 1 |  | 0.12 | 0.22 | 3 | -1 | 220 | no | Line fault ELTS - BATS -- 2PHG | ELTS_BATS
|  | 1 | 2PHG | 3.12 | Line |  |  | 32090 | 32480 |  | 1 |  | 0 | 0 |  |  | 220 | no | - Runback Trip ELTS - MLTS -- 2PHG | ELTS_MLTS
7 | Fault |  | 2PHG | 3 | Line |  |  | 32040 | 32080 |  | 1 |  | 0.12 | 0.22 | 3 | -1 | 220 | no | Line fault BATS - BETS -- 2PHG | BATS_BETS
8 | Fault |  | 2PHG | 3 | Line |  |  | 32040 | 32480 |  | 1 |  | 0.12 | 0.22 | 3 | -1 | 220 | no | Line fault BATS - MLTS -- 2PHG | BATS_MLTS
9 | Fault |  | 2PHG | 3 | Line |  |  | 32831 | 32610 |  | 1 |  | 0.12 | 0.22 | 3 | -1 | 220 | no | Line fault WETS - RCTS -- 2PHG | WETS_RCTS
|  | 1 | 2PHG | 3.12 | Line |  |  | 32831 | 32380 |  | 1 |  | 0 | 0 |  |  | 220 | no | - Runback Trip WETS - KGTS -- 2PHG | WETS_KGTS
10 | Fault |  | 2PHG | 3 | Line |  |  | 22201 | 23010 |  | 1 |  | 0.12 | 0.22 | 3 | -1 | 220 | no | Line fault DLP220 - BLRD -- 2PHG | DLP220_BLRD
11 | Fault |  | 2PHG | 3 | Line |  |  | 11358 | 32610 |  | 1 |  | 0.12 | 0.22 | 3 | -1 | 220 | no | Line fault KMTS - RCTS -- 2PHG | KMTS_RCTS
12 | Fault |  | 2PHG | 3 | Line |  |  | 32280 | 32793 |  | 1 |  | 0.12 | 0.22 | 3 | -1 | 220 | no | Line fault HOTS - MRT -- 2PHG | HOTS_MRT
|  | 1 | 2PHG | 3.12 | Line |  |  | 32793 | 11358 |  | 1 |  | 0 | 0 |  |  | 220 | no | - Runback Trip MRT - KMTS -- 2PHG | MRT_KMTS
13 | Fault |  | 2PHG | 3 | Line |  |  | 32040 | 32816 |  | 1 |  | 0.12 | 0.22 | 3 | -1 | 220 | no | Line fault BATS - WBTS -- 2PHG | BATS_WBTS
|  | 1 | 2PHG | 3.12 | Line |  |  | 32816 | 32050 |  | 1 |  | 0 | 0 |  |  | 220 | no | - Runback Trip WBTS - ARTS -- 2PHG | WBTS_ARTS
14 | Fault |  | 2PHG | 3 | Line |  |  | 32380 | 32080 |  | 1 |  | 0.12 | 0.22 | 3 | -1 | 220 | no | Line fault KGTS - BETS -- 2PHG | KGTS_BETS
15 | Fault |  | 2PHG | 3 | Line |  |  | 21200 | 21893 |  | 1 |  | 0.1 | 0.12 | 3 | -1 | 220 | no | Line fault DLP330 - WAG -- 2PHG | DLP330_WAG
16 | Fault |  | 2PHG | 3 | Line |  |  | 11190 | 32610 |  | 1 |  | 0.12 | 0.52 | 3 | -1 | 220 | no | Line fault BRG - RCTS -- 2PHG | BRG_RCTS
17 | Fault |  | 2PHG | 3 | Line |  |  | 32080 | 32230 |  | 1 |  | 0.12 | 0.22 | 3 | -1 | 220 | no | Line fault BETS - FVTS -- 2PHG | BETS_FVTS
|  | 1 | 2PHG | 3.22 | Line |  |  | 32230 | 32700 |  | 1 |  | 0 | 0 |  |  | 220 | no | - Runback Trip FVTS - SHTS -- 2PHG | FVTS_SHTS
18 | Fault |  | 3PHG | 3 | Line |  |  | 36700 | 36716 |  | 1 |  | 0.14 | 3.64 | 3 | 0 | 66 | no | Line fault SHTS66 - NSF -- 3PHG | SHTS66_NSF
19 | Fault |  | 3PHG | 3 | Line |  |  | 36716 | 36700 |  | 1 |  | 0.54 | 0.54 | 3 | 0 | 66 | no | Line fault NSF - SHTS66 -- 3PHG | NSF_SHTS66
20 | Fault |  | 3PHG | 3 | Line |  |  | 36716 | 36706 |  | 1 |  | 0.14 | 3.64 | 3 | 0 | 66 | no | Line fault NSF - NKA -- 3PHG | NSF_NKA
21 | Fault |  | 3PHG | 3 | Line |  |  | 36706 | 36716 |  | 1 |  | 0.14 | 3.64 | 3 | 0 | 66 | no | Line fault NKA - NSF -- 3PHG | NKA_NSF
22 | Fault |  | 3PHG | 3 | Line |  |  | 36700 | 367170 |  | 1 |  | 0.14 | 3.84 | 3 | 0 | 66 | no | Line fault SHTS66 - LSF -- 3PHG | SHTS66_LSF
23 | Fault |  | 3PHG | 3 | Line |  |  | 367170 | 36700 |  | 1 |  | 0.54 | 0.54 | 3 | 0 | 66 | no | Line fault LSF - SHTS66 -- 3PHG | LSF_SHTS66
|  | 1 | 2PHG | 3.54 | Line |  |  | 36717 | 367172 |  | 1 |  | 0 | 0 |  |  | 66 | no | - Runback Trip LSF - LSF2 -- 2PHG | LSF_LSF2
24 | Fault |  | 3PHG | 3 | Line |  |  | 36704 | 367170 |  | 1 |  | 0.14 | 4.64 | 3 | 0 | 66 | no | Line fault KYM1 - LSF -- 3PHG | KYM1_LSF
|  | 1 | 2PHG | 3.14 | Line |  |  | 36717 | 367172 |  | 1 |  | 0 | 0 |  |  | 66 | no | - Runback Trip LSF - LSF2 -- 2PHG | LSF_LSF2
25 | Fault |  | 3PHG | 3 | Line |  |  | 367170 | 36704 |  | 1 |  | 0.54 | 0.54 | 3 | 0 | 66 | no | Line fault LSF - KYM1 -- 3PHG | LSF_KYM1
|  | 1 | 2PHG | 3.54 | Line |  |  | 36717 | 367172 |  | 1 |  | 0 | 0 |  |  | 66 | no | - Runback Trip LSF - LSF2 -- 2PHG | LSF_LSF2
26 | Fault |  | 3PHG | 3 | Line |  |  | 36700 | 36704 |  | 1 |  | 0.14 | 2.54 | 3 | 0 | 66 | no | Line fault SHTS66 - KYM1 -- 3PHG | SHTS66_KYM1
|  | 1 | 2PHG | 3.14 | Line |  |  | 36717 | 367172 |  | 1 |  | 0 | 0 |  |  | 66 | no | - Runback Trip LSF - LSF2 -- 2PHG | LSF_LSF2
27 | Fault |  | 3PHG | 3 | Line |  |  | 36704 | 36700 |  | 1 |  | 0.54 | 0.54 | 3 | 0 | 66 | no | Line fault KYM1 - SHTS66 -- 3PHG | KYM1_SHTS66
28 | Fault |  | 3PHG | 3 | Line |  |  | 36700 | 36707 |  | 1 |  | 0.17 | 0.37 | 3 | 0 | 66 | no | Line fault SHTS66 - SHN1 -- 3PHG | SHTS66_SHN1
29 | Fault |  | 3PHG | 3 | Line |  |  | 36700 | 36708 |  | 1 |  | 0.14 | 0.74 | 3 | 0 | 66 | no | Line fault SHTS66 - STN -- 3PHG | SHTS66_STN
30 | Fault |  | 3PHG | 3 | Line |  |  | 36700 | 36705 |  | 1 |  | 0.14 | 2.54 | 3 | 0 | 66 | no | Line fault SHTS66 - MNA -- 3PHG | SHTS66_MNA
31 | Fault |  | 3PHG | 3 | Line |  |  | 36700 | 36715 |  | 1 |  | 0.14 | 0.74 | 3 | 0 | 66 | no | Line fault SHTS66 - SHP -- 3PHG | SHTS66_SHP
32 | Fault |  | 3PHG | 3 | Line |  |  | 36704 | 36703 |  | 1 |  | 0.54 | 0.54 | 3 | 0 | 66 | no | Line fault KYM1 - ECA1 -- 3PHG | KYM1_ECA1
33 | Fault |  | 3PHG | 3 | Line |  |  | 36703 | 36704 |  | 1 |  | 0.14 | 0.34 | 3 | 0 | 66 | no | Line fault ECA1 - KYM1 -- 3PHG | ECA1_KYM1
34 | Fault |  | 3PHG | 3 | Line |  |  | 36704 | 36703 |  | 1 |  | 0.54 | 0.54 | 3 | 0 | 66 | no | Line fault KYM1 - ECA1 -- 3PHG | KYM1_ECA1
35 | Fault |  | 3PHG | 3 | Line |  |  | 36703 | 36704 |  | 1 |  | 0.14 | 4.34 | 3 | 0 | 66 | no | Line fault ECA1 - KYM1 -- 3PHG | ECA1_KYM1
36 | Fault |  | 3PHG | 3 | Line |  |  | 36715 | 36704 |  | 1 |  | 0.14 | 2.64 | 3 | 0 | 66 | no | Line fault SHP - KYM1 -- 3PHG | SHP_KYM1
37 | Fault |  | 3PHG | 3 | Line |  |  | 36704 | 36715 |  | 1 |  | 0.54 | 0.54 | 3 | 0 | 66 | no | Line fault KYM1 - SHP -- 3PHG | KYM1_SHP
38 | Fault |  | 3PHG | 3 | Line |  |  | 37704 | 37734 |  | 1 |  | 1.149 | 1.149 | 3 | 0 | 66 | no | Line fault KYM22 - KSSF -- 3PHG | KYM22_KSSF
39 | Fault |  | 2PHG | 3 | Line |  |  | 36700 | 36716 |  | 1 |  | 0.14 | 0.54 | 3 | 0 | 66 | no | Line fault SHTS66 - NSF -- 2PHG | SHTS66_NSF
40 | Fault |  | 2PHG | 3 | Line |  |  | 32080 | 32230 |  | 1 |  | 0.12 | 0.22 | 3 | -1 | 66 | no | Line fault BETS - FVTS -- 2PHG | BETS_FVTS
41 | Fault |  | 2PHG | 3 | Line |  |  | 32080 | 32230 |  | 1 |  | 0.12 | 0.22 | 3 | -1 | 66 | no | Line fault BETS - FVTS -- 2PHG | BETS_FVTS
42 | Fault |  | 2PHG | 3 | Line |  |  | 367170 | 36700 |  | 1 |  | 0.14 | 0.54 | 3 | 0 | 66 | no | Line fault LSF - SHTS66 -- 2PHG | LSF_SHTS66
|  | 1 | 2PHG | 3.14 | Line |  |  | 36717 | 367172 |  | 1 |  | 0 | 0 |  |  | 66 | no | - Runback Trip LSF - LSF2 -- 2PHG | LSF_LSF2
43 | Fault |  | 2PHG | 3 | Line |  |  | 36700 | 367170 |  | 1 |  | 0.14 | 0.54 | 3 | 0 | 66 | no | Line fault SHTS66 - LSF -- 2PHG | SHTS66_LSF
|  | 1 | 2PHG | 3.14 | Line |  |  | 36717 | 367172 |  | 1 |  | 0 | 0 |  |  | 66 | no | - Runback Trip LSF - LSF2 -- 2PHG | LSF_LSF2
44 | Fault |  | 2PHG | 3 | Line |  |  | 367170 | 36704 |  | 1 |  | 0.14 | 0.54 | 3 | 0 | 66 | no | Line fault LSF - KYM1 -- 2PHG | LSF_KYM1
|  | 1 | 2PHG | 3.14 | Line |  |  | 36717 | 367172 |  | 1 |  | 0 | 0 |  |  | 66 | no | - Runback Trip LSF - LSF2 -- 2PHG | LSF_LSF2
45 | Fault |  | 2PHG | 3 | Line |  |  | 36704 | 367170 |  | 1 |  | 0.14 | 0.54 | 3 | 0 | 66 | no | Line fault KYM1 - LSF -- 2PHG | KYM1_LSF
|  | 1 | 2PHG | 3.14 | Line |  |  | 36717 | 367172 |  | 1 |  | 0 | 0 |  |  | 66 | no | - Runback Trip LSF - LSF2 -- 2PHG | LSF_LSF2
46 | Fault |  | 2PHG | 3 | Line |  |  | 36700 | 36706 |  | 1 |  | 0.14 | 0.54 | 3 | -1 | 66 | no | Line fault SHTS66 - NKA -- 2PHG | SHTS66_NKA
47 | Fault |  | 2PHG | 3 | Line |  |  | 36700 | 36704 |  | 1 |  | 0.14 | 0.54 | 3 | 0 | 66 | no | Line fault SHTS66 - KYM1 -- 2PHG | SHTS66_KYM1
48 | Fault |  | 2PHG | 3 | Line |  |  | 36704 | 36700 |  | 1 |  | 0.14 | 0.54 | 3 | 0 | 66 | no | Line fault KYM1 - SHTS66 -- 2PHG | KYM1_SHTS66
49 | Fault |  | 2PHG | 3 | Line |  |  | 36704 | 36703 |  | 1 |  | 0.14 | 0.54 | 3 | 0 | 66 | no | Line fault KYM1 - ECA1 -- 2PHG | KYM1_ECA1
50 | Fault |  | 2PHG | 3 | Line |  |  | 36704 | 36703 |  | 2 |  | 0.14 | 0.54 | 3 | 0 | 66 | no | Line fault KYM1 - ECA1 -- 2PHG | KYM1_ECA1
51 | Fault |  | 2PHG | 3 | Line |  |  | 36704 | 36715 |  | 1 |  | 0.14 | 0.54 | 3 | 0 | 66 | no | Line fault KYM1 - SHP -- 2PHG | KYM1_SHP
52 | Fault |  | 2PHG | 3 | Line |  |  | 36700 | 36708 |  | 1 |  | 0.14 | 0.54 | 3 | 0 | 66 | no | Line fault SHTS66 - STN -- 2PHG | SHTS66_STN
53 | Fault |  | 2PHG | 3 | Line |  |  | 36700 | 36705 |  | 1 |  | 0.14 | 0.54 | 3 | 0 | 66 | no | Line fault SHTS66 - MNA -- 2PHG | SHTS66_MNA
54 | Fault |  | 2PHG | 3 | Line |  |  | 36700 | 36707 |  | 1 |  | 0.14 | 0.54 | 3 | 0 | 66 | no | Line fault SHTS66 - SHN1 -- 2PHG | SHTS66_SHN1
55 | Fault |  | 3PHG | 3 | Line |  |  | 36700 | 88888 |  | 1 |  | 0.14 | 0.54 | 3 | 0 | 66 | no | Line fault SHTS66 - WGNSF -- 3PHG | SHTS66_WGNSF
56 | Fault |  | 3PHG | 3 | Line |  |  | 36706 | 88888 |  | 1 |  | 0.14 | 0.54 | 3 | 0 | 66 | no | Line fault NKA - WGNSF -- 3PHG | NKA_WGNSF
57 | V_stp_profile |  | 2PHG | 3 | Line |  |  | 36700 | 36707 |  | 1 |  | 0.14 | 0.54 | 3 | 0 | 66 | no | Line fault SHTS66 - SHN1 -- 2PHG | SHTS66_SHN1
Note on A16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: LL: Fault 11: Not applicable in LL - Kiamal not in low demand case -> update: MRT, RCTS -> update the fault line: HL: 11358 - 32610 LL: 32793 - 32610
Note on A62: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Fault 46: not available: Wunghnu SF tapped in between SHST to NKA
Note on A71: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Fault 55: Added with consideration of Wunghnu connection
Note on A72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Fault 56: Added with consideration of Wunghnu connection

## Profiles
category
profile name | MAT_V_STEP_Fig3 |  | MAT_V_STEP_Fig8 |  | MAT_V_STEP_Fig9 |  | MAT_V_STEP_Fig10.1 |  | MAT_V_STEP_Fig10.2 |  | MAT_V_STEP_Fig10.3 |  | MAT_VREF_STEP_Fig2 |  | MAT_QREF_STEP_Fig4 |  | MAT_QREF_STEP_Fig4_BESS |  | MAT_QREF_STEP_Fig4.1 |  | MAT_P_STEP_Fig5 |  | MAT_P_STEP_Fig5_BESS |  | MAT_ANG_STEP+/-40deg |  | MAT_ANG_STEP+/-60deg |  | MAT_ANG_STEP |  | MAT_P_STEP_Fig12 |  | MAT_P_STEP_Fig12_BESS |  | AVAIL_P_-20% |  | AVAIL_P_+20% |  | MAT_F_RAMP_4Hzs |  | MAT_F_RAMP_2Hzs |  | MAT_P_STEP |  | V_STP_STEP_+/-5% |  | V_STEP_+/-5% |  | V_STP_STEP_-/+5% |  | V_STEP_-/+5% |  | P_STEP_+25% |  | P_STEP_+75% |  | P_STEP_-25% |  | P_STEP_-75% |  | F_RAMP_+/-1Hz_4Hzs |  | F_PROFILE_Fig6_1 |  | F_PROFILE_Fig6_2 |  | F_PROFILE_Fig6_3 |  | F_PROFILE_Fig6_4 |  | F_PROFILE_Fig7_1 |  | F_PROFILE_Fig7_2 |  | S5253_UF_short |  | S5253_OF_short |  | S5253_UF |  | S5253_OF |  | S5.2.5.3_47Hz |  | S5254_LVRT |  | S5254_HVRT |  | S5254_110_CUO |  | S5254_090_CUO |  | S5254_LVRT_REL |  | S5254_HVRT_REL |  | S5254_110_CUO_REL |  | S5254_090_CUO_REL |  | S5257_OF_ShedLoad |  | UF_TRIP |  | OF_TRIP |  | LV_TRIP |  | HV_TRIP |  | S52511_F_db |  | S52511_+/-1Hz |  | S52513_V0+/-5% |  | S52513_Vmax-2.5%/+5% |  | S52513_Vmin+2.5%/-5% |  | S52513_Q0+/-15BM |  | S52513_Q0+/-15 |  | S52513_Qmax-10/+20 |  | S52513_Qmin+10/-20 |  | S52513_Q0+/-5 |  | S52513_Qmax-10/+20 |  | S52513_Qmin+10/-20 |  | S52513_PF0+/-1% |  | S52513_PFMax-0.5%/+1.5% |  | S52513_PFMin+0.5%/-1.5% |  | S52513_V_STEP_+/-5% |  | S52514_-/+50% |  | S52514_-/+50% |  | FLAT_RUN_300 | FLAT_RUN_5 | FLAT_RUN_5 |  | FLAT_RUN_10 |  | FLAT_RUN_20 |  | S5255_85 |  | S5255_80 |  | S5255_75 |  | S5255_70 |  | S5255_60 |  | S5255_50 |  | S5255_40 |  | S5255_30 |  | S5255_115 |  | S5255_120 |  | S5255_125 |  | S5255_130 |  | S5255_135 |  | S5255_140 |  | F_PROFILE_TestFChange |  | S5.2.5.4_HVRT_temp
Scaling: the setpoint profiles: will be scaled using the bases defined in the context menu of the Setpoint block if the selected option is "absolute". If the selected option is "relative", the profile will be based on the initial value from the "setpoints" sheet. This can be useful for applying X% variation to a quantity. For the Grid source profiles: the voltage will be scaled on basekV defined in the context menu of the GridSourceBlock (absolute) or based on the initial voltage (relative). The frequency is always absolute and expressed in Hz and the setting is ignored THe Angle Profile will always be in degrees relative to the initial value, henve the setting is also ignored | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | relative |  | relative |  |  |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | relative |  | absolute |  | relative |  | absolute |  | relative |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute | [23 empty] | absolute |  | absolute |  | absolute |  | absolute |  | relative |  | relative |  | relative |  | relative | [15 empty] | relative |  | relative |  | relative |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | relative |  | absolute |  | absolute |  | relative |  | relative |  | relative |  | relative |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  |  |  | absolute
scaling factor (PSCAD / PSSE) |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 118800 |  | 118800 |  | 118800 |  | 118800 |  | 118800 | [7 empty] | 118800 |  |  | 1 | 0.0012828 | 1 | 0.0012828 | [5 empty] | 118800 | [5 empty] | 0.98039 |  |  |  | 118800 |  | 118800 |  | 118800 |  | 118800 | [61 empty] | 118800 |  | 118800 |  | 118800 |  | 118800 |  |  |  | 118800 |  | 118800 |  | 1 |  | 1 |  | 1 |  |  |  | 118800 |  | 118800
offset (PSCAD / PSSE) | [34 empty] | 0 |  | 0
| time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y
point 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 0.05 | 0 | 1000 | 0 | 311 | 0 | 50 | 0 | 50 | 0 | 1 | 0 | 1.02 | 0 | 1.02 | 0 | 1.06 | 0 | 1 | 0 | 0.05 | 0 | 0.05 | 0 | 1 | 0 | 1 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 1.02 | 0 | 1.02 | 0 | 1.02 | 0 | 1.02 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 1.02 | 0 | 1.02 | 0 | 50 | 0 | 50 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.395 | 0 | -0.395 | 0 | 0 | 0 | 0.395 | 0 | -0.395 | 0 | 1 | 0 | 0.93 | 0 | -0.93 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1.02 | 0 | 1.02 | 0 | 1.02 | 0 | 1.02 | 0 | 1.02 | 0 | 1.02 | 0 | 1.02 | 0 | 1.02 | 0 | 1.02 | 0 | 1.02 | 0 | 1.02 | 0 | 1.02 | 0 | 1.02 | 0 | 1.02 | 0 | 50 | 0 | 1.02
point 2 | 7 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 0 | 5 | 0 | 5 | 0 | 5 | 1 | 5 | 1 | 5 | 40 | 5 | 60 | 5 | 20 | 5 | 0.05 | 5 | 0.05 | 5 | 1000 | 2.5 | 311 | 5 | 50 | 5 | 50 | 5 | 1 | 5 | 1.02 | 5 | 1.02 | 5 | 1.06 | 5 | 1 | 5 | 0.05 | 5 | 0.05 | 5 | 1 | 5 | 1 | 5 | 50 | 10 | 50 | 10 | 50 | 10 | 50 | 10 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 1.02 | 5 | 1.02 | 5 | 1.02 | 5 | 1.02 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 1.02 | 5 | 1.02 | 5 | 50 | 5 | 50 | 5 | 1 | 5 | 1 | 5 | 1 | 10 | 0 | 5 | 0 | 10 | 0.395 | 10 | -0.395 | 10 | 0 | 10 | 0.395 | 10 | -0.395 | 5 | 1 | 10 | 0.93 | 10 | -0.93 | 5 | 1 | 5 | 1 | 5 | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 5 | 1.02 | 5 | 1.02 | 5 | 1.02 | 5 | 1.02 | 5 | 1.02 | 5 | 1.02 | 5 | 1.02 | 5 | 1.02 | 5 | 1.02 | 5 | 1.02 | 5 | 1.02 | 5 | 1.02 | 5 | 1.02 | 5 | 1.02 | 1 | 50 | 5 | 1.02
. | 7.001 | 1.05 | 11 | 0.9 | 5.001 | 1.1 | 5.001 | 0.1 | 5.001 | 0.5 | 5.001 | 0.8 | 5.001 | 1.05 | 5.001 | -0.3 | 5.001 | -0.3 | 5.001 | -0.15 | 5.001 | 0.5 | 5.001 | 0.5 | 15 | 0 | 15 | 0 | 15 | 0 | 5.001 | 0.2 | 5.001 | 0.2 | 35 | 490 | 2.51 | 400 | 5.5 | 52 | 6 | 52 | 7 | 1 | 5.001 | 1.071 | 5.001 | 1.071 | 5.001 | 1.007 | 5.001 | 0.95 | 5.001 | 0.3 | 5.001 | 0.8 | 5.001 | 0.75 | 5.001 | 0.25 | 5.5 | 51 | 10.5 | 52 | 10.5 | 51.75 | 10.5 | 51.5 | 10.5 | 52 | 5.75 | 47 | 8 | 47 | 5.75 | 47 | 5.5 | 52 | 5.75 | 47 | 5.5 | 52 | 5.75 | 47 | 5.001 | 0.714 | 5.001 | 1.377 | 5.001 | 1.122 | 5.001 | 0.918 | 5.001 | 0.7 | 5.001 | 1.35 | 5.001 | 1.1 | 5.001 | 0.918 | 5.5 | 50.5 | 6 | 45 | 6 | 55 | 5.001 | 0.2 | 5.001 | 1.5 | 5.5 | 50.015 | 5.5 | 51 | 5.001 | 1.05 | 5.001 | 0.975 | 5.001 | 1.025 | 10.001 | -0.126 | 5.001 | -0.126 | 10.001 | 0.32093 | 10.001 | -0.32093 | 10.001 | -0.1 | 10.001 | 0.32093 | 10.001 | -0.32093 | 5.001 | 0.99 | 10.001 | 0.94 | 10.001 | -0.94 | 5.001 | 1.05 | 15 | 0.5 | 15 | 0.5 | 300 | 1 | 5 | 1 | 10 | 1 | 20 | 1 | 5.01 | 0.85 | 5.01 | 0.8 | 5.01 | 0.75 | 5.01 | 0.7 | 5.01 | 0.6 | 5.01 | 0.5 | 5.01 | 0.4 | 5.01 | 0.3 | 5.01 | 1.15 | 5.01 | 1.2 | 5.01 | 1.25 | 5.01 | 1.3 | 5.01 | 1.35 | 5.01 | 1.4 | 1.5 | 52 | 5.001 | 1.35
. | 17 | 1.05 | 20 | 0.9 | 15 | 1.1 | 5.43 | 0.1 | 5.43 | 0.5 | 5.43 | 0.8 | 15 | 1.05 | 15 | -0.3 | 15 | -0.3 | 15 | -0.15 | 15 | 0.5 | 15 | 0.5 | 30 | 0 | 30 | 0 | 30 | 0 | 10 | 0.2 | 10 | 0.2 | 40 | 490 | 15 | 400 | 15 | 52 | 15 | 52 | 7.001 | 0.8 | 12.5 | 1.071 | 12.5 | 1.071 | 12.5 | 1.007 | 12.5 | 0.95 | 10 | 0.3 | 10 | 0.8 | 10 | 0.75 | 10 | 0.25 | 15 | 51 | 20 | 52 | 20 | 51.75 | 20 | 51.5 | 20 | 52 | 15 | 47 | 15 | 47 | 15.75 | 47 | 15.5 | 52 | 125.75 | 47 | 205.5 | 52 | 600.75 | 47 | 7 | 0.714 | 5.02 | 1.377 | 30 | 1.122 | 30 | 0.918 | 7 | 0.7 | 5.02 | 1.35 | 30 | 1.1 | 30 | 0.918 | 15.5 | 50.5 | 15 | 45 | 15 | 55 | 15 | 0.2 | 15 | 1.5 | 10.5 | 50.015 | 10.5 | 51 | 12.5 | 1.05 | 12.5 | 0.975 | 12.5 | 1.025 | 17.5 | -0.126 | 12.5 | -0.126 | 17.5 | 0.32093 | 17.5 | -0.32093 | 17.5 | -0.1 | 17.5 | 0.32093 | 17.5 | -0.32093 | 12.5 | 0.99 | 17.5 | 0.94 | 17.5 | -0.94 | 12.5 | 1.05 | 25 | 0.5 | 25 | 0.5 | [8 empty] | 5.43 | 0.85 | 5.43 | 0.8 | 5.43 | 0.75 | 5.43 | 0.7 | 5.43 | 0.6 | 5.43 | 0.5 | 5.43 | 0.4 | 5.43 | 0.3 | 5.43 | 1.15 | 5.43 | 1.2 | 5.43 | 1.25 | 5.43 | 1.3 | 5.43 | 1.35 | 5.43 | 1.4 | 6 | 52 | 5.02 | 1.35
. | 17.001 | 1 | 26 | 1.1 | 15.01 | 0.95 | 5.431 | 0.8 | 5.431 | 0.8 | 5.431 | 0.8 | 15.001 | 1 | 15.001 | 0 | 15.001 | 0 | 15.001 | 0 | 15.001 | 0.05 | 15.001 | 0.05 | [6 empty] | 10.001 | 0.4 | 10.001 | 0.4 |  |  | 45 | 400 | 15.5 | 50 | 16 | 50 | 12 | 0.8 | 12.5001 | 1.02 | 12.5001 | 1.02 | 12.5001 | 1.06 | 12.5001 | 1 | 10.001 | 0.05 | 10.001 | 0.05 | 10.001 | 1 | 10.001 | 1 | 15.5 | 50 | 20.5 | 50 | 20.5 | 50 | 20.5 | 50 | 20.5 | 50 | 15.75 | 50 | 18 | 50 | 16 | 48 | 16 | 50 | 126 | 48 | 206 | 50 | 606.5 | 50 | 7.001 | 0.816 | 5.021 | 1.326 | 30.001 | 1.02 | 30.001 | 1.02 | 7.001 | 0.8 | 5.021 | 1.3 | 30.001 | 1 | 30.001 | 1 | 16 | 50 | 16 | 50 | 16 | 50 | 15.001 | 1.02 | 15.001 | 1.02 | 11 | 50 | 11 | 50 | 12.5001 | 1 | 12.5001 | 1.025 | 12.5001 | 0.975 | 17.5001 | 0 | 12.5001 | 0 | 17.5001 | 0.54315 | 17.5001 | -0.54315 | 17.5001 | 0 | 17.5001 | 0.54315 | 17.5001 | -0.54315 | 12.5001 | 1 | 17.5001 | 0.92 | 17.5001 | -0.92 | 12.5001 | 1 | 35 | 1 | 35 | 1 | [8 empty] | 5.44 | 1.02 | 5.44 | 1.02 | 5.44 | 1.02 | 5.44 | 1.02 | 5.44 | 1.02 | 5.44 | 1.02 | 5.44 | 1.02 | 5.44 | 1.02 | 5.44 | 1.02 | 5.44 | 1.02 | 5.44 | 1.02 | 5.44 | 1.02 | 5.44 | 1.02 | 5.44 | 1.02 |  |  | 5.021 | 1.3
. | 27 | 1 | 35 | 1.1 | 25 | 0.95 | 6.43 | 1 | 6.43 | 1 | 6.43 | 1 | 25 | 1 | 25 | 0 | 25 | 0 | 25 | 0 | 25 | 0.05 | 25 | 0.05 | [6 empty] | 15 | 0.4 | 15 | 0.4 |  |  | 50 | 400 | 25 | 50 | 25 | 50 | 12.001 | 0.6 | 20 | 1.02 | 20 | 1.02 | 20 | 1.06 | 20 | 1 | 15 | 0.05 | 15 | 0.05 | 15 | 1 | 15 | 1 | 25 | 50 | 33.001 | 50 | 33.001 | 50 | 33.001 | 50 | 33.001 | 50 | 28.001 | 50 | 28.001 | 50 | 26 | 48 | 26 | 50 | 205.75 | 48 | 216 | 50 | 616 | 50 | 15 | 0.816 | 5.2 | 1.326 | 38 | 1.02 | 38 | 1.02 | 15 | 0.8 | 5.2 | 1.3 | 38 | 1 | 38 | 1 | 20 | 50 | 20 | 50 | 20 | 50 | 20 | 1.02 | 20 | 1.02 | 15 | 50 | 15 | 50 | 20 | 1 | 20 | 1.025 | 20 | 0.975 | 25 | 0 | 20 | 0 | 25 | 0.54315 | 25 | -0.54315 | 25 | 0 | 25 | 0.54315 | 25 | -0.54315 | 20 | 1 | 25 | 0.92 | 25 | -0.92 | 20 | 1 | 37 | 1 | 37 | 1 | [8 empty] | 10 | 1.02 | 10 | 1.02 | 10 | 1.02 | 10 | 1.02 | 10 | 1.02 | 10 | 1.02 | 10 | 1.02 | 10 | 1.02 | 10 | 1.02 | 10 | 1.02 | 10 | 1.02 | 10 | 1.02 | 10 | 1.02 | 10 | 1.02 |  |  | 5.2 | 1.3
. | 27.001 | 0.95 | 41 | 0.9 | 25.01 | 1.1 | 12 | 1 | 12 | 1 | 12 | 1 | 25.001 | 0.95 | 25.001 | 0.3 | 25.001 | 0.3 | 25.001 | 0.15 | 25.001 | 1 | 25.001 | 1 | [6 empty] | 15.001 | 0.6 | 15.001 | 0.6 | [8 empty] | 17 | 0.6 | 20.001 | 0.969 | [28 empty] | 26.5 | 50 |  |  | 206.25 | 50 |  |  |  |  | 15.001 | 0.918 | 5.201 | 1.275 |  |  |  |  | 15.001 | 0.9 | 5.201 | 1.25 | [14 empty] | 15.5 | 49.985 | 15.5 | 49 | 20.001 | 0.95 | 20.001 | 1 | 20.001 | 1 | 25.001 | 0.126 | 20.001 | 0.126 | 25.001 | 0.395 | 25.001 | -0.395 | 25.001 | 0.1 | 25.001 | 0.395 | 25.001 | -0.395 | 20.001 | -0.99 | 25.001 | 0.93 | 25.001 | -0.93 | 20.001 | 0.95 | [42 empty] | 5.201 | 1.25
. | 37 | 0.95 | 50 | 0.9 | 35 | 1.1 | [6 empty] | 35 | 0.95 | 35 | 0.3 | 35 | 0.3 | 35 | 0.15 | 50 | 1 | 50 | 1 | [6 empty] | 20 | 0.6 | 20 | 0.6 | [8 empty] | 17.001 | 0.4 | 27.5 | 0.969 | [28 empty] | 36 | 50 |  |  | 216 | 50 |  |  |  |  | 25 | 0.918 | 7 | 1.275 |  |  |  |  | 25 | 0.9 | 7 | 1.25 | [14 empty] | 20.5 | 49.985 | 20.5 | 49 | 27.5 | 0.95 | 25 | 1 | 25 | 1 | 32.5 | 0.126 | 27.5 | 0.126 | 30 | 0.395 | 30 | -0.395 | 32.5 | 0.1 | 30 | 0.395 | 30 | -0.395 | 27.5 | -0.99 | 30 | 0.93 | 30 | -0.93 | 27.5 | 0.95 | [42 empty] | 7 | 1.25
. | 37.001 | 1 | 56 | 1 | 35.001 | 1 | [6 empty] | 35.001 | 1 | 35.001 | 0 | 35.001 | 0 | 35.001 | 0 | [10 empty] | 20.001 | 0.8 | 20.001 | 0.8 | [8 empty] | 22 | 0.4 | 27.5001 | 1.02 | [38 empty] | 25.001 | 1.02 | 7.001 | 1.224 |  |  |  |  | 25.001 | 1 | 7.001 | 1.2 | [14 empty] | 21 | 50 | 21 | 50 | 27.5001 | 1 |  |  |  |  | 32.5001 | 0 | 27.5001 | 0 |  |  |  |  | 32.5001 | 0 |  |  |  |  | 27.5001 | 1 |  |  |  |  | 27.5001 | 1 | [42 empty] | 7.001 | 1.2
. | 47 | 1 | 65 | 1 | 45 | 1 | [6 empty] | 45 | 1 | 43 | 0 | 43 | 0 | 43 | 0 | [10 empty] | 25 | 0.8 | 25 | 0.8 | [8 empty] | 22.001 | 0.2 | 35 | 1.02 | [38 empty] | 33 | 1.02 | 25 | 1.224 |  |  |  |  | 33 | 1 | 25 | 1.2 | [14 empty] | 25 | 50 | 25 | 50 | 35 | 1 |  |  |  |  | 40 | 0 | 35 | 0 |  |  |  |  | 40 | 0 |  |  |  |  | 35 | 1 |  |  |  |  | 35 | 1 | [42 empty] | 25 | 1.2
. | [30 empty] | 25.001 | 1 | 25.001 | 1 | [8 empty] | 27 | 0.2 | [42 empty] | 25.001 | 1.173 | [6 empty] | 25.001 | 1.15 | [88 empty] | 25.001 | 1.15
. | [30 empty] | 30 | 1 | 30 | 1 | [8 empty] | 27.001 | 1 | [42 empty] | 30 | 1.173 | [6 empty] | 30 | 1.15 | [88 empty] | 30 | 1.15
. | [42 empty] | 42 | 1 | [42 empty] | 30.01 | 1.02 | [6 empty] | 30.01 | 1 | [88 empty] | 30.01 | 1.02
point n | [86 empty] | 38 | 1.02 | [6 empty] | 38 | 1 | [88 empty] | 70 | 1.02
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Category always has to be defined in the first column belonging to a new category. Every profile defined in this sheet must have a corresponging category assigned. This is used for the labelling of the output data generated by the test script.
Note on A4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: will only be used if profile type is "absolute" Reply: Used for SMA model as the voltage to be controlled at absolute Volt value
Note on Q4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Q should change to 0.3pu = 24MVAr with base being Pmax = 80MW. New actuall Q command should be 24MVAr base on 94.94MVAr = 0.2528pu
Note on S4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Q should change to 0.3pu = 24MVAr with base being Pmax = 80MW. New actuall Q command should be 24MVAr base on 94.94MVAr = 0.2528pu
Note on A5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: will only be applied if profile type is "absolute"

## Setpoints
Description: This sheet is used to initialise the model at different setpoints. The "name" of the PSCAD setting to be adjusted is for readability only and is not used. The module that contains the component is separated by a colon in case is is a submodule of "Main" The value of each parameter needs to be defined for each of the setpoint IDs | [5 empty] | AEMo min SCR | [44 empty] | AemoSCR | [44 empty] | Inf Grid | [44 empty] | AemoSCR Q-CTRL | [44 empty] | AEMO SCR Pf-Ctrl | [44 empty] | Inf Grid Q-Ctrl | [44 empty] | AEMOMin Q-Ctrl | [44 empty] | AemoSCR Q-Ctrl | [44 empty] | Aemo Min SCR Pf-Ctrl | [44 empty] | P=0.5 |  |  |  | SCR=1 |  |  |  | SCR=3 |  |  |  | P=0.5 |  | SCR=1 |  |  |  | SCR=3 |  |  |  | IniSchemeFlag=0; min SCR | IniFlag =0 AEMO SCR
[5 empty] | ParameterName | Combined- Pmax1 |  |  |  |  | Combined - Pmax2 |  |  |  |  | Combined - P0 |  |  |  |  | Combined - Pmin |  |  |  |  | BESS only - Pmax |  |  |  |  | BESS only - P0 |  |  |  |  | BESS only - Pmin |  |  |  |  | PV only - Pmax |  |  |  |  | PV only - Pmin |  |  |  |  | Combined- Pmax1 |  |  |  |  | Combined - Pmax2 |  |  |  |  | Combined - P0 |  |  |  |  | Combined - Pmin |  |  |  |  | BESS only - Pmax |  |  |  |  | BESS only - P0 |  |  |  |  | BESS only - Pmin |  |  |  |  | PV only - Pmax |  |  |  |  | PV only - Pmin |  |  |  |  | Combined- Pmax1 |  |  |  |  | Combined - Pmax2 |  |  |  |  | Combined - P0 |  |  |  |  | Combined - Pmin |  |  |  |  | BESS only - Pmax |  |  |  |  | BESS only - P0 |  |  |  |  | BESS only - Pmin |  |  |  |  | PV only - Pmax |  |  |  |  | PV only - Pmin |  |  |  |  | Combined- Pmax1 |  |  |  |  | Combined - Pmax2 |  |  |  |  | Combined - P0 |  |  |  |  | Combined - Pmin |  |  |  |  | BESS only - Pmax |  |  |  |  | BESS only - P0 |  |  |  |  | BESS only - Pmin |  |  |  |  | PV only - Pmax |  |  |  |  | PV only - Pmin |  |  |  |  | Combined- Pmax1 |  |  |  |  | Combined - Pmax2 |  |  |  |  | Combined - P0 |  |  |  |  | Combined - Pmin |  |  |  |  | BESS only - Pmax |  |  |  |  | BESS only - P0 |  |  |  |  | BESS only - Pmin |  |  |  |  | PV only - Pmax |  |  |  |  | PV only - Pmin |  |  |  |  | Combined- Pmax1 |  |  |  |  | Combined - Pmax2 |  |  |  |  | Combined - P0 |  |  |  |  | Combined - Pmin |  |  |  |  | BESS only - Pmax |  |  |  |  | BESS only - P0 |  |  |  |  | BESS only - Pmin |  |  |  |  | PV only - Pmax |  |  |  |  | PV only - Pmin |  |  |  |  | Combined- Pmax1 |  |  |  |  | Combined - Pmax2 |  |  |  |  | Combined - P0 |  |  |  |  | Combined - Pmin |  |  |  |  | BESS only - Pmax |  |  |  |  | BESS only - P0 |  |  |  |  | BESS only - Pmin |  |  |  |  | PV only - Pmax |  |  |  |  | PV only - Pmin |  |  |  |  | Combined- Pmax1 |  |  |  |  | Combined - Pmax2 |  |  |  |  | Combined - P0 |  |  |  |  | Combined - Pmin |  |  |  |  | BESS only - Pmax |  |  |  |  | BESS only - P0 |  |  |  |  | BESS only - Pmin |  |  |  |  | PV only - Pmax |  |  |  |  | PV only - Pmin |  |  |  |  | Combined- Pmax1 |  |  |  |  | Combined - Pmax2 |  |  |  |  | Combined - P0 |  |  |  |  | Combined - Pmin |  |  |  |  | BESS only - Pmax |  |  |  |  | BESS only - P0 |  |  |  |  | BESS only - Pmin |  |  |  |  | PV only - Pmax |  |  |  |  | PV only - Pmin |  |  |  |  | AemoSCR PV+BESS | AEMo SCR BESS | AemoSCR PV+BESS avail_P_50 | AEMo SCR BESS Avail_P_50 | X/R=14, PV+BESS | X/R=14, BESS | X/R=3, PV+BESS | X/R=3, BESS | X/R=14, PV+BESS | X/R=14, BESS | X/R=3, PV+BESS | X/R=3, BESS | AemoSCR PV | AEMo SCR BESS | X/R=14, PV | X/R=14, BESS | X/R=3, PV | X/R=3, BESS | X/R=14, PV | X/R=14, BESS | X/R=3, PV | X/R=3, BESS
GENERAL |  |  |  |  | Setpoint ID | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212 | 213 | 214 | 215 | 216 | 217 | 218 | 219 | 220 | 221 | 222 | 223 | 224 | 225 | 226 | 227 | 228 | 229 | 230 | 231 | 232 | 233 | 234 | 235 | 236 | 237 | 238 | 239 | 240 | 241 | 242 | 243 | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273 | 274 | 275 | 276 | 277 | 278 | 279 | 280 | 281 | 282 | 283 | 284 | 285 | 286 | 287 | 288 | 289 | 290 | 291 | 292 | 293 | 294 | 295 | 296 | 297 | 298 | 299 | 300 | 301 | 302 | 303 | 304 | 305 | 306 | 307 | 308 | 309 | 310 | 311 | 312 | 313 | 314 | 315 | 316 | 317 | 318 | 319 | 320 | 321 | 322 | 323 | 324 | 325 | 326 | 327 | 328 | 329 | 330 | 331 | 332 | 333 | 334 | 335 | 336 | 337 | 338 | 339 | 340 | 341 | 342 | 343 | 344 | 345 | 346 | 347 | 348 | 349 | 350 | 351 | 352 | 353 | 354 | 355 | 356 | 357 | 358 | 359 | 360 | 361 | 362 | 363 | 364 | 365 | 366 | 367 | 368 | 369 | 370 | 371 | 372 | 373 | 374 | 375 | 376 | 377 | 378 | 379 | 380 | 381 | 382 | 383 | 384 | 385 | 386 | 387 | 388 | 389 | 390 | 391 | 392 | 393 | 394 | 395 | 396 | 397 | 398 | 399 | 400 | 401 | 402 | 403 | 404 | 405 | 406 | 407 | 408 | 409 | 410 | 411 | 412 | 413 | 414 | 415 | 416 | 417 | 418 | 419 | 420 | 421 | 422 | 423 | 424 | 425 | 426 | 427 | 428 | 429
[5 empty] | GridMVA | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 882.3 | 882.3 | 882.3 | 882.3 | 118.8 | 118.8 | 118.8 | 118.8 | 356.4 | 356.4 | 356.4 | 356.4 | 1109 | 1109 | 118.8 | 118.8 | 118.8 | 118.8 | 356.4 | 356.4 | 356.4 | 356.4 | 483 | 1109
system normal voltage | 1.02 |  |  |  | SCR | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 8403.35 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 9.32 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 7.41 | 7.41 | 7.41 | 7.41 | 1 | 1 | 1 | 1 | 2.99 | 2.99 | 2.99 | 2.99 | 9.32 | 9.32 | 1 | 1 | 1 | 1 | 2.99 | 2.99 | 2.99 | 2.99 | 4.06 | 9.32
droop | 0.05 |  |  |  | X_R | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.43 | 3.43 | 3.43 | 3.43 | 14 | 14 | 3 | 3 | 14 | 14 | 3 | 3 | 3.43 | 3.43 | 14 | 14 | 3 | 3 | 14 | 14 | 3 | 3 | 3.42 | 3.43
droop basis | 46.926 |  |  |  | Pini | 1 | 1 | 1 | 1 | 1 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0 | 0.5 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0.5 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1
[5 empty] | P1ini | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0.5 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0.5 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0
[5 empty] | Qini | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Q1ini | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pavai | bar: Combined- Pmax1 1 to X/R=3, BESS 429
[5 empty] | V_POC | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02
[5 empty] | P | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 68.904 | 68.904 | 68.904 | 68.904 | 68.904 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 68.904 | 68.904 | 68.904 | 68.904 | 68.904 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 68.904 | 68.904 | 68.904 | 68.904 | 68.904 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 68.904 | 68.904 | 68.904 | 68.904 | 68.904 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 68.904 | 68.904 | 68.904 | 68.904 | 68.904 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 68.904 | 68.904 | 68.904 | 68.904 | 68.904 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 68.904 | 68.904 | 68.904 | 68.904 | 68.904 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 68.904 | 68.904 | 68.904 | 68.904 | 68.904 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 68.904 | 68.904 | 68.904 | 68.904 | 68.904 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 59.4 | 0 | 59.4 | 0 | 118.8 | 0 | 118.8 | 0 | 118.8 | 0 | 118.8 | 0 | 59.4 | 0 | 118.8 | 0 | 118.8 | 0 | 118.8 | 0 | 118.8 | 0 | 118.8 | 118.8
[5 empty] | Q | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 0 | -15 | 0 | -15 | 0 | 0 | -15 | 0 | -15 | 0 | 0 | -15 | 0 | -15 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 0 | -15 | 0 | -15 | 0 | 0 | -15 | 0 | -15 | 0 | 0 | -15 | 0 | -15 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 0 | -15 | 0 | -15 | 0 | 0 | -15 | 0 | -15 | 0 | 0 | -15 | 0 | -15 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 0 | -15 | 0 | -15 | 0 | 0 | -15 | 0 | -15 | 0 | 0 | -15 | 0 | -15 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 0 | -15 | 0 | -15 | 0 | 0 | -15 | 0 | -15 | 0 | 0 | -15 | 0 | -15 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 0 | -15 | 0 | -15 | 0 | 0 | -15 | 0 | -15 | 0 | 0 | -15 | 0 | -15 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 0 | -15 | 0 | -15 | 0 | 0 | -15 | 0 | -15 | 0 | 0 | -15 | 0 | -15 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 0 | -15 | 0 | -15 | 0 | 0 | -15 | 0 | -15 | 0 | 0 | -15 | 0 | -15 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 0 | -15 | 0 | -15 | 0 | 0 | -15 | 0 | -15 | 0 | 0 | -15 | 0 | -15 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PSSE-specific |  |  |  |  | P_PV1 | 119.18 | 119.18 | 119.18 | 118.9 | 118.9 | 68.904 | 68.904 | 68.904 | 68.904 | 68.904 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | [15 empty] | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 68.904 | 68.904 | 68.904 | 68.904 | 68.904 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | [15 empty] | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 68.904 | 68.904 | 68.904 | 68.904 | 68.904 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | [15 empty] | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 119.18 | 119.18 | 119.18 | 118.9 | 118.9 | 68.904 | 68.904 | 68.904 | 68.904 | 68.904 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | [15 empty] | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 68.904 | 68.904 | 68.904 | 68.904 | 68.904 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | [15 empty] | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 68.904 | 68.904 | 68.904 | 68.904 | 68.904 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | [15 empty] | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 68.904 | 68.904 | 68.904 | 68.904 | 68.904 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | [15 empty] | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 68.904 | 68.904 | 68.904 | 68.904 | 68.904 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | [15 empty] | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 68.904 | 68.904 | 68.904 | 68.904 | 68.904 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | [15 empty] | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 59.95 |  | 59.95 | 0 | 118.9 |  | 118.9 |  | 118.9 |  | 118.9 |  | 59.4 |  | 118.8 |  | 118.8 |  | 118.8 |  | 118.8 |  | 118.8 | 118.8
[5 empty] | Q_PV1 | 7.1921 | 29.6429 | -6.832 | 36.217 | -10.058 | 11.158 | [29 empty] | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 7.1921 | 29.6429 | -6.832 | 36.217 | -10.058 | 11.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [15 empty] | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 7.1921 | 29.6429 | -6.832 | 36.217 | -10.058 | 11.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [15 empty] | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 7.1921 | 29.6429 | -6.832 | 36.217 | -10.058 | 11.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [15 empty] | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 7.1921 | 29.6429 | -6.832 | 36.217 | -10.058 | 11.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [15 empty] | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 7.1921 | 29.6429 | -6.832 | 36.217 | -10.058 | 11.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [15 empty] | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 7.1921 | 29.6429 | -6.832 | 36.217 | -10.058 | 11.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [15 empty] | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 7.1921 | 29.6429 | -6.832 | 36.217 | -10.058 | 11.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [15 empty] | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 7.1921 | 29.6429 | -6.832 | 36.217 | -10.058 | 11.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [15 empty] | 0 | 35.64 | -35.64 | 46.926 | -46.926 | 0 | 35.64 | -35.64 | 46.926 | -46.926 | -1.9087 |  | -1.9087 |  | -0.3 |  | -0.3 |  | -0.3 |  | -0.3 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
[5 empty] | LOC_PV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | [15 empty] | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | [15 empty] | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | [15 empty] | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | [15 empty] | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | [15 empty] | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | [15 empty] | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | [15 empty] | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | [15 empty] | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | [15 empty] | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | HV1 | MV1 |  | MV1 |  | MV1 |  | MV1 |  | MV1 |  | MV1 |  | HV1 |  | HV1 |  | HV1 |  | HV1 |  | HV1 |  | HV1 | HV1
[5 empty] | BUS_PV1 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | [15 empty] | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | [15 empty] | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | [15 empty] | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | [15 empty] | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | [15 empty] | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | [15 empty] | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | [15 empty] | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | [15 empty] | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | [15 empty] | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 |  | 334095 |  | 334095 |  | 334095 |  | 334095 |  | 334095 |  | 334095 |  | 334095 |  | 334095 |  | 334095 |  | 334095 |  | 334095 | 334095
|  |  |  | c | offline_machines | BESS only - Pmax 21: [334095]; BESS only - Pmax 22: [334095]; BESS only - Pmax 23: [334095]; BESS only - Pmax 24: [334095]; BESS only - Pmax 25: [334095]; BESS only - P0 26: [334095]; BESS only - P0 27: [334095]; BESS only - P0 28: [334095]; BESS only - P0 29: [334095]; BESS only - P0 30: [334095]; BESS only - Pmin 31: [334095]; BESS only - Pmin 32: [334095]; BESS only - Pmin 33: [334095]; BESS only - Pmin 34: [334095]; BESS only - Pmin 35: [334095]; BESS only - Pmax 66: [334095]; BESS only - Pmax 67: [334095]; BESS only - Pmax 68: [334095]; BESS only - Pmax 69: [334095]; BESS only - Pmax 70: [334095]; BESS only - P0 71: [334095]; BESS only - P0 72: [334095]; BESS only - P0 73: [334095]; BESS only - P0 74: [334095]; BESS only - P0 75: [334095]; BESS only - Pmin 76: [334095]; BESS only - Pmin 77: [334095]; BESS only - Pmin 78: [334095]; BESS only - Pmin 79: [334095]; BESS only - Pmin 80: [334095]; BESS only - Pmax 111: [334095]; BESS only - Pmax 112: [334095]; BESS only - Pmax 113: [334095]; BESS only - Pmax 114: [334095]; BESS only - Pmax 115: [334095]; BESS only - P0 116: [334095]; BESS only - P0 117: [334095]; BESS only - P0 118: [334095]; BESS only - P0 119: [334095]; BESS only - P0 120: [334095]; BESS only - Pmin 121: [334095]; BESS only - Pmin 122: [334095]; BESS only - Pmin 123: [334095]; BESS only - Pmin 124: [334095]; BESS only - Pmin 125: [334095]; BESS only - Pmax 156: [334095]; BESS only - Pmax 157: [334095]; BESS only - Pmax 158: [334095]; BESS only - Pmax 159: [334095]; BESS only - Pmax 160: [334095]; BESS only - P0 161: [334095]; BESS only - P0 162: [334095]; BESS only - P0 163: [334095]; BESS only - P0 164: [334095]; BESS only - P0 165: [334095]; BESS only - Pmin 166: [334095]; BESS only - Pmin 167: [334095]; BESS only - Pmin 168: [334095]; BESS only - Pmin 169: [334095]; BESS only - Pmin 170: [334095]; BESS only - Pmax 201: [334095]; BESS only - Pmax 202: [334095]; BESS only - Pmax 203: [334095]; BESS only - Pmax 204: [334095]; BESS only - Pmax 205: [334095]; BESS only - P0 206: [334095]; BESS only - P0 207: [334095]; BESS only - P0 208: [334095]; BESS only - P0 209: [334095]; BESS only - P0 210: [334095]; BESS only - Pmin 211: [334095]; BESS only - Pmin 212: [334095]; BESS only - Pmin 213: [334095]; BESS only - Pmin 214: [334095]; BESS only - Pmin 215: [334095]; BESS only - Pmax 246: [334095]; BESS only - Pmax 247: [334095]; BESS only - Pmax 248: [334095]; BESS only - Pmax 249: [334095]; BESS only - Pmax 250: [334095]; BESS only - P0 251: [334095]; BESS only - P0 252: [334095]; BESS only - P0 253: [334095]; BESS only - P0 254: [334095]; BESS only - P0 255: [334095]; BESS only - Pmin 256: [334095]; BESS only - Pmin 257: [334095]; BESS only - Pmin 258: [334095]; BESS only - Pmin 259: [334095]; BESS only - Pmin 260: [334095]; BESS only - Pmax 291: [334095]; BESS only - Pmax 292: [334095]; BESS only - Pmax 293: [334095]; BESS only - Pmax 294: [334095]; BESS only - Pmax 295: [334095]; BESS only - P0 296: [334095]; BESS only - P0 297: [334095]; BESS only - P0 298: [334095]; BESS only - P0 299: [334095]; BESS only - P0 300: [334095]; BESS only - Pmin 301: [334095]; BESS only - Pmin 302: [334095]; BESS only - Pmin 303: [334095]; BESS only - Pmin 304: [334095]; BESS only - Pmin 305: [334095]; BESS only - Pmax 336: [334095]; BESS only - Pmax 337: [334095]; BESS only - Pmax 338: [334095]; BESS only - Pmax 339: [334095]; BESS only - Pmax 340: [334095]; BESS only - P0 341: [334095]; BESS only - P0 342: [334095]; BESS only - P0 343: [334095]; BESS only - P0 344: [334095]; BESS only - P0 345: [334095]; BESS only - Pmin 346: [334095]; BESS only - Pmin 347: [334095]; BESS only - Pmin 348: [334095]; BESS only - Pmin 349: [334095]; BESS only - Pmin 350: [334095]; BESS only - Pmax 381: [334095]; BESS only - Pmax 382: [334095]; BESS only - Pmax 383: [334095]; BESS only - Pmax 384: [334095]; BESS only - Pmax 385: [334095]; BESS only - P0 386: [334095]; BESS only - P0 387: [334095]; BESS only - P0 388: [334095]; BESS only - P0 389: [334095]; BESS only - P0 390: [334095]; BESS only - Pmin 391: [334095]; BESS only - Pmin 392: [334095]; BESS only - Pmin 393: [334095]; BESS only - Pmin 394: [334095]; BESS only - Pmin 395: [334095]; AEMo SCR BESS 407: [334095]; AEMo SCR BESS Avail_P_50 409: [334095]; X/R=14, BESS 411: [334095]; X/R=3, BESS 413: [334095]; X/R=14, BESS 415: [334095]; X/R=3, BESS 417: [334095]; AEMo SCR BESS 419: [334095]; X/R=14, BESS 421: [334095]; X/R=3, BESS 423: [334095]; X/R=14, BESS 425: [334095]; X/R=3, BESS 427: [334095]
[5 empty] | disconnect_buses | BESS only - Pmax 21: [334092, 334093, 334094, 334095]; BESS only - Pmax 22: [334092, 334093, 334094, 334095]; BESS only - Pmax 23: [334092, 334093, 334094, 334095]; BESS only - Pmax 24: [334092, 334093, 334094, 334095]; BESS only - Pmax 25: [334092, 334093, 334094, 334095]; BESS only - P0 26: [334092, 334093, 334094, 334095]; BESS only - P0 27: [334092, 334093, 334094, 334095]; BESS only - P0 28: [334092, 334093, 334094, 334095]; BESS only - P0 29: [334092, 334093, 334094, 334095]; BESS only - P0 30: [334092, 334093, 334094, 334095]; BESS only - Pmin 31: [334092, 334093, 334094, 334095]; BESS only - Pmin 32: [334092, 334093, 334094, 334095]; BESS only - Pmin 33: [334092, 334093, 334094, 334095]; BESS only - Pmin 34: [334092, 334093, 334094, 334095]; BESS only - Pmin 35: [334092, 334093, 334094, 334095]; BESS only - Pmax 66: [334092, 334093, 334094, 334095]; BESS only - Pmax 67: [334092, 334093, 334094, 334095]; BESS only - Pmax 68: [334092, 334093, 334094, 334095]; BESS only - Pmax 69: [334092, 334093, 334094, 334095]; BESS only - Pmax 70: [334092, 334093, 334094, 334095]; BESS only - P0 71: [334092, 334093, 334094, 334095]; BESS only - P0 72: [334092, 334093, 334094, 334095]; BESS only - P0 73: [334092, 334093, 334094, 334095]; BESS only - P0 74: [334092, 334093, 334094, 334095]; BESS only - P0 75: [334092, 334093, 334094, 334095]; BESS only - Pmin 76: [334092, 334093, 334094, 334095]; BESS only - Pmin 77: [334092, 334093, 334094, 334095]; BESS only - Pmin 78: [334092, 334093, 334094, 334095]; BESS only - Pmin 79: [334092, 334093, 334094, 334095]; BESS only - Pmin 80: [334092, 334093, 334094, 334095]; BESS only - Pmax 111: [334092, 334093, 334094, 334095]; BESS only - Pmax 112: [334092, 334093, 334094, 334095]; BESS only - Pmax 113: [334092, 334093, 334094, 334095]; BESS only - Pmax 114: [334092, 334093, 334094, 334095]; BESS only - Pmax 115: [334092, 334093, 334094, 334095]; BESS only - P0 116: [334092, 334093, 334094, 334095]; BESS only - P0 117: [334092, 334093, 334094, 334095]; BESS only - P0 118: [334092, 334093, 334094, 334095]; BESS only - P0 119: [334092, 334093, 334094, 334095]; BESS only - P0 120: [334092, 334093, 334094, 334095]; BESS only - Pmin 121: [334092, 334093, 334094, 334095]; BESS only - Pmin 122: [334092, 334093, 334094, 334095]; BESS only - Pmin 123: [334092, 334093, 334094, 334095]; BESS only - Pmin 124: [334092, 334093, 334094, 334095]; BESS only - Pmin 125: [334092, 334093, 334094, 334095]; BESS only - Pmax 156: [334092, 334093, 334094, 334095]; BESS only - Pmax 157: [334092, 334093, 334094, 334095]; BESS only - Pmax 158: [334092, 334093, 334094, 334095]; BESS only - Pmax 159: [334092, 334093, 334094, 334095]; BESS only - Pmax 160: [334092, 334093, 334094, 334095]; BESS only - P0 161: [334092, 334093, 334094, 334095]; BESS only - P0 162: [334092, 334093, 334094, 334095]; BESS only - P0 163: [334092, 334093, 334094, 334095]; BESS only - P0 164: [334092, 334093, 334094, 334095]; BESS only - P0 165: [334092, 334093, 334094, 334095]; BESS only - Pmin 166: [334092, 334093, 334094, 334095]; BESS only - Pmin 167: [334092, 334093, 334094, 334095]; BESS only - Pmin 168: [334092, 334093, 334094, 334095]; BESS only - Pmin 169: [334092, 334093, 334094, 334095]; BESS only - Pmin 170: [334092, 334093, 334094, 334095]; BESS only - Pmax 201: [334092, 334093, 334094, 334095]; BESS only - Pmax 202: [334092, 334093, 334094, 334095]; BESS only - Pmax 203: [334092, 334093, 334094, 334095]; BESS only - Pmax 204: [334092, 334093, 334094, 334095]; BESS only - Pmax 205: [334092, 334093, 334094, 334095]; BESS only - P0 206: [334092, 334093, 334094, 334095]; BESS only - P0 207: [334092, 334093, 334094, 334095]; BESS only - P0 208: [334092, 334093, 334094, 334095]; BESS only - P0 209: [334092, 334093, 334094, 334095]; BESS only - P0 210: [334092, 334093, 334094, 334095]; BESS only - Pmin 211: [334092, 334093, 334094, 334095]; BESS only - Pmin 212: [334092, 334093, 334094, 334095]; BESS only - Pmin 213: [334092, 334093, 334094, 334095]; BESS only - Pmin 214: [334092, 334093, 334094, 334095]; BESS only - Pmin 215: [334092, 334093, 334094, 334095]; BESS only - Pmax 246: [334092, 334093, 334094, 334095]; BESS only - Pmax 247: [334092, 334093, 334094, 334095]; BESS only - Pmax 248: [334092, 334093, 334094, 334095]; BESS only - Pmax 249: [334092, 334093, 334094, 334095]; BESS only - Pmax 250: [334092, 334093, 334094, 334095]; BESS only - P0 251: [334092, 334093, 334094, 334095]; BESS only - P0 252: [334092, 334093, 334094, 334095]; BESS only - P0 253: [334092, 334093, 334094, 334095]; BESS only - P0 254: [334092, 334093, 334094, 334095]; BESS only - P0 255: [334092, 334093, 334094, 334095]; BESS only - Pmin 256: [334092, 334093, 334094, 334095]; BESS only - Pmin 257: [334092, 334093, 334094, 334095]; BESS only - Pmin 258: [334092, 334093, 334094, 334095]; BESS only - Pmin 259: [334092, 334093, 334094, 334095]; BESS only - Pmin 260: [334092, 334093, 334094, 334095]; BESS only - Pmax 291: [334092, 334093, 334094, 334095]; BESS only - Pmax 292: [334092, 334093, 334094, 334095]; BESS only - Pmax 293: [334092, 334093, 334094, 334095]; BESS only - Pmax 294: [334092, 334093, 334094, 334095]; BESS only - Pmax 295: [334092, 334093, 334094, 334095]; BESS only - P0 296: [334092, 334093, 334094, 334095]; BESS only - P0 297: [334092, 334093, 334094, 334095]; BESS only - P0 298: [334092, 334093, 334094, 334095]; BESS only - P0 299: [334092, 334093, 334094, 334095]; BESS only - P0 300: [334092, 334093, 334094, 334095]; BESS only - Pmin 301: [334092, 334093, 334094, 334095]; BESS only - Pmin 302: [334092, 334093, 334094, 334095]; BESS only - Pmin 303: [334092, 334093, 334094, 334095]; BESS only - Pmin 304: [334092, 334093, 334094, 334095]; BESS only - Pmin 305: [334092, 334093, 334094, 334095]; BESS only - Pmax 336: [334092, 334093, 334094, 334095]; BESS only - Pmax 337: [334092, 334093, 334094, 334095]; BESS only - Pmax 338: [334092, 334093, 334094, 334095]; BESS only - Pmax 339: [334092, 334093, 334094, 334095]; BESS only - Pmax 340: [334092, 334093, 334094, 334095]; BESS only - P0 341: [334092, 334093, 334094, 334095]; BESS only - P0 342: [334092, 334093, 334094, 334095]; BESS only - P0 343: [334092, 334093, 334094, 334095]; BESS only - P0 344: [334092, 334093, 334094, 334095]; BESS only - P0 345: [334092, 334093, 334094, 334095]; BESS only - Pmin 346: [334092, 334093, 334094, 334095]; BESS only - Pmin 347: [334092, 334093, 334094, 334095]; BESS only - Pmin 348: [334092, 334093, 334094, 334095]; BESS only - Pmin 349: [334092, 334093, 334094, 334095]; BESS only - Pmin 350: [334092, 334093, 334094, 334095]; BESS only - Pmax 381: [334092, 334093, 334094, 334095]; BESS only - Pmax 382: [334092, 334093, 334094, 334095]; BESS only - Pmax 383: [334092, 334093, 334094, 334095]; BESS only - Pmax 384: [334092, 334093, 334094, 334095]; BESS only - Pmax 385: [334092, 334093, 334094, 334095]; BESS only - P0 386: [334092, 334093, 334094, 334095]; BESS only - P0 387: [334092, 334093, 334094, 334095]; BESS only - P0 388: [334092, 334093, 334094, 334095]; BESS only - P0 389: [334092, 334093, 334094, 334095]; BESS only - P0 390: [334092, 334093, 334094, 334095]; BESS only - Pmin 391: [334092, 334093, 334094, 334095]; BESS only - Pmin 392: [334092, 334093, 334094, 334095]; BESS only - Pmin 393: [334092, 334093, 334094, 334095]; BESS only - Pmin 394: [334092, 334093, 334094, 334095]; BESS only - Pmin 395: [334092, 334093, 334094, 334095]; AEMo SCR BESS 407: [334092, 334093, 334094, 334095]; AEMo SCR BESS Avail_P_50 409: [334092, 334093, 334094, 334095]; X/R=14, BESS 411: [334092, 334093, 334094, 334095]; X/R=3, BESS 413: [334092, 334093, 334094, 334095]; X/R=14, BESS 415: [334092, 334093, 334094, 334095]; X/R=3, BESS 417: [334092, 334093, 334094, 334095]; AEMo SCR BESS 419: [334092, 334093, 334094, 334095]; X/R=14, BESS 421: [334092, 334093, 334094, 334095]; X/R=3, BESS 423: [334092, 334093, 334094, 334095]; X/R=14, BESS 425: [334092, 334093, 334094, 334095]; X/R=3, BESS 427: [334092, 334093, 334094, 334095]
[5 empty] | TR1_from | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | [15 empty] | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | [15 empty] | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | [15 empty] | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | [15 empty] | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | [15 empty] | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | [15 empty] | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | [15 empty] | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | [15 empty] | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | [15 empty] | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 |  | 334091 |  | 334091 |  | 334091 |  | 334091 |  | 334091 |  | 334091 |  | 334091 |  | 334091 |  | 334091 |  | 334091 |  | 334091 | 334091
[5 empty] | TR1_to | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | [15 empty] | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | [15 empty] | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | [15 empty] | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | [15 empty] | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | [15 empty] | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | [15 empty] | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | [15 empty] | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | [15 empty] | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | [15 empty] | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 |  | 334090 |  | 334090 |  | 334090 |  | 334090 |  | 334090 |  | 334090 |  | 334090 |  | 334090 |  | 334090 |  | 334090 |  | 334090 | 334090
[5 empty] | TR1_tap | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 0.9875 | 1.025 | 0.9625 | 1.025 | 0.9625 | 0.9875 | 1.0125 | 0.9625 | 1.025 | 0.9625 | 1 | 1 | 0.9875 | 1.0125 | 0.9875 | 0.9875 | 1 | 0.975 | 1 | 0.975 | 0.9875 | 1 | 0.975 | 1 | 0.975 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 0.9875 | 1.0125 | 0.9625 | 1.025 | 0.9625 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 0.9875 | 1.025 | 0.9625 | 1.025 | 0.9625 | 0.9875 | 1.0125 | 0.9625 | 1.025 | 0.9625 | 1 | 1 | 0.9875 | 1.0125 | 0.9875 | 0.9875 | 1 | 0.975 | 1 | 0.975 | 0.9875 | 1 | 0.975 | 1 | 0.975 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 0.9875 | 1.0125 | 0.9625 | 1.025 | 0.9625 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 0.9875 | 1.025 | 0.9625 | 1.025 | 0.9625 | 0.9875 | 1.0125 | 0.9625 | 1.025 | 0.9625 | 1 | 1 | 0.9875 | 1.0125 | 0.9875 | 0.9875 | 1 | 0.975 | 1 | 0.975 | 0.9875 | 1 | 0.975 | 1 | 0.975 | 1 | 1.025 | 0.975 | 1.05 | 0.9625 | 0.9875 | 1.0125 | 0.9625 | 1.025 | 0.9625 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 0.9875 | 1.025 | 0.9625 | 1.025 | 0.9625 | 0.9875 | 1.0125 | 0.9625 | 1.025 | 0.9625 | 1 | 1 | 0.9875 | 1.0125 | 0.9875 | 0.9875 | 1 | 0.975 | 1 | 0.975 | 0.9875 | 1 | 0.975 | 1 | 0.975 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 0.9875 | 1.0125 | 0.9625 | 1.025 | 0.9625 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 0.9875 | 1.025 | 0.9625 | 1.025 | 0.9625 | 0.9875 | 1.0125 | 0.9625 | 1.025 | 0.9625 | 1 | 1 | 0.9875 | 1.0125 | 0.9875 | 0.9875 | 1 | 0.975 | 1 | 0.975 | 0.9875 | 1 | 0.975 | 1 | 0.975 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 0.9875 | 1.0125 | 0.9625 | 1.025 | 0.9625 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 0.9875 | 1.025 | 0.9625 | 1.025 | 0.9625 | 0.9875 | 1.0125 | 0.9625 | 1.025 | 0.9625 | 1 | 1 | 0.9875 | 1.0125 | 0.9875 | 0.9875 | 1 | 0.975 | 1 | 0.975 | 0.9875 | 1 | 0.975 | 1 | 0.975 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 0.9875 | 1.0125 | 0.9625 | 1.025 | 0.9625 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 0.9875 | 1.025 | 0.9625 | 1.025 | 0.9625 | 0.9875 | 1.0125 | 0.9625 | 1.025 | 0.9625 | 1 | 1 | 0.9875 | 1.0125 | 0.9875 | 0.9875 | 1 | 0.975 | 1 | 0.975 | 0.9875 | 1 | 0.975 | 1 | 0.975 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 0.9875 | 1.0125 | 0.9625 | 1.025 | 0.9625 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 0.9875 | 1.025 | 0.9625 | 1.025 | 0.9625 | 0.9875 | 1.0125 | 0.9625 | 1.025 | 0.9625 | 1 | 1 | 0.9875 | 1.0125 | 0.9875 | 0.9875 | 1 | 0.975 | 1 | 0.975 | 0.9875 | 1 | 0.975 | 1 | 0.975 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 0.9875 | 1.0125 | 0.9625 | 1.025 | 0.9625 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 0.9875 | 1.025 | 0.9625 | 1.025 | 0.9625 | 0.9875 | 1.0125 | 0.9625 | 1.025 | 0.9625 | 1 | 1 | 0.9875 | 1.0125 | 0.9875 | 0.9875 | 1 | 0.975 | 1 | 0.975 | 0.9875 | 1 | 0.975 | 1 | 0.975 | 1 | 1.025 | 0.975 | 1.0375 | 0.9625 | 0.9875 | 1.0125 | 0.9625 | 1.025 | 0.9625 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9875 | 0.9875 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[5 empty] | dyr | [45 empty] | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | HOR_v0_8.dyr | [55 empty] | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_Q.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | HOR_v0_8_PF.dyr | [22 empty] | HOR_v0_8_INI.dyr | HOR_v0_8_INI.dyr
PSCAD-specific | Name | ProjectNo | Module | PSCAD ID | Symbol
| GridSource | Project1 | Main | 1927070795 | SCL | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 882.3 | 882.3 | 882.3 | 882.3 | 118.8 | 118.8 | 118.8 | 118.8 | 356.4 | 356.4 | 356.4 | 356.4 | 1109 | 1109 | 118.8 | 118.8 | 118.8 | 118.8 | 356.4 | 356.4 | 356.4 | 356.4 | 483 | 1109
| GridSource | Project1 | Main | 1927070795 | X_R | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.43 | 3.43 | 3.43 | 3.43 | 14 | 14 | 3 | 3 | 14 | 14 | 3 | 3 | 3.43 | 3.43 | 14 | 14 | 3 | 3 | 14 | 14 | 3 | 3 | 3.42 | 3.43
| V setpoint | Project1 | Main | 163769877 | VstpDefault | 1.02 | 1.058 | 0.98203 | 1.07 | 0.97 | 1.02 | 1.058 | 0.98203 | 1.07 | 0.97 | 1.02 | 1.058 | 0.98203 | 1.07 | 0.97 | 1.02 | 1.058 | 0.98203 | 1.07 | 0.97 | 0.996 | 1.0384 | 0.954 | 1.052 | 0.954 | 0.99 | 1.0324 | 0.9505 | 1.046 | 0.9505 | 0.995 | 1.0378 | 0.9535 | 1.0515 | 0.9535 | 1.02 | 1.058 | 0.98203 | 1.041 | 0.999 | 1.02 | 1.058 | 0.98203 | 1.041 | 0.999 | 1.0198 | 1.043 | 0.9965 | 1.0517 | 0.9895 | 1.0198 | 1.043 | 0.9965 | 1.0517 | 0.9895 | 1.0123 | 1.036 | 0.9896 | 1.0435 | 0.9835 | 1.0135 | 1.0382 | 0.9915 | 1.0544 | 0.9848 | 0.996 | 1.0384 | 0.954 | 1.052 | 0.954 | 0.99 | 1.0324 | 0.9505 | 1.046 | 0.9505 | 0.995 | 1.0378 | 0.9535 | 1.0515 | 0.9535 | 1.02 | 1.058 | 0.98203 | 1.041 | 0.999 | 1.02 | 1.058 | 0.98203 | 1.041 | 0.999 | 1.0198 | 1.043 | 0.9965 | 1.0517 | 0.9895 | 1.0198 | 1.043 | 0.9965 | 1.0517 | 0.9895 | 1.0123 | 1.036 | 0.9896 | 1.0435 | 0.9835 | 1.0135 | 1.0382 | 0.9915 | 1.0544 | 0.9848 | 0.996 | 1.0384 | 0.954 | 1.052 | 0.954 | 0.99 | 1.0324 | 0.9505 | 1.046 | 0.9505 | 0.995 | 1.0378 | 0.9535 | 1.0515 | 0.9535 | 1.02 | 1.058 | 0.98203 | 1.041 | 0.999 | 1.02 | 1.058 | 0.98203 | 1.041 | 0.999 | 1.0198 | 1.043 | 0.9965 | 1.0517 | 0.9895 | 1.0198 | 1.043 | 0.9965 | 1.0517 | 0.9895 | 1.0123 | 1.036 | 0.9896 | 1.0435 | 0.9835 | 1.0135 | 1.0382 | 0.9915 | 1.0544 | 0.9848 | 0.996 | 1.0384 | 0.954 | 1.052 | 0.954 | 0.99 | 1.0324 | 0.9505 | 1.046 | 0.9505 | 0.995 | 1.0378 | 0.9535 | 1.0515 | 0.9535 | 1.02 | 1.058 | 0.98203 | 1.041 | 0.999 | 1.02 | 1.058 | 0.98203 | 1.041 | 0.999 | 1.0198 | 1.043 | 0.9965 | 1.0517 | 0.9895 | 1.0198 | 1.043 | 0.9965 | 1.0517 | 0.9895 | 1.0123 | 1.036 | 0.9896 | 1.0435 | 0.9835 | 1.0135 | 1.0382 | 0.9915 | 1.0544 | 0.9848 | 0.996 | 1.0384 | 0.954 | 1.052 | 0.954 | 0.99 | 1.0324 | 0.9505 | 1.046 | 0.9505 | 0.995 | 1.0378 | 0.9535 | 1.0515 | 0.9535 | 1.02 | 1.058 | 0.98203 | 1.041 | 0.999 | 1.02 | 1.058 | 0.98203 | 1.041 | 0.999 | 1.0198 | 1.043 | 0.9965 | 1.0517 | 0.9895 | 1.0198 | 1.043 | 0.9965 | 1.0517 | 0.9895 | 1.0123 | 1.036 | 0.9896 | 1.0435 | 0.9835 | 1.0135 | 1.0382 | 0.9915 | 1.0544 | 0.9848 | 0.996 | 1.0384 | 0.954 | 1.052 | 0.954 | 0.99 | 1.0324 | 0.9505 | 1.046 | 0.9505 | 0.995 | 1.0378 | 0.9535 | 1.0515 | 0.9535 | 1.02 | 1.058 | 0.98203 | 1.041 | 0.999 | 1.02 | 1.058 | 0.98203 | 1.041 | 0.999 | 1.0198 | 1.043 | 0.9965 | 1.0517 | 0.9895 | 1.0198 | 1.043 | 0.9965 | 1.0517 | 0.9895 | 1.0123 | 1.036 | 0.9896 | 1.0435 | 0.9835 | 1.0135 | 1.0382 | 0.9915 | 1.0544 | 0.9848 | 0.996 | 1.0384 | 0.954 | 1.052 | 0.954 | 0.99 | 1.0324 | 0.9505 | 1.046 | 0.9505 | 0.995 | 1.0378 | 0.9535 | 1.0515 | 0.9535 | 1.02 | 1.058 | 0.98203 | 1.041 | 0.999 | 1.02 | 1.058 | 0.98203 | 1.041 | 0.999 | 1.0198 | 1.043 | 0.9965 | 1.0517 | 0.9895 | 1.0198 | 1.043 | 0.9965 | 1.0517 | 0.9895 | 1.0123 | 1.036 | 0.9896 | 1.0435 | 0.9835 | 1.0135 | 1.0382 | 0.9915 | 1.0544 | 0.9848 | 0.996 | 1.0384 | 0.954 | 1.052 | 0.954 | 0.99 | 1.0324 | 0.9505 | 1.046 | 0.9505 | 0.995 | 1.0378 | 0.9535 | 1.0515 | 0.9535 | 1.02 | 1.058 | 0.98203 | 1.041 | 0.999 | 1.02 | 1.058 | 0.98203 | 1.041 | 0.999 | 1.0198 | 1.043 | 0.9965 | 1.0517 | 0.9895 | 1.0198 | 1.043 | 0.9965 | 1.0517 | 0.9895 | 1.0123 | 1.036 | 0.9896 | 1.0435 | 0.9835 | 1.0135 | 1.0382 | 0.9915 | 1.0544 | 0.9848 | 0.996 | 1.0384 | 0.954 | 1.052 | 0.954 | 0.99 | 1.0324 | 0.9505 | 1.046 | 0.9505 | 0.995 | 1.0378 | 0.9535 | 1.0515 | 0.9535 | 1.02 | 1.058 | 0.98203 | 1.041 | 0.999 | 1.02 | 1.058 | 0.98203 | 1.041 | 0.999 | 1.0147 | 0.9913 | 1.0147 | 0.9913 | 1.0198 | 0.996 | 1.0198 | 0.996 | 1.0198 | 0.996 | 1.0198 | 0.996 | 1.02 | 0.9913 | 1.02 | 0.996 | 1.02 | 0.996 | 1.02 | 0.996 | 1.02 | 0.996 | 1.02 | 1.02
| Q setpoint | Project1 | Main | 163769877 | QstpDefault | 0.060489 | 0.24931 | -0.05746 | 0.3046 | -0.084592 | 0.093844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29975 | -0.29975 | 0.39467 | -0.39467 | 0 | 0.29975 | -0.29975 | 0.39467 | -0.39467 | 0.060489 | 0.24931 | -0.05746 | 0.3046 | -0.084592 | 0.093844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29975 | -0.29975 | 0.39467 | -0.39467 | 0 | 0.29975 | -0.29975 | 0.39467 | -0.39467 | 0.060489 | 0.24931 | -0.05746 | 0.3046 | -0.084592 | 0.093844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29975 | -0.29975 | 0.39467 | -0.39467 | 0 | 0.29975 | -0.29975 | 0.39467 | -0.39467 | 0.060489 | 0.24931 | -0.05746 | 0.3046 | -0.084592 | 0.093844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29975 | -0.29975 | 0.39467 | -0.39467 | 0 | 0.29975 | -0.29975 | 0.39467 | -0.39467 | 0.060489 | 0.24931 | -0.05746 | 0.3046 | -0.084592 | 0.093844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29975 | -0.29975 | 0.39467 | -0.39467 | 0 | 0.29975 | -0.29975 | 0.39467 | -0.39467 | 0.060489 | 0.24931 | -0.05746 | 0.3046 | -0.084592 | 0.093844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29975 | -0.29975 | 0.39467 | -0.39467 | 0 | 0.29975 | -0.29975 | 0.39467 | -0.39467 | 0.060489 | 0.24931 | -0.05746 | 0.3046 | -0.084592 | 0.093844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29975 | -0.29975 | 0.39467 | -0.39467 | 0 | 0.29975 | -0.29975 | 0.39467 | -0.39467 | 0.060489 | 0.24931 | -0.05746 | 0.3046 | -0.084592 | 0.093844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29975 | -0.29975 | 0.39467 | -0.39467 | 0 | 0.29975 | -0.29975 | 0.39467 | -0.39467 | 0.060489 | 0.24931 | -0.05746 | 0.3046 | -0.084592 | 0.093844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29975 | -0.29975 | 0.39467 | -0.39467 | 0 | 0.29975 | -0.29975 | 0.39467 | -0.39467 | -0.016053 | 0 | -0.016053 | 0 | -0.0025231 | 0 | -0.0025231 | 0 | -0.0025231 | 0 | -0.0025231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PF setpoint | Project1 | Main | 163769877 | PFstpDefault | 0.99818 | 0.97043 | -0.99836 | 0.95661 | -0.99644 | 0.98714 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 0.99818 | 0.9703 | -0.99835 | 0.95661 | -0.99644 | 0.98714 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 0.99818 | 0.9703 | -0.99835 | 0.95661 | -0.99644 | 0.98714 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 0.99818 | 0.97043 | -0.99836 | 0.95661 | -0.99644 | 0.98714 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 0.99818 | 0.9703 | -0.99835 | 0.95661 | -0.99644 | 0.98714 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 0.99818 | 0.9703 | -0.99835 | 0.95661 | -0.99644 | 0.98714 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 0.99818 | 0.9703 | -0.99835 | 0.95661 | -0.99644 | 0.98714 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 0.99818 | 0.9703 | -0.99835 | 0.95661 | -0.99644 | 0.98714 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 0.99818 | 0.9703 | -0.99835 | 0.95661 | -0.99644 | 0.98714 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | -0.99949 | 1 | -0.99949 | 1 | -1 | 1 | -1 | 1 | -1 | 1 | -1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| P setpoint | Project1 | Main | 163769877 | PstpDefault | 1 | 1 | 1 | 1 | 1 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0 | 0.5 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0.5 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1
| P1 setpoint | Project1 | Main | 163769877 | P1stpDefault | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0.5 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0.5 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0
| Irradiance | Project1 | Main | 163769877 | AUXstpDefault | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 311 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
| HV_tap | Project1 | Main | 534238275 | Pos0 | 9 | 11 | 7 | 12 | 6 | 9 | 11 | 7 | 12 | 6 | 8 | 11 | 6 | 11 | 6 | 8 | 10 | 6 | 11 | 6 | 9 | 9 | 8 | 10 | 8 | 8 | 9 | 7 | 9 | 7 | 8 | 9 | 7 | 9 | 7 | 9 | 11 | 7 | 12 | 6 | 8 | 10 | 6 | 11 | 6 | 9 | 11 | 7 | 12 | 6 | 9 | 11 | 7 | 12 | 6 | 8 | 11 | 6 | 11 | 6 | 8 | 10 | 6 | 11 | 6 | 9 | 9 | 8 | 10 | 8 | 8 | 9 | 7 | 9 | 7 | 8 | 9 | 7 | 9 | 7 | 9 | 11 | 7 | 12 | 6 | 8 | 10 | 6 | 11 | 6 | 9 | 11 | 7 | 12 | 6 | 9 | 11 | 7 | 12 | 6 | 8 | 11 | 6 | 11 | 6 | 8 | 10 | 6 | 11 | 6 | 9 | 9 | 8 | 10 | 8 | 8 | 9 | 7 | 9 | 7 | 8 | 9 | 7 | 9 | 7 | 9 | 11 | 7 | 13 | 6 | 8 | 10 | 6 | 11 | 6 | 9 | 11 | 7 | 12 | 6 | 9 | 11 | 7 | 12 | 6 | 8 | 11 | 6 | 11 | 6 | 8 | 10 | 6 | 11 | 6 | 9 | 9 | 8 | 10 | 8 | 8 | 9 | 7 | 9 | 7 | 8 | 9 | 7 | 9 | 7 | 9 | 11 | 7 | 12 | 6 | 8 | 10 | 6 | 11 | 6 | 9 | 11 | 7 | 12 | 6 | 9 | 11 | 7 | 12 | 6 | 8 | 11 | 6 | 11 | 6 | 8 | 10 | 6 | 11 | 6 | 9 | 9 | 8 | 10 | 8 | 8 | 9 | 7 | 9 | 7 | 8 | 9 | 7 | 9 | 7 | 9 | 11 | 7 | 12 | 6 | 8 | 10 | 6 | 11 | 6 | 9 | 11 | 7 | 12 | 6 | 9 | 11 | 7 | 12 | 6 | 8 | 11 | 6 | 11 | 6 | 8 | 10 | 6 | 11 | 6 | 9 | 9 | 8 | 10 | 8 | 8 | 9 | 7 | 9 | 7 | 8 | 9 | 7 | 9 | 7 | 9 | 11 | 7 | 12 | 6 | 8 | 10 | 6 | 11 | 6 | 9 | 11 | 7 | 12 | 6 | 9 | 11 | 7 | 12 | 6 | 8 | 11 | 6 | 11 | 6 | 8 | 10 | 6 | 11 | 6 | 9 | 9 | 8 | 10 | 8 | 8 | 9 | 7 | 9 | 7 | 8 | 9 | 7 | 9 | 7 | 9 | 11 | 7 | 12 | 6 | 8 | 10 | 6 | 11 | 6 | 9 | 11 | 7 | 12 | 6 | 9 | 11 | 7 | 12 | 6 | 8 | 11 | 6 | 11 | 6 | 8 | 10 | 6 | 11 | 6 | 9 | 9 | 8 | 10 | 8 | 8 | 9 | 7 | 9 | 7 | 8 | 9 | 7 | 9 | 7 | 9 | 11 | 7 | 12 | 6 | 8 | 10 | 6 | 11 | 6 | 9 | 11 | 7 | 12 | 6 | 9 | 11 | 7 | 12 | 6 | 8 | 11 | 6 | 11 | 6 | 8 | 10 | 6 | 11 | 6 | 9 | 9 | 8 | 10 | 8 | 8 | 9 | 7 | 9 | 7 | 8 | 9 | 7 | 9 | 7 | 9 | 11 | 7 | 12 | 6 | 8 | 10 | 6 | 11 | 6 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
| Confilg File Number | Project1 | Main | 1105776716 | FileNum | bar: Combined- Pmax1 1 to X/R=3, BESS 429
| Initial PV React Pwr | Project1 | Main | 1105776716 | PvPwrRtInit | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 0 | -15000 | 0 | -15000 | 0 | 0 | -15000 | 0 | -15000 | 0 | 0 | -15000 | 0 | -15000 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 0 | -15000 | 0 | -15000 | 0 | 0 | -15000 | 0 | -15000 | 0 | 0 | -15000 | 0 | -15000 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 0 | -15000 | 0 | -15000 | 0 | 0 | -15000 | 0 | -15000 | 0 | 0 | -15000 | 0 | -15000 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 0 | -15000 | 0 | -15000 | 0 | 0 | -15000 | 0 | -15000 | 0 | 0 | -15000 | 0 | -15000 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 0 | -15000 | 0 | -15000 | 0 | 0 | -15000 | 0 | -15000 | 0 | 0 | -15000 | 0 | -15000 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 0 | -15000 | 0 | -15000 | 0 | 0 | -15000 | 0 | -15000 | 0 | 0 | -15000 | 0 | -15000 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 0 | -15000 | 0 | -15000 | 0 | 0 | -15000 | 0 | -15000 | 0 | 0 | -15000 | 0 | -15000 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 0 | -15000 | 0 | -15000 | 0 | 0 | -15000 | 0 | -15000 | 0 | 0 | -15000 | 0 | -15000 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 0 | -15000 | 0 | -15000 | 0 | 0 | -15000 | 0 | -15000 | 0 | 0 | -15000 | 0 | -15000 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 35640 | -35640 | 46926 | -46926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Initial PV Pwr | Project1 | Main | 1105776716 | PvPwrAtInit | 119180 | 119180 | 119180 | 118900 | 118900 | 68904 | 68904 | 68904 | 68904 | 68904 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118800 | 118800 | 118800 | 118800 | 118800 | 5940 | 5940 | 5940 | 5940 | 5940 | 118900 | 118900 | 118900 | 118900 | 118900 | 68904 | 68904 | 68904 | 68904 | 68904 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118800 | 118800 | 118800 | 118800 | 118800 | 5940 | 5940 | 5940 | 5940 | 5940 | 118900 | 118900 | 118900 | 118900 | 118900 | 68904 | 68904 | 68904 | 68904 | 68904 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118800 | 118800 | 118800 | 118800 | 118800 | 5940 | 5940 | 5940 | 5940 | 5940 | 119180 | 119180 | 119180 | 118900 | 118900 | 68904 | 68904 | 68904 | 68904 | 68904 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118800 | 118800 | 118800 | 118800 | 118800 | 5940 | 5940 | 5940 | 5940 | 5940 | 118900 | 118900 | 118900 | 118900 | 118900 | 68904 | 68904 | 68904 | 68904 | 68904 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118800 | 118800 | 118800 | 118800 | 118800 | 5940 | 5940 | 5940 | 5940 | 5940 | 118900 | 118900 | 118900 | 118900 | 118900 | 68904 | 68904 | 68904 | 68904 | 68904 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118800 | 118800 | 118800 | 118800 | 118800 | 5940 | 5940 | 5940 | 5940 | 5940 | 118900 | 118900 | 118900 | 118900 | 118900 | 68904 | 68904 | 68904 | 68904 | 68904 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118800 | 118800 | 118800 | 118800 | 118800 | 5940 | 5940 | 5940 | 5940 | 5940 | 118900 | 118900 | 118900 | 118900 | 118900 | 68904 | 68904 | 68904 | 68904 | 68904 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118800 | 118800 | 118800 | 118800 | 118800 | 5940 | 5940 | 5940 | 5940 | 5940 | 118900 | 118900 | 118900 | 118900 | 118900 | 68904 | 68904 | 68904 | 68904 | 68904 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118800 | 118800 | 118800 | 118800 | 118800 | 5940 | 5940 | 5940 | 5940 | 5940 | 59950 | 0 | 59950 | 0 | 118900 | 0 | 118900 | 0 | 118900 | 0 | 118900 | 0 | 59400 | 0 | 118800 | 0 | 118800 | 0 | 118800 | 0 | 118800 | 0 | 118800 | 118800
| Q ctrl mode | Project1 | Main | 1105776716 | FileNum | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Note on AY3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not required and also not working without shifting limits of solar plant.
Note on CR3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not required and also not working without shifting limits of solar plant.
Note on EK3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not required and also not working without shifting limits of solar plant.
Note on GD3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not required and also not working without shifting limits of solar plant.
Note on HW3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not required and also not working without shifting limits of solar plant.
Note on JP3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not required and also not working without shifting limits of solar plant.
Note on LI3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not required and also not working without shifting limits of solar plant.
Note on NB3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not required and also not working without shifting limits of solar plant.
Note on OU3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not required and also not working without shifting limits of solar plant.
Note on F13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: to be specified in MW Reply: P at POC
Note on H14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: need to figure out what the flows at
Note on BA14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: need to figure out what the flows at
Note on CT14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: need to figure out what the flows at
Note on EM14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: need to figure out what the flows at
Note on GF14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: need to figure out what the flows at
Note on HY14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: need to figure out what the flows at
Note on JR14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: need to figure out what the flows at
Note on LK14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: need to figure out what the flows at
Note on ND14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: need to figure out what the flows at
Note on F15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: P (MW) at generator1 branch
Note on F21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: transformer tap settinngs are not required to be provided, but can be provided explicitly in the given format to enforce a specific tap setting.
Note on F24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A separate DYR file will be used in testing Qcontrol mode.

## SteadyStateStudies
This sheet lists the contingency scenarios to be considered in Steady State studies. + CaseNr: name of the contingency scenarios; If left blank, the event occuring on that row is considered to be in the same scenario above it. + TestType: Contingency (trip, disconnect) or setpoint changes (Generation output changes, voltage change, tap changes) *note: + TestType is contingency, inputs are ini_status and end_status + TestType is setpoint changes, inputs are ini_value and end_value + Element: the element to which contingency is apply; if TestType setpoint change type, then element depends on type of change (e.g. Genchange -> machine; Tap change -> Tx) + i_bus, j_bus, k_bus, id: Connected buses and identification number of the element. If contingency element is a machine or a Shunt, the j_bus and k_bus are not needed. Similarly, k_bus is only used for three winding transformer contingency. + status: either 1 or 0: the element is activated or not - applicable to contingency + value: the specific values implemented - only applicable for setpoint change
CaseNr | TestType | Element | i_bus | j_bus | k_bus | id | ini_status | end_status | ini_value | end_value | run in PSS/E? | CaseDescription | Case_Code | test group | simulation batch
1 | Trip | Line | 306581 | 384080 |  | 1 | 1 | 0 |  |  | yes | ARTS-WBTS-BATS (ARARAT to WAUBRA to BALLARAT) 220kV line OOS | 3ARAR_T_220B - 3WAUBRA_220A_id1 | trip a line | S52512
| Trip | Line | 309080 | 384080 |  | 1 | 1 | 0 |  |  | yes | ARTS-WBTS-BATS (ARARAT to WAUBRA to BALLARAT) 220kV line OOS | 3BALRAT_220A - 3WAUBRA_220A_id1 | trip a line | S52512
| Trip | Bus | 384080 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 384001 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 384030 |  |  | 1 | 1 | 0 |  |  | yes
2 | Trip | Line | 306585 | 321580 |  | 1 | 1 | 0 |  |  | yes | ARTS-CWTS (ARARAT to CROWNLANDS) 220kV line OOS | 3ARAR_T_220F - 3CROWLA_220A_id1 | trip a line | S52512
3 | Trip | Line | 316580 | 321580 |  | 1 | 1 | 0 |  |  | yes | CWTS-BGTS-HOTS (CROWNLANDS to BULGANA to HORSHAM) 220kV line OOS | 3BULGTS_220A - 3CROWLA_220A_id1 | trip a line | S52512
| Trip | Line | 316580 | 334081 |  | 1 | 1 | 0 |  |  | yes | CWTS-BGTS-HOTS (CROWNLANDS to BULGANA to HORSHAM) 220kV line OOS | 3BULGTS_220A - HOTS 220 KV_POC_id1 | trip a line | S52512
| Trip | Bus | 32393 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 32500 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 316580 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 316702 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 316737 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 32467 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 316530 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 316581 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 316731 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 316738 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 32499 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 316531 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 316701 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 316736 |  |  | 1 | 1 | 0 |  |  | yes
4 | Trip | Line | 334081 | 355880 |  | 1 | 1 | 0 |  |  | yes | HOTS-MRTS-KMTS (HORSHAM to MURRAWARRA to KIAMAL) 220kV line OOS | HOTS 220 KV_POC - 3MURRAW_220A_id1 | trip a line | S52512
| Trip | Line | 342280 | 355880 |  | 1 | 1 | 0 |  |  | yes | HOTS-MRTS-KMTS (HORSHAM to MURRAWARRA to KIAMAL) 220kV line OOS | 3KIAMAL_220A - 3MURRAW_220A_id1 | trip a line | S52512
| Trip | Bus | 69 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 339 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 5102 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 5201 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 5204 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 32000 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 337 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 2204 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 5103 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 5202 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 5301 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 355880 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 338 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 5101 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 5104 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 5203 |  |  | 1 | 1 | 0 |  |  | yes
| Trip | Bus | 5401 |  |  | 1 | 1 | 0 |  |  | yes
5 | Trip | Line | 342280 | 364080 |  | 1 | 1 | 0 |  |  | yes | KMTS-RCTS (KIAMAL to REDCLIFF) 220kV line OOS | 3KIAMAL_220A - 3REDCLF_220A_id1 | trip a line | S52512
6 | Trip | Tx_2w | 334030 | 334081 |  | 1 | 1 | 0 |  |  | yes | KMTS-RCTS (KIAMAL to REDCLIFF) 220kV line OOS | 3HORSHM__66A - HOTS 220 KV_POC_id1 | trip a Tx | S52512
7 | ChgMW | Machine | 334094 |  |  | 1 | 1 | 1 | 60 | 45 | yes | ChgMW Machine HOR_LV_PV_id1 | GenChange (100% to 75%) | change generation output | S52512
| ChgMW | Machine | 334095 |  |  | 1 | 1 | 1 | 60 | 45 | yes | ChgMW Machine HOR_LV_BESS_id1 | GenChange (100% to 75%) | change generation output | S52512
8 | ChgMW | Machine | 334094 |  |  | 1 | 1 | 1 | 60 | 30 | yes | ChgMW Machine HOR_LV_PV_id1 | GenChange (100% to 50%) | change generation output | S52512
| ChgMW | Machine | 334095 |  |  | 1 | 1 | 1 | 60 | 30 | yes | ChgMW Machine HOR_LV_BESS_id1 | GenChange (100% to 50%) | change generation output | S52512
9 | ChgMW | Machine | 334094 |  |  | 1 | 1 | 1 | 60 | 15 | yes | ChgMW Machine HOR_LV_PV_id1 | GenChange (100% to 25%) | change generation output | S52512
| ChgMW | Machine | 334095 |  |  | 1 | 1 | 1 | 60 | 15 | yes | ChgMW Machine HOR_LV_BESS_id1 | GenChange (100% to 25%) | change generation output | S52512
10 | ChgMW | Machine | 334094 |  |  | 1 | 1 | 1 | 0.3 | 0.3 | yes | ChgMW Machine HOR_LV_PV_id1 | GenChange (-100% to -75%) | change generation output | S52512
| ChgMW | Machine | 334095 |  |  | 1 | 1 | 1 | -99.4 | -74.55 | yes | ChgMW Machine HOR_LV_BESS_id1 | GenChange (-100% to -75%) | change generation output | S52512
11 | ChgMW | Machine | 334094 |  |  | 1 | 1 | 1 | 0.3 | 0.3 | yes | ChgMW Machine HOR_LV_PV_id1 | GenChange (-100% to -50%) | change generation output | S52512
| ChgMW | Machine | 334095 |  |  | 1 | 1 | 1 | -99.4 | -49.7 | yes | ChgMW Machine HOR_LV_BESS_id1 | GenChange (-100% to -50%) | change generation output | S52512
12 | ChgMW | Machine | 334094 |  |  | 1 | 1 | 1 | 0.3 | 0.3 | yes | ChgMW Machine HOR_LV_PV_id1 | GenChange (-100% to -25%) | change generation output | S52512
| ChgMW | Machine | 334095 |  |  | 1 | 1 | 1 | -99.4 | -24.85 | yes | ChgMW Machine HOR_LV_BESS_id1 | GenChange (-100% to -25%) | change generation output | S52512
13 | Trip | Machine | 334094 |  |  | 1 | 1 | 0 | 60 | 0 | yes | Trip Machine HOR_LV_PV_id1 | GenTrip (100% to 0%) | Trip a generator | S52512
| Trip | Machine | 334095 |  |  | 1 | 1 | 0 | 60 | 0 | yes | Trip Machine HOR_LV_BESS_id1 | GenTrip (100% to 0%) | Trip a generator | S52512
|  | Shunt | 334091 |  |  | 1 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id1 |  | runback | S52512
|  | Shunt | 334091 |  |  | 2 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id2 |  | runback | S52512
|  | Shunt | 334091 |  |  | 3 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id3 |  | runback | S52512
|  | Shunt | 334091 |  |  | 4 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id4 |  | runback | S52512
14 | Trip | Machine | 334094 |  |  | 1 | 1 | 0 | 45 | 0 | yes | Trip Machine HOR_LV_PV_id1 | GenTrip (75% to 0%) | Trip a generator | S52512
| Trip | Machine | 334095 |  |  | 1 | 1 | 0 | 45 | 0 | yes | Trip Machine HOR_LV_BESS_id1 | GenTrip (75% to 0%) | Trip a generator | S52512
|  | Shunt | 334091 |  |  | 1 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id1 |  | runback | S52512
|  | Shunt | 334091 |  |  | 2 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id2 |  | runback | S52512
|  | Shunt | 334091 |  |  | 3 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id3 |  | runback | S52512
|  | Shunt | 334091 |  |  | 4 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id4 |  | runback | S52512
15 | Trip | Machine | 334094 |  |  | 1 | 1 | 0 | 30 | 0 | yes | Trip Machine HOR_LV_PV_id1 | GenTrip (50% to 0%) | Trip a generator | S52512
|  | Machine | 334095 |  |  | 1 | 1 | 0 | 30 | 0 | yes | Machine HOR_LV_BESS_id1 | GenTrip (50% to 0%) | Trip a generator | S52512
|  | Shunt | 334091 |  |  | 1 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id1 |  | runback | S52512
|  | Shunt | 334091 |  |  | 2 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id2 |  | runback | S52512
|  | Shunt | 334091 |  |  | 3 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id3 |  | runback | S52512
|  | Shunt | 334091 |  |  | 4 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id4 |  | runback | S52512
16 | Trip | Machine | 334094 |  |  | 1 | 1 | 0 | 15 | 0 | yes | Trip Machine HOR_LV_PV_id1 | GenTrip (25% to 0%) | Trip a generator | S52512
|  | Machine | 334095 |  |  | 1 | 1 | 0 | 15 | 0 | yes | Machine HOR_LV_BESS_id1 | GenTrip (25% to 0%) | Trip a generator | S52512
|  | Shunt | 334091 |  |  | 1 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id1 |  | runback | S52512
|  | Shunt | 334091 |  |  | 2 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id2 |  | runback | S52512
|  | Shunt | 334091 |  |  | 3 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id3 |  | runback | S52512
|  | Shunt | 334091 |  |  | 4 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id4 |  | runback | S52512
17 | Trip | Machine | 334094 |  |  | 1 | 1 | 0 | 0.3 | 0 | yes | Trip Machine HOR_LV_PV_id1 | GenTrip (-100% to 0%) | Trip a generator | S52512
|  | Machine | 334095 |  |  | 1 | 1 | 0 | -99.4 | 0 | yes | Machine HOR_LV_BESS_id1 | GenTrip (-100% to 0%) | Trip a generator | S52512
|  | Shunt | 334091 |  |  | 1 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id1 |  | runback | S52512
|  | Shunt | 334091 |  |  | 2 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id2 |  | runback | S52512
|  | Shunt | 334091 |  |  | 3 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id3 |  | runback | S52512
|  | Shunt | 334091 |  |  | 4 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id4 |  | runback | S52512
18 | Trip | Machine | 334094 |  |  | 1 | 1 | 0 | 0.3 | 0 | yes | Trip Machine HOR_LV_PV_id1 | GenTrip (-50% to 0%) | Trip a generator | S52512
|  | Machine | 334095 |  |  | 1 | 1 | 0 | -49.7 | 0 | yes | Machine HOR_LV_BESS_id1 | GenTrip (-50% to 0%) | Trip a generator | S52512
|  | Shunt | 334091 |  |  | 1 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id1 |  | runback | S52512
|  | Shunt | 334091 |  |  | 2 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id2 |  | runback | S52512
|  | Shunt | 334091 |  |  | 3 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id3 |  | runback | S52512
|  | Shunt | 334091 |  |  | 4 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id4 |  | runback | S52512
19 | Trip | Machine | 334094 |  |  | 1 | 1 | 0 | 0.3 | 0 | yes | Trip Machine HOR_LV_PV_id1 | GenTrip (-25% to 0%) | Trip a generator | S52512
|  | Machine | 334095 |  |  | 1 | 1 | 0 | -24.85 | 0 | yes | Machine HOR_LV_BESS_id1 | GenTrip (-25% to 0%) | Trip a generator | S52512
|  | Shunt | 334091 |  |  | 1 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id1 |  | runback | S52512
|  | Shunt | 334091 |  |  | 2 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id2 |  | runback | S52512
|  | Shunt | 334091 |  |  | 3 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id3 |  | runback | S52512
|  | Shunt | 334091 |  |  | 4 | 1 | 0 |  | 0 | yes | Shunt HOR_MV_id4 |  | runback | S52512
20 | FaultCal | Bus | 334081 | [7 empty] | yes | FaultCal Bus HOR_POC_id | HSFBESS_high_genon.sav | Fault Level calculations | S528
|  | Bus | 334090 | [7 empty] | yes | Bus HOR_HV_id |  | Fault Level calculations | S528
|  | Bus | 334091 | [7 empty] | yes | Bus HOR_MV_id |  | Fault Level calculations | S528
|  | Bus | 334092 | [7 empty] | yes | Bus HOR_MV_PV_id |  | Fault Level calculations | S528
|  | Bus | 334093 | [7 empty] | yes | Bus HOR_MV_BESS_id |  | Fault Level calculations | S528
|  | Bus | 334094 | [7 empty] | yes | Bus HOR_LV_PV_id |  | Fault Level calculations | S528
|  | Bus | 334095 | [7 empty] | yes | Bus HOR_LV_BESS_id |  | Fault Level calculations | S528
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Consecutive cases. leave empty if it belong to / associated with previous contingency case
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: if Element is a Machine, shunt or Bus, then J_bus = empty
Note on J2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: dedicated for generation output before contingency occurs
Note on K2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: dedicated for generation output after contingency occurs

## PowerQuality
This sheet lists the operational scenarios to be considered in Power Quality studies. + CaseNr: name of the operational scenarios; + Variation Name: This is the name for a variation from the base model quantities (e.g. +/- 10% BoP) + Inverter Characteristic: This is a change from the base model (e.g. BESS Charging, BESS Discharging, Q at Night, etc.)
Run? | CaseNr | Scenario Name | Variation Name | Inverter Characteristic | Fault Level | PV MW | PV Mvar |  |  |  | Filters in service?
0 | 01a | 01a_Pmax Qmax_100%P PV_100%Q BESS |  | BESS Discharging | Maximum | 90 | 35.55 |  | PQ01a | Pmax Qmax_100%P PV_100%Q BESS | No
0 | 02a | 02a_Pmax Qmin_100%P PV_100%Q BESS |  | BESS Discharging | Maximum | 90 | -35.55 |  | PQ02a | Pmax Qmin_100%P PV_100%Q BESS | No
0 | 03a | 03a_Pmax Qmax_50%P PV_50%Q BESS |  | BESS Discharging | Maximum | 90 | 35.55 |  | PQ03a | Pmax Qmax_50%P PV_50%Q BESS | No
0 | 04a | 04a_Pmax Qmin_50%P PV_50%Q BESS |  | BESS Discharging | Maximum | 90 | -35.55 |  | PQ04a | Pmax Qmin_50%P PV_50%Q BESS | No
0 | 05a | 05a_Pmin Qmax_100%P BESS_100%Q PV |  | BESS Charging | Maximum | -50 | 35.55 |  | PQ05a | Pmin Qmax_100%P BESS_100%Q PV | No
0 | 06a | 06a_Pmin Qmin_100%P BESS_100%Q PV |  | BESS Charging | Maximum | -50 | -35.55 |  | PQ06a | Pmin Qmin_100%P BESS_100%Q PV | No
0 | 07a | 07a_01a+BESS Coll Fdr1 Outage |  | BESS Discharging | Maximum | 90 | 35.55 |  | PQ07a | PQ01a+BESS Coll Fdr1 Outage | No
0 | 08a | 08a_02a+BESS Coll Fdr1 Outage |  | BESS Discharging | Maximum | 90 | -35.55 |  | PQ08a | PQ02a+BESS Coll Fdr1 Outage | No
0 | 09a | 09a_03a+BESS Coll Fdr1 Outage |  | BESS Discharging | Maximum | 90 | 35.55 |  | PQ09a | PQ03a+BESS Coll Fdr1 Outage | No
0 | 10a | 10a_04a+BESS Coll Fdr1 Outage |  | BESS Discharging | Maximum | 90 | -35.55 |  | PQ10a | PQ04a+BESS Coll Fdr1 Outage | No
0 | 11a | 11a_05a+BESS Coll Fdr1 Outage |  | BESS Charging | Maximum | -50 | 35.55 |  | PQ11a | PQ05a+BESS Coll Fdr1 Outage | No
0 | 12a | 12a_06a+BESS Coll Fdr1 Outage |  | BESS Charging | Maximum | -50 | -35.55 |  | PQ12a | PQ06a+BESS Coll Fdr1 Outage | No
0 | 13a | 13a_01a+PV Coll Fdr2 Outage |  | BESS Discharging | Maximum | 90 | 35.55 |  | PQ13a | PQ01a+PV Coll Fdr2 Outage | No
0 | 14a | 14a_02a+PV Coll Fdr2 Outage |  | BESS Discharging | Maximum | 90 | -35.55 |  | PQ14a | PQ02a+PV Coll Fdr2 Outage | No
0 | 15a | 15a_03a+PV Coll Fdr2 Outage |  | BESS Discharging | Maximum | 90 | 35.55 |  | PQ15a | PQ03a+PV Coll Fdr2 Outage | No
0 | 16a | 16a_04a+PV Coll Fdr2 Outage |  | BESS Discharging | Maximum | 90 | -35.55 |  | PQ16a | PQ04a+PV Coll Fdr2 Outage | No
0 | 17a | 17a_05a+PV Coll Fdr2 Outage |  | BESS Charging | Maximum | -50 | 35.55 |  | PQ17a | PQ05a+PV Coll Fdr2 Outage | No
0 | 18a | 18a_06a+PV Coll Fdr2 Outage |  | BESS Charging | Maximum | -50 | -35.55 |  | PQ18a | PQ06a+PV Coll Fdr2 Outage | No
0 | 19a | 19a_01a_+10%TX_Z | +10%BoP | BESS Discharging | Maximum | 90 | 35.55 |  | PQ19a | PQ01a_+10%TX_Z | No
0 | 20a | 20a_02a_+10%TX_Z | +10%BoP | BESS Discharging | Maximum | 90 | -35.55 |  | PQ20a | PQ02a_+10%TX_Z | No
0 | 21a | 21a_03a_+10%TX_Z | +10%BoP | BESS Discharging | Maximum | 90 | 35.55 |  | PQ21a | PQ03a_+10%TX_Z | No
0 | 22a | 22a_04a_+10%TX_Z | +10%BoP | BESS Discharging | Maximum | 90 | -35.55 |  | PQ22a | PQ04a_+10%TX_Z | No
0 | 23a | 23a_05a_+10%TX_Z | +10%BoP | BESS Charging | Maximum | -50 | 35.55 |  | PQ23a | PQ05a_+10%TX_Z | No
0 | 24a | 24a_06a_+10%TX_Z | +10%BoP | BESS Charging | Maximum | -50 | -35.55 |  | PQ24a | PQ06a_+10%TX_Z | No
0 | 25a | 25a_01a_-10%TX_Z | -10%BoP | BESS Discharging | Maximum | 90 | 35.55 |  | PQ25a | PQ01a_-10%TX_Z | No
0 | 26a | 26a_02a_-10%TX_Z | -10%BoP | BESS Discharging | Maximum | 90 | -35.55 |  | PQ26a | PQ02a_-10%TX_Z | No
0 | 27a | 27a_03a_-10%TX_Z | -10%BoP | BESS Discharging | Maximum | 90 | 35.55 |  | PQ27a | PQ03a_-10%TX_Z | No
0 | 28a | 28a_04a_-10%TX_Z | -10%BoP | BESS Discharging | Maximum | 90 | -35.55 |  | PQ28a | PQ04a_-10%TX_Z | No
0 | 29a | 29a_05a_-10%TX_Z | -10%BoP | BESS Charging | Maximum | -50 | 35.55 |  | PQ29a | PQ05a_-10%TX_Z | No
0 | 30a | 30a_06a_-10%TX_Z | -10%BoP | BESS Charging | Maximum | -50 | -35.55 |  | PQ30a | PQ06a_-10%TX_Z | No
0 | 31a | 31a_Pmax_Qmax_PV Only |  | BESS Discharging | Maximum | 90 | 35.55 |  | PQ31a | PQPmax_Qmax_PV Only | No
0 | 32a | 32a_Pmax_Qmin_PV Only |  | BESS Discharging | Maximum | 90 | -35.55 |  | PQ32a | PQPmax_Qmin_PV Only | No
0 | 33a | 33a_Pmax_Qmax_BESS Only |  | BESS Discharging | Maximum | 90 | 35.55 |  | PQ33a | PQPmax_Qmax_BESS Only | No
0 | 34a | 34a_Pmax_Qmin_BESS Only |  | BESS Discharging | Maximum | 90 | -35.55 |  | PQ34a | PQPmax_Qmin_BESS Only | No
0 | 35a | 35a_Pmin_Qmax_BESS Only |  | BESS Charging | Maximum | -50 | 35.55 |  | PQ35a | PQPmin_Qmax_BESS Only | No
0 | 36a | 36a_Pmin_Qmin_BESS Only |  | BESS Charging | Maximum | -50 | -35.55 |  | PQ36a | PQPmin_Qmin_BESS Only | No
0 | 37a | 37a_Qmax_Night |  | Q at Night | Maximum | 90 | 35.55 |  | PQ37a | PQQmax_Night | No
0 | 38a | 38a_Qmin_Night |  | Q at Night | Maximum | 90 | -35.55 |  | PQ38a | PQQmin_Night | No
1 | 01b | 01b_01a with HF |  | BESS Discharging |  |  |  | 1 |  | 01b_01b with HF
1 | 02b | 02b_02a with HF |  | BESS Discharging | [5 empty] | 02b_02b with HF
1 | 03b | 03b_03a with HF |  | BESS Discharging | [5 empty] | 03b_03b with HF
1 | 04b | 04b_04a with HF |  | BESS Discharging | [5 empty] | 04b_04b with HF
1 | 05b | 05b_05a with HF |  | BESS Charging | [5 empty] | 05b_05b with HF
1 | 06b | 06b_06a with HF |  | BESS Charging | [5 empty] | 06b_06b with HF
1 | 07b | 07b_07a with HF |  | BESS Discharging |  |  |  | 1 |  | 07b_07b with HF
1 | 08b | 08b_08a with HF |  | BESS Discharging | [5 empty] | 08b_08b with HF
1 | 09b | 09b_09a with HF |  | BESS Discharging | [5 empty] | 09b_09b with HF
1 | 10b | 10b_10a with HF |  | BESS Discharging | [5 empty] | 10b_10b with HF
1 | 11b | 11b_11a with HF |  | BESS Charging | [5 empty] | 11b_11b with HF
1 | 12b | 12b_12a with HF |  | BESS Charging | [5 empty] | 12b_12b with HF
1 | 13b | 13b_13a with HF |  | BESS Discharging |  |  |  | 1 |  | 13b_13b with HF
1 | 14b | 14b_14a with HF |  | BESS Discharging | [5 empty] | 14b_14b with HF
1 | 15b | 15b_15a with HF |  | BESS Discharging | [5 empty] | 15b_15b with HF
1 | 16b | 16b_16a with HF |  | BESS Discharging | [5 empty] | 16b_16b with HF
1 | 17b | 17b_17a with HF |  | BESS Charging | [5 empty] | 17b_17b with HF
1 | 18b | 18b_18a with HF |  | BESS Charging | [5 empty] | 18b_18b with HF
1 | 19b | 19b_19a with HF | +10%BoP | BESS Discharging |  |  |  | 1 |  | 19b_19b with HF
1 | 20b | 20b_20a with HF | +10%BoP | BESS Discharging | [5 empty] | 20b_20b with HF
1 | 21b | 21b_21a with HF | +10%BoP | BESS Discharging | [5 empty] | 21b_21b with HF
1 | 22b | 22b_22a with HF | +10%BoP | BESS Discharging | [5 empty] | 22b_22b with HF
1 | 23b | 23b_23a with HF | +10%BoP | BESS Charging |  |  |  | 1 |  | 23b_23b with HF
1 | 24b | 24b_24a with HF | +10%BoP | BESS Charging | [5 empty] | 24b_24b with HF
1 | 25b | 25b_25a with HF | -10%BoP | BESS Discharging |  |  |  | 1 |  | 25b_25b with HF
1 | 26b | 26b_26a with HF | -10%BoP | BESS Discharging | [5 empty] | 26b_26b with HF
1 | 27b | 27b_27a with HF | -10%BoP | BESS Discharging | [5 empty] | 27b_27b with HF
1 | 28b | 28b_28a with HF | -10%BoP | BESS Discharging | [5 empty] | 28b_28b with HF
1 | 29b | 29b_29a with HF | -10%BoP | BESS Charging |  |  |  | 1 |  | 29b_29b with HF
1 | 30b | 30b_30a with HF | -10%BoP | BESS Charging | [5 empty] | 30b_30b with HF
1 | 31b | 31b_31a with HF |  | BESS Discharging |  |  |  | 1 |  | 31b_31b with HF
1 | 32b | 32b_32a with HF |  | BESS Discharging | [5 empty] | 32b_32b with HF
1 | 33b | 33b_33a with HF |  | BESS Discharging |  |  |  | 1 |  | 33b_33b with HF
1 | 34b | 34b_34a with HF |  | BESS Discharging | [5 empty] | 34b_34b with HF
1 | 35b | 35b_35a with HF |  | BESS Charging | [5 empty] | 35b_35b with HF
1 | 36b | 36b_36a with HF |  | BESS Charging | [5 empty] | 36b_36b with HF
1 | 37b | 37b_37a with HF |  | Q at Night | [5 empty] | 37b_37b with HF
1 | 38b | 38b_38a with HF |  | Q at Night | [5 empty] | 38b_38b with HF
1 | 01b | 01b_01a with HF |  | BESS Discharging
1 | 07b | 07b_07a with HF |  | BESS Discharging
1 | 13b | 13b_13a with HF |  | BESS Discharging
1 | 19b | 19b_19a with HF | +10%BoP | BESS Discharging
1 | 23b | 23b_23a with HF | +10%BoP | BESS Charging
1 | 25b | 25b_25a with HF | -10%BoP | BESS Discharging
1 | 29b | 29b_29a with HF | -10%BoP | BESS Charging
1 | 31b | 31b_31a with HF |  | BESS Discharging
1 | 33b | 33b_33a with HF |  | BESS Discharging
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Put exact name as how it is written in operational scenarios in PF
Note on D2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Leave blank if no variation to be used
Note on E2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Leave blank if base model version to be used

## PQ Limits
Notes: All limits are in percent
Harmonic_Order | Planning_Limits | Allocation_Limits_AAS | Allocation_Limits_MAS | Background_Harmonic_Distortion | Alpha_Factors
THD | 0 | 0 | 0
2 | 1.4 | 0.1 | 0 | 0.50052 | 1
3 | 2 | 0.1 | 0 | 0.24332 | 1
4 | 0.8 | 0.1 | 0 | 0.19767 | 1
5 | 2 | 0.17 | 0 | 0.70954 | 1
6 | 0.4 | 0.1 | 0 | 0.104 | 1
7 | 2 | 0.17 | 0 | 0.34069 | 1
8 | 0.4 | 0.1 | 0 | 0.12242 | 1
9 | 1 | 0.1 | 0 | 0.12408 | 1
10 | 0.35 | 0.1 | 0 | 0.090883 | 1
11 | 1.5 | 0.27 | 0 | 0.17768 | 1
12 | 0.31833 | 0.1 | 0 | 0.072736 | 1
13 | 1.5 | 0.27 | 0 | 0.18952 | 1
14 | 0.29571 | 0.1 | 0 | 0.072023 | 1
15 | 0.3 | 0.1 | 0 | 0.15 | 1
16 | 0.27875 | 0.1 | 0 | 0.13937 | 1
17 | 1.2 | 0.18 | 0 | 0.6 | 1
18 | 0.26556 | 0.1 | 0 | 0.13278 | 1
19 | 1.0737 | 0.18 | 0 | 0.53684 | 1
20 | 0.255 | 0.1 | 0 | 0.1275 | 1
21 | 0.2 | 0.1 | 0 | 0.1 | 1
22 | 0.24636 | 0.1 | 0 | 0.12318 | 1
23 | 0.88696 | 0.13 | 0 | 0.44348 | 1
24 | 0.23917 | 0.1 | 0 | 0.11958 | 1
25 | 0.816 | 0.13 | 0 | 0.408 | 1
26 | 0.23308 | 0.1 | 0 | 0.11654 | 1
27 | 0.2 | 0.1 | 0 | 0.1 | 1
28 | 0.22786 | 0.1 | 0 | 0.11393 | 1
29 | 0.70345 | 0.11 | 0 | 0.35172 | 1
30 | 0.22333 | 0.1 | 0 | 0.11167 | 1
31 | 0.65806 | 0.11 | 0 | 0.32903 | 1
32 | 0.21937 | 0.1 | 0 | 0.10969 | 1
33 | 0.2 | 0.1 | 0 | 0.1 | 1
34 | 0.21588 | 0.1 | 0 | 0.10794 | 1
35 | 0.58286 | 0.1 | 0 | 0.29143 | 1
36 | 0.21278 | 0.1 | 0 | 0.10639 | 1
37 | 0.55135 | 0.1 | 0 | 0.27568 | 1
38 | 0.21 | 0.1 | 0 | 0.105 | 1
39 | 0.2 | 0.1 | 0 | 0.1 | 1
40 | 0.2075 | 0.1 | 0 | 0.10375 | 1
41 | 0.49756 | 0.1 | 0 | 0.24878 | 1
42 | 0.20524 | 0.1 | 0 | 0.10262 | 1
43 | 0.47442 | 0.1 | 0 | 0.23721 | 1
44 | 0.20318 | 0.1 | 0 | 0.10159 | 1
45 | 0.2 | 0.1 | 0 | 0.1 | 1
46 | 0.2013 | 0.1 | 0 | 0.10065 | 1
47 | 0.43404 | 0.1 | 0 | 0.21702 | 1
48 | 0.19958 | 0.1 | 0 | 0.099792 | 1
49 | 0.41633 | 0.1 | 0 | 0.20816 | 1
50 | 0.198 | 0.1 | 0 | 0.099 | 1

## TestTypes
layers (optional) | Layer 1 | Layer 2
Test Type
Steady_State | 0 | 1
F_profile | 0 | 1
ANG_profile | 0 | 1
V_profile | 0 | 1
V_stp_profile | 0 | 1
Q_stp_profile | 0 | 1
PF_stp_profile | 0 | 1
P_stp_profile | 0 | 0
ORT | 0 | 0
Fault | 4 | 0
Fault_TOV | 0 | 0
Multifault_random | 0 | 1
Multifault | 0 | 1
P_prim_lim_profile | 0 | 0
Auxiliary_profile | 0 | 0
Note on A5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Angle change profile is defined as a step profile and not as a linear interpolated profile. The reason is that the profile cannot be programmes into a test source but rather needs to be written vie the PSS/E API. A step profile limits the number or changes that need to be made during runtime.
Note on A11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Oscillatory rejection test
Note on A12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: inductive or ohmic fault, different types. to be specified by residual voltage at POC+X/R or resistance+reactcance or Impedance+X/R ratio.
Note on A13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: capacitive fault to increase voltage

## Bus Lib
Num | Bus_num | Bus_name_PSSE | Bus_name_full
1 | 0 | N/A | N/A
2 | 11190 | BRG | BRG
3 | 11358 | KMTS | KMTS
4 | 21200 | DLP330 | DLP330
5 | 21893 | WAG | WAG
6 | 22201 | DLP220 | DLP220
7 | 23010 | BLRD | BLRD
8 | 32040 | BATS | BATS
9 | 32050 | ARTS | ARTS
10 | 32080 | BETS | BETS
11 | 32090 | ELTS | ELTS
12 | 32180 | DDTS | DDTS
13 | 32230 | FVTS | FVTS
14 | 32240 | GNTS1 | GNTS1
15 | 32280 | HOTS | HOTS
16 | 32380 | KGTS | KGTS
17 | 32480 | MLTS | MLTS
18 | 32610 | RCTS | RCTS
19 | 32641 | ROTS_A | ROTS_A
20 | 32680 | RWTS | RWTS
21 | 32700 | SHTS | SHTS
22 | 32793 | MRT | MRT
23 | 32816 | WBTS | WBTS
24 | 32831 | WETS | WETS
25 | 32851 | TTS | TTS
26 | 32940 | YPS | YPS
27 | 36700 | SHTS66 | SHTS66
28 | 36703 | ECA1 | ECA1
29 | 36703 | ECA2 | ECA2
30 | 36704 | KYM1 | KYM1
31 | 36704 | KYM | KYM
32 | 36705 | MNA | MNA
33 | 36706 | NKA | NKA
34 | 36707 | SHN1 | SHN1
35 | 36708 | STN | STN
36 | 36715 | SHP | SHP
37 | 36716 | NSF | NSF
38 | 36717 | LSF | LSF
39 | 37704 | KYM22 | KYM22
40 | 37734 | KSSF | KSSF
41 | 367172 | LSF2 | LSF2
42 | 367177 | LSF2Tx | LSF2Tx
43 | 367177 | LSF2Tx | LSF2Tx
44 | 88888 | WGNSF | WGNSF
45 | 367170 | LSF | LSF
46 | 306580 | 3ARAR_T_220A | ARART 220 kV
47 | 306585 | 3ARAR_T_220F | ARART 220 kV
48 | 316580 | 3BULGTS_220A | BULGANA 220 kV
49 | 334081 | HOTS 220 KV_POC | HOR_POC
50 | 342280 | 3KIAMAL_220A | KIAMAL 220 kV
51 | 306581 | 3ARAR_T_220B | ARART 220 kV
52 | 321580 | 3CROWLA_220A | CROWNLANDS 220 KV
53 | 355880 | 3MURRAW_220A | MURRA WARRA 220 kV
54 | 364080 | 3REDCLF_220A | RED CLIFF 220 kV
55 | 309080 | 3BALRAT_220A | BALARAT 220 kV
56 | 384080 | 3WAUBRA_220A | WAUBRA 220 kV
57 | 334030 | 3HORSHM__66A | HORSHAM 66 kV
58 | 334090 | HOR_HV | HOR_HV
59 | 334091 | HOR_MV | HOR_MV
60 | 334092 | HOR_MV_PV | HOR_MV_PV
61 | 334093 | HOR_MV_BESS | HOR_MV_BESS
62 | 334094 | HOR_LV_PV | HOR_LV_PV
63 | 334095 | HOR_LV_BESS | HOR_LV_BESS

## MonitorBuses
bus_number | bus_name | bus_code
306580 | 3ARAR_T_220A | ARART 220 kV | 3ARAR_T_220A = 306580 # ARART 220 kV | 3ARAR_T_220A = 306580 # ARART 220 kV
306585 | 3ARAR_T_220F | ARART 220 kV | 3ARAR_T_220F = 306585 # ARART 220 kV | 3ARAR_T_220F = 306585 # ARART 220 kV
316580 | 3BULGTS_220A | BULGANA 220 kV | 3BULGTS_220A = 316580 # BULGANA 220 kV | 3BULGTS_220A = 316580 # BULGANA 220 kV
334081 | HOTS 220 KV_POC | HOR_POC | HOTS 220 KV_POC = 334081 # HOR_POC | HOTS 220 KV_POC = 334081 # HORSHAM 220 kV
342280 | 3KIAMAL_220A | KIAMAL 220 kV | 3KIAMAL_220A = 342280 # KIAMAL 220 kV | 3KIAMAL_220A = 342280 # KIAMAL 220 kV
306581 | 3ARAR_T_220B | ARART 220 kV | 3ARAR_T_220B = 306581 # ARART 220 kV | 3ARAR_T_220B = 306581 # ARART 220 kV
321580 | 3CROWLA_220A | CROWNLANDS 220 KV | 3CROWLA_220A = 321580 # CROWNLANDS 220 KV | 3CROWLA_220A = 321580 # CROWNLANDS 220 KV
355880 | 3MURRAW_220A | MURRA WARRA 220 kV | 3MURRAW_220A = 355880 # MURRA WARRA 220 kV | 3MURRAW_220A = 355880 # MURRA WARRA 220 kV
364080 | 3REDCLF_220A | RED CLIFF 220 kV | 3REDCLF_220A = 364080 # RED CLIFF 220 kV | 3REDCLF_220A = 364080 # RED CLIFF 220 kV
309080 | 3BALRAT_220A | BALARAT 220 kV | 3BALRAT_220A = 309080 # BALARAT 220 kV | 3BALRAT_220A = 309080 # BALARAT 220 kV
384080 | 3WAUBRA_220A | WAUBRA 220 kV | 3WAUBRA_220A = 384080 # WAUBRA 220 kV | 3WAUBRA_220A = 384080 # WAUBRA 220 kV

## MonitorBranches
brch_from | brch_to | brch_id | brch_name | brch_code | brch_name | brch_code | brch_name
309080 | 384080 | 1 | 3BALRAT_220A - 3WAUBRA_220A | 3BALRAT_220A - 3WAUBRA_220A | 3BALRAT_220A - 3WAUBRA_220A | BALARAT 220 kV - WAUBRA 220 kV
306581 | 384080 | 1 | 3ARAR_T_220B - 3WAUBRA_220A | 3ARAR_T_220B - 3WAUBRA_220A | 3ARAR_T_220B - 3WAUBRA_220A | ARART 220 kV - WAUBRA 220 kV
306585 | 321580 | 1 | 3ARAR_T_220F - 3CROWLA_220A | 3ARAR_T_220F - 3CROWLA_220A | 3ARAR_T_220F - 3CROWLA_220A | ARART 220 kV - CROWNLANDS 220 KV
316580 | 321580 | 1 | 3BULGTS_220A - 3CROWLA_220A | 3BULGTS_220A - 3CROWLA_220A | 3BULGTS_220A - 3CROWLA_220A | BULGANA 220 kV - CROWNLANDS 220 KV
316580 | 334081 | 1 | 3BULGTS_220A - HOTS 220 KV | 3BULGTS_220A - HOTS 220 KV_POC | 3BULGTS_220A - HOTS 220 KV_POC | BULGANA 220 kV - HOR_POC
334030 | 334081 | 1 | 3HORSHM__66A - HOTS 220 KV | 3HORSHM__66A - HOTS 220 KV_POC | 3HORSHM__66A - HOTS 220 KV_POC | HORSHAM 66 kV - HOR_POC
334030 | 334081 | 2 | 3HORSHM__66A - HOTS 220 KV | 3HORSHM__66A - HOTS 220 KV_POC | 3HORSHM__66A - HOTS 220 KV_POC | HORSHAM 66 kV - HOR_POC
334081 | 355880 | 1 | HOTS 220 KV - 3MURRAW_220A | HOTS 220 KV_POC - 3MURRAW_220A | HOTS 220 KV_POC - 3MURRAW_220A | HOR_POC - MURRA WARRA 220 kV
342280 | 355880 | 1 | 3KIAMAL_220A -3MURRAW_220A | 3KIAMAL_220A - 3MURRAW_220A | 3KIAMAL_220A - 3MURRAW_220A | KIAMAL 220 kV - MURRA WARRA 220 kV
342280 | 364080 | 1 | 3KIAMAL_220A - 3REDCLF_220A | 3KIAMAL_220A - 3REDCLF_220A | 3KIAMAL_220A - 3REDCLF_220A | KIAMAL 220 kV - RED CLIFF 220 kV