## CATL_25C_0.9pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 25 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1490 |  | VDC
Nom. Battery Voltage** |  |  |  | 1291.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1159 |  | VDC |  | Please select:
AC Voltage |  |  |  | 0.9 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @25°C, 1159Vdc min. battery voltage and 0.9pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2268.0028 | 2268.0023 | 2268.0025 | 2268.002 | 0 | 0 | 0 | 0 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.002
0.01 | 2268.0028 | 2268.0023 | 2268.0025 | 2268.002 | 0.02268 | 0.02268 | -0.02268 | -0.02268 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.002
0.05 | 2282.228 | 2279.3649 | 2280.3628 | 2277.8304 | 114.1114 | 113.9682 | -114.0181 | -113.8915 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.0023
0.1 | 2296.4559 | 2290.7298 | 2292.7256 | 2287.6608 | 229.6456 | 229.073 | -229.2726 | -228.7661 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.0023
0.15 | 2338.5097 | 2325.2826 | 2328.3629 | 2315.3944 | 350.7764 | 348.7924 | -349.2544 | -347.3092 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.0023
0.2 | 2380.5634 | 2359.8354 | 2364.0001 | 2343.128 | 476.1127 | 471.9671 | -472.8 | -468.6256 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.0023
0.25 | 2449.5714 | 2417.0691 | 2420.2186 | 2387.0711 | 612.3929 | 604.2673 | -605.0547 | -596.7678 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.0023
0.3 | 2518.5795 | 2474.3028 | 2476.4371 | 2431.0143 | 755.5739 | 742.2909 | -742.9311 | -729.3043 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.0023
0.35 | 2609.4155 | 2554.2344 | 2550.3104 | 2489.0566 | 913.2954 | 893.9821 | -892.6086 | -871.1698 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.0023
0.4 | 2700.2516 | 2634.1661 | 2624.1837 | 2547.099 | 1080.1006 | 1053.6664 | -1049.6735 | -1018.8396 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.0023
0.45 | 2809.7044 | 2734.1703 | 2712.3967 | 2616.8219 | 1264.367 | 1230.3766 | -1220.5785 | -1177.5699 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.0023
0.5 | 2919.1571 | 2834.1745 | 2800.6097 | 2686.5449 | 1459.5786 | 1417.0873 | -1400.3049 | -1343.2724 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.0023
0.51 | 2944.2394 | 2858.0423 | 2819.8237 | 2703.448 | 1501.5621 | 1457.6016 | -1438.1101 | -1378.7585 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.0023
0.52 | 2969.3216 | 2881.9102 | 2839.0377 | 2720.3512 | 1544.0472 | 1498.5933 | -1476.2996 | -1414.5826 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.0023
0.53 | 2994.4038 | 2905.778 | 2858.2517 | 2737.2543 | 1587.034 | 1540.0623 | -1514.8734 | -1450.7448 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.0023
0.54 | 3019.486 | 2929.6458 | 2877.4657 | 2754.1574 | 1630.5225 | 1582.0087 | -1553.8315 | -1487.245 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.0023
0.55 | 3044.5683 | 2953.5137 | 2896.6798 | 2771.0606 | 1674.5126 | 1624.4325 | -1593.1739 | -1524.0833 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.0023
0.56 | 3069.6505 | 2977.3815 | 2915.8938 | 2787.9637 | 1719.0043 | 1667.3336 | -1632.9005 | -1561.2597 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.0023
0.57 | 3094.7327 | 3001.2493 | 2935.1078 | 2804.8669 | 1763.9977 | 1710.7121 | -1673.0114 | -1598.7741 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.0023
0.58 | 3119.815 | 3025.1171 | 2954.3218 | 2821.77 | 1809.4927 | 1754.5679 | -1713.5066 | -1636.6266 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.0023
0.59 | 3144.8972 | 3048.985 | 2973.5358 | 2838.6732 | 1855.4893 | 1798.9011 | -1754.3861 | -1674.8172 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.0023
0.6 | 3169.9794 | 3072.8528 | 2992.7498 | 2855.5763 | 1901.9877 | 1843.7117 | -1795.6499 | -1713.3458 | 2268.0028 | -2268.0023 | 2268.0025 | -2268.0023
0.61 | 3197.497 | 3101.189 | 3013.6695 | 2860.966 | 1950.4732 | 1891.7253 | -1838.3384 | -1745.1892 | 2268.0028 | -2268.0023 | 2268.0025 | -2267.0335
0.62 | 3225.0146 | 3129.5252 | 3034.5892 | 2866.3556 | 1999.509 | 1940.3056 | -1881.4453 | -1777.1405 | 2268.0028 | -2268.0023 | 2268.0025 | -2248.9478
0.63 | 3252.5321 | 3157.8613 | 3055.5089 | 2871.7452 | 2049.0953 | 1989.4526 | -1924.9706 | -1809.1995 | 2268.0028 | -2268.0023 | 2268.0025 | -2230.1834
0.64 | 3280.0497 | 3186.1975 | 3076.4286 | 2877.1349 | 2099.2318 | 2039.1664 | -1968.9143 | -1841.3663 | 2268.0028 | -2268.0023 | 2268.0025 | -2210.7182
0.65 | 3307.5673 | 3214.5337 | 3097.3483 | 2882.5245 | 2149.9187 | 2089.4469 | -2013.2764 | -1873.6409 | 2268.0028 | -2268.0023 | 2268.0025 | -2190.529
0.66 | 3335.0849 | 3242.8699 | 3118.268 | 2887.9141 | 2201.156 | 2140.2941 | -2058.0569 | -1906.0233 | 2268.0028 | -2268.0023 | 2268.0025 | -2169.5905
0.67 | 3362.6024 | 3271.2061 | 3139.1877 | 2893.3037 | 2252.9436 | 2191.7081 | -2103.2558 | -1938.5135 | 2268.0028 | -2268.0023 | 2268.0025 | -2147.8761
0.68 | 3390.12 | 3299.5422 | 3160.1074 | 2898.6934 | 2305.2816 | 2243.6887 | -2148.873 | -1971.1115 | 2268.0028 | -2268.0023 | 2268.0025 | -2125.3571
0.69 | 3417.6376 | 3327.8784 | 3181.0271 | 2904.083 | 2358.1699 | 2296.2361 | -2194.9087 | -2003.8173 | 2268.0028 | -2268.0023 | 2268.0025 | -2102.0025
0.7 | 3445.1552 | 3356.2146 | 3201.9468 | 2909.4726 | 2411.6086 | 2349.3502 | -2241.3628 | -2036.6309 | 2268.0028 | -2268.0023 | 2268.0025 | -2077.7791
0.71 | 3474.833 | 3384.6412 | 3201.2379 | 2912.5671 | 2467.1314 | 2403.0953 | -2272.8789 | -2067.9227 | 2268.0028 | -2268.0023 | 2254.3171 | -2051.0347
0.72 | 3504.5109 | 3413.0679 | 3200.529 | 2915.6616 | 2523.2478 | 2457.4089 | -2304.3809 | -2099.2764 | 2268.0028 | -2268.0023 | 2221.0841 | -2023.3935
0.73 | 3534.1887 | 3441.4945 | 3199.8202 | 2918.7561 | 2579.9578 | 2512.291 | -2335.8687 | -2130.692 | 2268.0028 | -2268.0023 | 2186.908 | -1994.8155
0.74 | 3563.8666 | 3469.9212 | 3199.1113 | 2921.8506 | 2637.2613 | 2567.7417 | -2367.3423 | -2162.1694 | 2268.0028 | -2268.0023 | 2151.7442 | -1965.2568
0.75 | 3593.5444 | 3498.3478 | 3198.4024 | 2924.9451 | 2695.1583 | 2623.7609 | -2398.8018 | -2193.7088 | 2268.0028 | -2268.0023 | 2115.5443 | -1934.6693
0.76 | 3623.2223 | 3526.7744 | 3197.6935 | 2928.0396 | 2753.6489 | 2680.3486 | -2430.2471 | -2225.3101 | 2268.0028 | -2268.0023 | 2078.2548 | -1903.0005
0.77 | 3652.9002 | 3555.2011 | 3196.9846 | 2931.1341 | 2812.7331 | 2737.5048 | -2461.6782 | -2256.9732 | 2268.0028 | -2268.0023 | 2039.8165 | -1870.1922
0.78 | 3682.578 | 3583.6277 | 3196.2758 | 2934.2286 | 2872.4109 | 2795.2296 | -2493.0951 | -2288.6983 | 2268.0028 | -2242.5608 | 2000.1639 | -1836.1801
0.79 | 3712.2559 | 3612.0544 | 3195.5669 | 2937.3231 | 2932.6821 | 2853.5229 | -2524.4978 | -2320.4852 | 2268.0028 | -2214.5752 | 1959.2239 | -1800.8929
0.8 | 3741.9337 | 3640.481 | 3194.858 | 2940.4175 | 2993.547 | 2912.3848 | -2555.8864 | -2352.334 | 2245.1602 | -2184.2886 | 1916.9148 | -1764.2505
0.81 | 3742.8718 | 3646.7461 | 3191.6083 | 2945.5836 | 3031.7262 | 2953.8643 | -2585.2027 | -2385.9227 | 2194.9319 | -2138.5608 | 1871.6545 | -1727.3782
0.82 | 3743.8099 | 3653.0111 | 3188.3587 | 2950.7496 | 3069.9241 | 2995.4691 | -2614.4541 | -2419.6147 | 2142.8202 | -2090.8503 | 1824.9002 | -1688.9014
0.83 | 3744.748 | 3659.2762 | 3185.109 | 2955.9157 | 3108.1408 | 3037.1993 | -2643.6404 | -2453.41 | 2088.6833 | -2041.0103 | 1776.5372 | -1648.7015
0.84 | 3745.686 | 3665.5413 | 3181.8593 | 2961.0817 | 3146.3763 | 3079.0547 | -2672.7618 | -2487.3086 | 2032.3583 | -1988.8728 | 1726.4336 | -1606.6427
0.85 | 3746.6241 | 3671.8064 | 3178.6096 | 2966.2478 | 3184.6305 | 3121.0354 | -2701.8182 | -2521.3106 | 1973.6567 | -1934.244 | 1674.4365 | -1562.568
0.86 | 3747.5622 | 3678.0714 | 3175.3599 | 2971.4138 | 3222.9035 | 3163.1414 | -2730.8096 | -2555.4159 | 1912.3586 | -1876.8979 | 1620.3672 | -1516.2947
0.87 | 3748.5003 | 3684.3365 | 3172.1103 | 2976.5799 | 3261.1952 | 3205.3728 | -2759.7359 | -2589.6245 | 1848.2045 | -1816.5685 | 1564.0144 | -1467.6078
0.88 | 3749.4384 | 3690.6016 | 3168.8606 | 2981.7459 | 3299.5058 | 3247.7294 | -2788.5973 | -2623.9364 | 1780.8845 | -1752.9386 | 1505.1254 | -1416.2508
0.89 | 3750.3764 | 3696.8666 | 3165.6109 | 2986.9119 | 3337.835 | 3290.2113 | -2817.3937 | -2658.3516 | 1710.0236 | -1685.6253 | 1443.3936 | -1361.9139
0.9 | 3751.3145 | 3703.1317 | 3162.3612 | 2992.078 | 3376.1831 | 3332.8185 | -2846.1251 | -2692.8702 | 1635.1601 | -1614.1577 | 1378.4413 | -1304.2166
0.91 | 3752.1151 | 3713.5735 | 3155.5896 | 2998.4455 | 3414.4248 | 3379.3519 | -2871.5865 | -2728.5854 | 1555.6579 | -1539.6782 | 1308.3335 | -1243.1802
0.92 | 3752.9158 | 3724.0154 | 3148.8179 | 3004.813 | 3452.6825 | 3426.0942 | -2896.9124 | -2764.428 | 1470.8366 | -1459.51 | 1234.0795 | -1177.6414
0.93 | 3753.7164 | 3734.4572 | 3142.0462 | 3011.1805 | 3490.9562 | 3473.0452 | -2922.103 | -2800.3979 | 1379.7142 | -1372.6353 | 1154.889 | -1106.7881
0.94 | 3754.517 | 3744.8991 | 3135.2745 | 3017.548 | 3529.246 | 3520.2051 | -2947.158 | -2836.4952 | 1280.9452 | -1277.6638 | 1069.6755 | -1029.5103
0.95 | 3755.3176 | 3755.3409 | 3128.5028 | 3023.9156 | 3567.5517 | 3567.5738 | -2972.0777 | -2872.7198 | 1172.5976 | -1172.6048 | 976.8747 | -944.2173
0.96 | 3760.2541 | 3760.2727 | 3119.7025 | 3036.0327 | 3609.8439 | 3609.8618 | -2994.9144 | -2914.5914 | 1052.8711 | -1052.8764 | 873.5167 | -850.0892
0.97 | 3765.1906 | 3765.2045 | 3110.9022 | 3048.1499 | 3652.2349 | 3652.2484 | -3017.5751 | -2956.7054 | 915.3363 | -915.3397 | 756.2756 | -741.0202
0.98 | 3770.1271 | 3770.1364 | 3102.1019 | 3060.267 | 3694.7245 | 3694.7336 | -3040.0599 | -2999.0617 | 750.2458 | -750.2477 | 617.3105 | -608.9854
0.99 | 3775.0635 | 3775.0682 | 3093.3016 | 3072.3842 | 3737.3129 | 3737.3175 | -3062.3686 | -3041.6603 | 532.5382 | -532.5389 | 436.3639 | -433.4131
1 | 3780 | 3780 | 3084.5013 | 3084.5013 | 3780 | 3780 | -3084.5013 | -3084.5013 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_25C_1.0pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 25 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1490 |  | VDC
Nom. Battery Voltage** |  |  |  | 1291.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1159 |  | VDC |  | Please select:
AC Voltage |  |  |  | 1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @25°C, 1159Vdc min. battery voltage and 1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2520.0032 | 2520.0025 | 2520.0027 | 2520.0022 | 0 | 0 | 0 | 0 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0022
0.01 | 2520.0032 | 2520.0025 | 2520.0027 | 2520.0022 | 0.0252 | 0.0252 | -0.0252 | -0.0252 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0022
0.05 | 2535.8089 | 2532.6277 | 2533.7364 | 2530.9227 | 126.7904 | 126.6314 | -126.6868 | -126.5461 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0025
0.1 | 2551.6177 | 2545.2553 | 2547.4729 | 2541.8454 | 255.1618 | 254.5255 | -254.7473 | -254.1845 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0025
0.15 | 2598.3441 | 2583.6473 | 2587.0699 | 2572.6605 | 389.7516 | 387.5471 | -388.0605 | -385.8991 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0025
0.2 | 2645.0704 | 2622.0393 | 2626.6668 | 2603.4755 | 529.0141 | 524.4079 | -525.3334 | -520.6951 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0025
0.25 | 2721.746 | 2685.6323 | 2689.1318 | 2652.3013 | 680.4365 | 671.4081 | -672.2829 | -663.0753 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0025
0.3 | 2798.4217 | 2749.2254 | 2751.5967 | 2701.127 | 839.5265 | 824.7676 | -825.479 | -810.3381 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0025
0.35 | 2899.3506 | 2838.0383 | 2833.6782 | 2765.6185 | 1014.7727 | 993.3134 | -991.7874 | -967.9665 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0025
0.4 | 3000.2795 | 2926.8512 | 2915.7596 | 2830.11 | 1200.1118 | 1170.7405 | -1166.3038 | -1132.044 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0025
0.45 | 3121.8937 | 3037.967 | 3013.7741 | 2907.5799 | 1404.8522 | 1367.0851 | -1356.1983 | -1308.411 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0025
0.5 | 3243.5079 | 3149.0828 | 3111.7886 | 2985.0499 | 1621.754 | 1574.5414 | -1555.8943 | -1492.5249 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0025
0.51 | 3271.3771 | 3175.6026 | 3133.1375 | 3003.8311 | 1668.4023 | 1619.5573 | -1597.9001 | -1531.9539 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0025
0.52 | 3299.2462 | 3202.1224 | 3154.4864 | 3022.6124 | 1715.608 | 1665.1037 | -1640.3329 | -1571.7584 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0025
0.53 | 3327.1154 | 3228.6422 | 3175.8353 | 3041.3937 | 1763.3711 | 1711.1804 | -1683.1927 | -1611.9386 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0025
0.54 | 3354.9845 | 3255.162 | 3197.1842 | 3060.1749 | 1811.6916 | 1757.7875 | -1726.4794 | -1652.4945 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0025
0.55 | 3382.8536 | 3281.6818 | 3218.5331 | 3078.9562 | 1860.5695 | 1804.925 | -1770.1932 | -1693.4259 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0025
0.56 | 3410.7228 | 3308.2016 | 3239.882 | 3097.7375 | 1910.0048 | 1852.5929 | -1814.3339 | -1734.733 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0025
0.57 | 3438.5919 | 3334.7215 | 3261.2309 | 3116.5188 | 1959.9974 | 1900.7912 | -1858.9016 | -1776.4157 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0025
0.58 | 3466.4611 | 3361.2413 | 3282.5798 | 3135.3 | 2010.5474 | 1949.5199 | -1903.8963 | -1818.474 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0025
0.59 | 3494.3302 | 3387.7611 | 3303.9287 | 3154.0813 | 2061.6548 | 1998.779 | -1949.3179 | -1860.908 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0025
0.6 | 3522.1994 | 3414.2809 | 3325.2776 | 3172.8626 | 2113.3196 | 2048.5685 | -1995.1665 | -1903.7175 | 2520.0032 | -2520.0025 | 2520.0027 | -2520.0025
0.61 | 3552.7744 | 3445.7655 | 3348.5217 | 3178.8511 | 2167.1924 | 2101.917 | -2042.5982 | -1939.0991 | 2520.0032 | -2520.0025 | 2520.0027 | -2518.9261
0.62 | 3583.3495 | 3477.2502 | 3371.7658 | 3184.8395 | 2221.6767 | 2155.8951 | -2090.4948 | -1974.6005 | 2520.0032 | -2520.0025 | 2520.0027 | -2498.8309
0.63 | 3613.9246 | 3508.7348 | 3395.0099 | 3190.828 | 2276.7725 | 2210.5029 | -2138.8562 | -2010.2217 | 2520.0032 | -2520.0025 | 2520.0027 | -2477.9815
0.64 | 3644.4997 | 3540.2195 | 3418.254 | 3196.8165 | 2332.4798 | 2265.7405 | -2187.6826 | -2045.9626 | 2520.0032 | -2520.0025 | 2520.0027 | -2456.3536
0.65 | 3675.0748 | 3571.7041 | 3441.4981 | 3202.805 | 2388.7986 | 2321.6077 | -2236.9738 | -2081.8232 | 2520.0032 | -2520.0025 | 2520.0027 | -2433.9211
0.66 | 3705.6498 | 3603.1888 | 3464.7422 | 3208.7935 | 2445.7289 | 2378.1046 | -2286.7299 | -2117.8037 | 2520.0032 | -2520.0025 | 2520.0027 | -2410.6561
0.67 | 3736.2249 | 3634.6734 | 3487.9863 | 3214.7819 | 2503.2707 | 2435.2312 | -2336.9508 | -2153.9039 | 2520.0032 | -2520.0025 | 2520.0027 | -2386.5291
0.68 | 3766.8 | 3666.158 | 3511.2304 | 3220.7704 | 2561.424 | 2492.9875 | -2387.6367 | -2190.1239 | 2520.0032 | -2520.0025 | 2520.0027 | -2361.5079
0.69 | 3797.3751 | 3697.6427 | 3534.4746 | 3226.7589 | 2620.1888 | 2551.3735 | -2438.7874 | -2226.4636 | 2520.0032 | -2520.0025 | 2520.0027 | -2335.5583
0.7 | 3827.9502 | 3729.1273 | 3557.7187 | 3232.7474 | 2679.5651 | 2610.3891 | -2490.4031 | -2262.9232 | 2520.0032 | -2520.0025 | 2520.0027 | -2308.6434
0.71 | 3860.9256 | 3760.7125 | 3556.931 | 3236.1857 | 2741.2572 | 2670.1059 | -2525.421 | -2297.6919 | 2520.0032 | -2520.0025 | 2504.7968 | -2278.9274
0.72 | 3893.901 | 3792.2976 | 3556.1434 | 3239.624 | 2803.6087 | 2730.4543 | -2560.4232 | -2332.5293 | 2520.0032 | -2520.0025 | 2467.8713 | -2248.2151
0.73 | 3926.8764 | 3823.8828 | 3555.3557 | 3243.0624 | 2866.6197 | 2791.4344 | -2595.4097 | -2367.4355 | 2520.0032 | -2520.0025 | 2429.8977 | -2216.4617
0.74 | 3959.8518 | 3855.468 | 3554.5681 | 3246.5007 | 2930.2903 | 2853.0463 | -2630.3804 | -2402.4105 | 2520.0032 | -2520.0025 | 2390.8269 | -2183.6187
0.75 | 3992.8272 | 3887.0531 | 3553.7804 | 3249.939 | 2994.6204 | 2915.2898 | -2665.3353 | -2437.4542 | 2520.0032 | -2520.0025 | 2350.6048 | -2149.6326
0.76 | 4025.8026 | 3918.6383 | 3552.9928 | 3253.3773 | 3059.6099 | 2978.1651 | -2700.2745 | -2472.5668 | 2520.0032 | -2520.0025 | 2309.172 | -2114.445
0.77 | 4058.778 | 3950.2234 | 3552.2052 | 3256.8156 | 3125.259 | 3041.672 | -2735.198 | -2507.748 | 2520.0032 | -2520.0025 | 2266.4628 | -2077.9913
0.78 | 4091.7534 | 3981.8086 | 3551.4175 | 3260.254 | 3191.5676 | 3105.8107 | -2770.1057 | -2542.9981 | 2520.0032 | -2491.7342 | 2222.4043 | -2040.2001
0.79 | 4124.7288 | 4013.3937 | 3550.6299 | 3263.6923 | 3258.5357 | 3170.5811 | -2804.9976 | -2578.3169 | 2520.0032 | -2460.6392 | 2176.9155 | -2000.9921
0.8 | 4157.7042 | 4044.9789 | 3549.8422 | 3267.1306 | 3326.1633 | 3235.9831 | -2839.8738 | -2613.7045 | 2494.6225 | -2426.9873 | 2129.9053 | -1960.2784
0.81 | 4158.7465 | 4051.9401 | 3546.2315 | 3272.8706 | 3368.5846 | 3282.0715 | -2872.4475 | -2651.0252 | 2438.8132 | -2376.1787 | 2079.6161 | -1919.3091
0.82 | 4159.7888 | 4058.9013 | 3542.6207 | 3278.6107 | 3411.0268 | 3328.299 | -2904.949 | -2688.4608 | 2380.9113 | -2323.167 | 2027.6669 | -1876.5572
0.83 | 4160.8311 | 4065.8625 | 3539.01 | 3284.3507 | 3453.4898 | 3374.6658 | -2937.3783 | -2726.0111 | 2320.7592 | -2267.7892 | 1973.9302 | -1831.8906
0.84 | 4161.8734 | 4072.8236 | 3535.3992 | 3290.0908 | 3495.9736 | 3421.1719 | -2969.7353 | -2763.6763 | 2258.1759 | -2209.8587 | 1918.2595 | -1785.1585
0.85 | 4162.9157 | 4079.7848 | 3531.7885 | 3295.8308 | 3538.4783 | 3467.8171 | -3002.0202 | -2801.4562 | 2192.9519 | -2149.16 | 1860.485 | -1736.1866
0.86 | 4163.958 | 4086.746 | 3528.1777 | 3301.5709 | 3581.0039 | 3514.6016 | -3034.2328 | -2839.351 | 2124.8429 | -2085.4421 | 1800.408 | -1684.7719
0.87 | 4165.0003 | 4093.7072 | 3524.567 | 3307.3109 | 3623.5503 | 3561.5253 | -3066.3733 | -2877.3605 | 2053.5606 | -2018.4094 | 1737.7938 | -1630.6754
0.88 | 4166.0426 | 4100.6684 | 3520.9562 | 3313.051 | 3666.1175 | 3608.5882 | -3098.4415 | -2915.4849 | 1978.7606 | -1947.7096 | 1672.3615 | -1573.612
0.89 | 4167.0849 | 4107.6296 | 3517.3455 | 3318.791 | 3708.7056 | 3655.7903 | -3130.4375 | -2953.724 | 1900.0262 | -1872.9169 | 1603.7707 | -1513.2377
0.9 | 4168.1272 | 4114.5908 | 3513.7347 | 3324.5311 | 3751.3145 | 3703.1317 | -3162.3612 | -2992.078 | 1816.8445 | -1793.5085 | 1531.6015 | -1449.1295
0.91 | 4169.0168 | 4126.1928 | 3506.2106 | 3331.6061 | 3793.8053 | 3754.8355 | -3190.6517 | -3031.7616 | 1728.5088 | -1710.7536 | 1453.7038 | -1381.3114
0.92 | 4169.9064 | 4137.7949 | 3498.6865 | 3338.6811 | 3836.3139 | 3806.7713 | -3218.7916 | -3071.5866 | 1634.2629 | -1621.6778 | 1371.1995 | -1308.4904
0.93 | 4170.796 | 4149.3969 | 3491.1624 | 3345.7561 | 3878.8403 | 3858.9391 | -3246.7811 | -3111.5532 | 1533.0158 | -1525.1503 | 1283.21 | -1229.7645
0.94 | 4171.6856 | 4160.9989 | 3483.6383 | 3352.8312 | 3921.3844 | 3911.339 | -3274.62 | -3151.6613 | 1423.2725 | -1419.6265 | 1188.5284 | -1143.9003
0.95 | 4172.5751 | 4172.601 | 3476.1143 | 3359.9062 | 3963.9464 | 3963.9709 | -3302.3085 | -3191.9109 | 1302.8862 | -1302.8942 | 1085.4163 | -1049.1304
0.96 | 4178.0601 | 4178.0808 | 3466.3361 | 3373.3697 | 4010.9377 | 4010.9576 | -3327.6827 | -3238.4349 | 1169.8568 | -1169.8626 | 970.5741 | -944.5435
0.97 | 4183.5451 | 4183.5606 | 3456.558 | 3386.8332 | 4058.0387 | 4058.0538 | -3352.8613 | -3285.2282 | 1017.0404 | -1017.0441 | 840.3062 | -823.3558
0.98 | 4189.0301 | 4189.0404 | 3446.7799 | 3400.2967 | 4105.2495 | 4105.2596 | -3377.8443 | -3332.2907 | 833.6065 | -833.6085 | 685.9005 | -676.6505
0.99 | 4194.515 | 4194.5202 | 3437.0018 | 3413.7602 | 4152.5699 | 4152.575 | -3402.6318 | -3379.6226 | 591.7092 | -591.7099 | 484.8488 | -481.5701
1 | 4200 | 4200 | 3427.2237 | 3427.2237 | 4200 | 4200 | -3427.2237 | -3427.2237 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_25C_1.1pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 25 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1490 |  | VDC
Nom. Battery Voltage** |  |  |  | 1291.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1159 |  | VDC |  | Please select:
AC Voltage |  |  |  | 1.1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @25°C, 1159Vdc min. battery voltage and 1.1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2520.0034 | 2520.0026 | 2520.0033 | 2520.0025 | 0 | 0 | 0 | 0 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0025
0.01 | 2520.0034 | 2520.0026 | 2520.0033 | 2520.0025 | 0.0252 | 0.0252 | -0.0252 | -0.0252 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0025
0.05 | 2537.1288 | 2533.1213 | 2536.6993 | 2532.6105 | 126.8564 | 126.6561 | -126.835 | -126.6305 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.1 | 2554.2577 | 2546.2425 | 2553.3987 | 2545.221 | 255.4258 | 254.6243 | -255.3399 | -254.5221 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.15 | 2605.2855 | 2585.931 | 2601.739 | 2581.7046 | 390.7928 | 387.8896 | -390.2609 | -387.2557 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.2 | 2656.3132 | 2625.6194 | 2650.0793 | 2618.1881 | 531.2626 | 525.1239 | -530.0159 | -523.6376 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.25 | 2736.8794 | 2693.4311 | 2725.9743 | 2675.8298 | 684.2199 | 673.3578 | -681.4936 | -668.9574 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.3 | 2817.4457 | 2761.2429 | 2801.8693 | 2733.4714 | 845.2337 | 828.3729 | -840.5608 | -820.0414 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.35 | 2923.0544 | 2854.2582 | 2900.368 | 2808.1679 | 1023.069 | 998.9904 | -1015.1288 | -982.8588 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.4 | 3028.6631 | 2947.2735 | 2998.8667 | 2882.8644 | 1211.4652 | 1178.9094 | -1199.5467 | -1153.1458 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.45 | 3154.484 | 3062.8784 | 3113.3006 | 2973.3807 | 1419.5178 | 1378.2953 | -1400.9853 | -1338.0213 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.5 | 3280.3049 | 3178.4834 | 3227.7344 | 3063.897 | 1640.1524 | 1589.2417 | -1613.8672 | -1531.9485 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.51 | 3308.6562 | 3206.5096 | 3252.0651 | 3085.6164 | 1687.4147 | 1635.3199 | -1658.5532 | -1573.6643 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.52 | 3337.0075 | 3234.5357 | 3276.3957 | 3107.3357 | 1735.2439 | 1681.9586 | -1703.7258 | -1615.8146 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.53 | 3365.3589 | 3262.5618 | 3300.7263 | 3129.0551 | 1783.6402 | 1729.1578 | -1749.3849 | -1658.3992 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.54 | 3393.7102 | 3290.588 | 3325.0569 | 3150.7745 | 1832.6035 | 1776.9175 | -1795.5307 | -1701.4182 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.55 | 3422.0615 | 3318.6141 | 3349.3876 | 3172.4939 | 1882.1338 | 1825.2378 | -1842.1632 | -1744.8716 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.56 | 3450.4129 | 3346.6402 | 3373.7182 | 3194.2133 | 1932.2312 | 1874.1185 | -1889.2822 | -1788.7594 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.57 | 3478.7642 | 3374.6664 | 3398.0488 | 3215.9327 | 1982.8956 | 1923.5598 | -1936.8878 | -1833.0816 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.58 | 3507.1155 | 3402.6925 | 3422.3794 | 3237.6521 | 2034.127 | 1973.5617 | -1984.9801 | -1877.8382 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.59 | 3535.4668 | 3430.7187 | 3446.7101 | 3259.3714 | 2085.9254 | 2024.124 | -2033.5589 | -1923.0291 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.6 | 3563.8182 | 3458.7448 | 3471.0407 | 3281.0908 | 2138.2909 | 2075.2469 | -2082.6244 | -1968.6545 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.61 | 3594.6572 | 3492.1485 | 3498.2025 | 3305.5673 | 2192.7409 | 2130.2106 | -2133.9035 | -2016.3961 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.62 | 3625.4963 | 3525.5522 | 3525.3642 | 3330.0439 | 2247.8077 | 2185.8423 | -2185.7258 | -2064.6272 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.63 | 3656.3353 | 3558.9558 | 3552.526 | 3354.5204 | 2303.4913 | 2242.1422 | -2238.0914 | -2113.3478 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.64 | 3687.1744 | 3592.3595 | 3579.6878 | 3378.9969 | 2359.7916 | 2299.1101 | -2291.0002 | -2162.558 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.65 | 3718.0134 | 3625.7632 | 3606.8495 | 3403.4734 | 2416.7087 | 2356.7461 | -2344.4522 | -2212.2577 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.66 | 3748.8525 | 3659.1669 | 3634.0113 | 3427.9499 | 2474.2426 | 2415.0502 | -2398.4475 | -2262.4469 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.67 | 3779.6915 | 3692.5706 | 3661.1731 | 3452.4264 | 2532.3933 | 2474.0223 | -2452.986 | -2313.1257 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.68 | 3810.5306 | 3725.9743 | 3688.3348 | 3476.9029 | 2591.1608 | 2533.6625 | -2508.0677 | -2364.294 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.69 | 3841.3696 | 3759.378 | 3715.4966 | 3501.3795 | 2650.545 | 2593.9708 | -2563.6927 | -2415.9518 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0026
0.7 | 3872.2087 | 3792.7816 | 3742.6584 | 3525.856 | 2710.5461 | 2654.9471 | -2619.8609 | -2468.0992 | 2520.0034 | -2520.0026 | 2520.0033 | -2517.9648
0.71 | 3904.9878 | 3829.5345 | 3759.6485 | 3530.8053 | 2772.5413 | 2718.9695 | -2669.3504 | -2506.8718 | 2520.0034 | -2520.0026 | 2520.0033 | -2486.399
0.72 | 3937.7669 | 3866.2874 | 3776.6386 | 3535.7546 | 2835.1922 | 2783.727 | -2719.1798 | -2545.7433 | 2520.0034 | -2520.0026 | 2520.0033 | -2453.722
0.73 | 3970.5461 | 3903.0404 | 3793.6287 | 3540.704 | 2898.4986 | 2849.2195 | -2769.349 | -2584.7139 | 2520.0034 | -2520.0026 | 2520.0033 | -2419.884
0.74 | 4003.3252 | 3939.7933 | 3810.6189 | 3545.6533 | 2962.4607 | 2915.447 | -2819.858 | -2623.7835 | 2520.0034 | -2520.0026 | 2520.0033 | -2384.8308
0.75 | 4036.1043 | 3976.5462 | 3827.609 | 3550.6026 | 3027.0783 | 2982.4096 | -2870.7067 | -2662.952 | 2520.0034 | -2520.0026 | 2520.0033 | -2348.5029
0.76 | 4068.8835 | 4013.2991 | 3844.5991 | 3555.552 | 3092.3514 | 3050.1073 | -2921.8953 | -2702.2195 | 2520.0034 | -2520.0026 | 2498.6937 | -2310.8353
0.77 | 4101.6626 | 4050.052 | 3861.5892 | 3560.5013 | 3158.2802 | 3118.54 | -2973.4237 | -2741.586 | 2520.0034 | -2520.0026 | 2463.8634 | -2271.7561
0.78 | 4134.4417 | 4086.8049 | 3878.5794 | 3565.4506 | 3224.8646 | 3187.7078 | -3025.2919 | -2781.0515 | 2520.0034 | -2520.0026 | 2427.1355 | -2231.186
0.79 | 4167.2209 | 4123.5578 | 3895.5695 | 3570.4 | 3292.1045 | 3257.6107 | -3077.4999 | -2820.616 | 2520.0034 | -2520.0026 | 2388.4003 | -2189.0367
0.8 | 4200 | 4160.3107 | 3904.8264 | 3575.3493 | 3360 | 3328.2486 | -3123.8612 | -2860.2795 | 2520 | -2496.1864 | 2342.8959 | -2145.2096
0.81 | 4200 | 4164.2796 | 3900.8546 | 3580.7193 | 3402 | 3373.0665 | -3159.6922 | -2900.3827 | 2463.0055 | -2442.058 | 2287.5777 | -2099.8408
0.82 | 4200 | 4168.2486 | 3896.8828 | 3586.0893 | 3444 | 3417.9638 | -3195.4439 | -2940.5933 | 2403.9268 | -2385.7534 | 2230.4336 | -2052.5467
0.83 | 4200 | 4172.2175 | 3892.911 | 3591.4593 | 3486 | 3462.9405 | -3231.1161 | -2980.9113 | 2342.6062 | -2327.1102 | 2171.3232 | -2003.1845
0.84 | 4200 | 4176.1864 | 3888.9391 | 3596.8293 | 3528 | 3507.9966 | -3266.7089 | -3021.3366 | 2278.8629 | -2265.9419 | 2110.0855 | -1951.5907
0.85 | 4200 | 4180.1553 | 3884.9673 | 3602.1994 | 3570 | 3553.132 | -3302.2222 | -3061.8694 | 2212.4873 | -2202.0335 | 2046.5335 | -1897.5763
0.86 | 4200 | 4184.1243 | 3880.9955 | 3607.5694 | 3612 | 3598.3469 | -3337.6561 | -3102.5096 | 2143.2349 | -2135.1337 | 1980.4488 | -1840.9211
0.87 | 4200 | 4188.0932 | 3877.0237 | 3612.9394 | 3654 | 3643.6411 | -3373.0106 | -3143.2572 | 2070.8172 | -2064.9466 | 1911.5732 | -1781.366
0.88 | 4200 | 4192.0621 | 3873.0518 | 3618.3094 | 3696 | 3689.0147 | -3408.2856 | -3184.1122 | 1994.8895 | -1991.1192 | 1839.5977 | -1718.6017
0.89 | 4200 | 4196.0311 | 3869.08 | 3623.6794 | 3738 | 3734.4677 | -3443.4812 | -3225.0746 | 1915.0342 | -1913.2245 | 1764.1478 | -1652.2548
0.9 | 4200 | 4200 | 3865.1082 | 3629.0494 | 3780 | 3780 | -3478.5974 | -3266.1444 | 1830.7376 | -1830.7376 | 1684.7616 | -1581.866
0.91 | 4200 | 4200 | 3856.8317 | 3638.5913 | 3822 | 3822 | -3509.7168 | -3311.118 | 1741.3546 | -1741.3546 | 1599.0742 | -1508.59
0.92 | 4200 | 4200 | 3848.5552 | 3648.1331 | 3864 | 3864 | -3540.6708 | -3356.2825 | 1646.0571 | -1646.0571 | 1508.3194 | -1429.7704
0.93 | 4200 | 4200 | 3840.2787 | 3657.675 | 3906 | 3906 | -3571.4592 | -3401.6378 | 1543.75 | -1543.75 | 1411.531 | -1344.4133
0.94 | 4200 | 4200 | 3832.0022 | 3667.2169 | 3948 | 3948 | -3602.082 | -3447.1839 | 1432.9327 | -1432.9327 | 1307.3812 | -1251.1607
0.95 | 4200 | 4200 | 3823.7257 | 3676.7588 | 3990 | 3990 | -3632.5394 | -3492.9208 | 1311.4496 | -1311.4496 | 1193.958 | -1148.0676
0.96 | 4200 | 4200 | 3812.9697 | 3695.207 | 4032 | 4032 | -3660.451 | -3547.3987 | 1176 | -1176 | 1067.6315 | -1034.658
0.97 | 4200 | 4200 | 3802.2138 | 3713.6553 | 4074 | 4074 | -3688.1474 | -3602.2456 | 1021.0406 | -1021.0406 | 924.3369 | -902.8078
0.98 | 4200 | 4200 | 3791.4579 | 3732.1035 | 4116 | 4116 | -3715.6287 | -3657.4614 | 835.7894 | -835.7894 | 754.4906 | -742.6792
0.99 | 4200 | 4200 | 3780.545 | 3750.5518 | 4158 | 4158 | -3742.7396 | -3713.0462 | 592.4829 | -592.4829 | 533.3115 | -529.0804
1 | 4200 | 4200 | 3769 | 3769 | 4200 | 4200 | -3769 | -3769 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_35C_0.9pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 35 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1490 |  | VDC
Nom. Battery Voltage** |  |  |  | 1291.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1159 |  | VDC |  | Please select:
AC Voltage |  |  |  | 0.9 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @35°C, 1159Vdc min. battery voltage and 0.9pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2268.0025 | 2268.002 | 2268.0022 | 2268.0017 | 0 | 0 | 0 | 0 | 2268.0025 | -2268.002 | 2268.0022 | -2268.0017
0.01 | 2268.0025 | 2268.002 | 2268.0022 | 2268.0017 | 0.02268 | 0.02268 | -0.02268 | -0.02268 | 2268.0025 | -2268.002 | 2268.0022 | -2268.0017
0.05 | 2280.3954 | 2277.9187 | 2278.7603 | 2276.5088 | 114.0198 | 113.8959 | -113.938 | -113.8254 | 2268.0025 | -2268.002 | 2268.0022 | -2268.002
0.1 | 2292.7908 | 2287.8374 | 2289.5207 | 2285.0176 | 229.2791 | 228.7837 | -228.9521 | -228.5018 | 2268.0025 | -2268.002 | 2268.0022 | -2268.002
0.15 | 2329.6071 | 2317.9707 | 2320.6829 | 2309.1909 | 349.4411 | 347.6956 | -348.1024 | -346.3786 | 2268.0025 | -2268.002 | 2268.0022 | -2268.002
0.2 | 2366.4234 | 2348.104 | 2351.8451 | 2333.3641 | 473.2847 | 469.6208 | -470.369 | -466.6728 | 2268.0025 | -2268.002 | 2268.0022 | -2268.002
0.25 | 2426.4426 | 2398.5313 | 2401.3577 | 2371.6299 | 606.6106 | 599.6328 | -600.3394 | -592.9075 | 2268.0025 | -2268.002 | 2268.0022 | -2268.002
0.3 | 2486.4617 | 2448.9587 | 2450.8703 | 2409.8958 | 745.9385 | 734.6876 | -735.2611 | -722.9687 | 2268.0025 | -2268.002 | 2268.0022 | -2268.002
0.35 | 2568.3511 | 2519.2033 | 2515.6859 | 2460.6934 | 898.9229 | 881.7211 | -880.4901 | -861.2427 | 2268.0025 | -2268.002 | 2268.0022 | -2268.002
0.4 | 2650.2404 | 2589.4478 | 2580.5014 | 2511.4911 | 1060.0962 | 1035.7791 | -1032.2006 | -1004.5964 | 2268.0025 | -2268.002 | 2268.0022 | -2268.002
0.45 | 2747.9412 | 2678.8616 | 2657.8022 | 2560.4112 | 1236.5735 | 1205.4877 | -1196.011 | -1152.1851 | 2268.0025 | -2268.002 | 2268.0022 | -2268.002
0.5 | 2845.6419 | 2768.2753 | 2735.103 | 2609.3314 | 1422.821 | 1384.1377 | -1367.5515 | -1304.6657 | 2268.0025 | -2268.002 | 2268.0022 | -2259.7473
0.51 | 2868.3004 | 2789.6763 | 2752.2885 | 2615.8201 | 1462.8332 | 1422.7349 | -1403.6671 | -1334.0683 | 2268.0025 | -2268.002 | 2268.0022 | -2250.0615
0.52 | 2890.9589 | 2811.0773 | 2769.474 | 2622.3088 | 1503.2986 | 1461.7602 | -1440.1265 | -1363.6006 | 2268.0025 | -2268.002 | 2268.0022 | -2239.8877
0.53 | 2913.6173 | 2832.4784 | 2786.6595 | 2628.7975 | 1544.2172 | 1501.2135 | -1476.9295 | -1393.2627 | 2268.0025 | -2268.002 | 2268.0022 | -2229.2141
0.54 | 2936.2758 | 2853.8794 | 2803.845 | 2635.2862 | 1585.5889 | 1541.0949 | -1514.0763 | -1423.0546 | 2268.0025 | -2268.002 | 2268.0022 | -2218.0282
0.55 | 2958.9342 | 2875.2804 | 2821.0304 | 2641.7749 | 1627.4138 | 1581.4042 | -1551.5667 | -1452.9762 | 2268.0025 | -2268.002 | 2268.0022 | -2206.317
0.56 | 2981.5927 | 2896.6814 | 2838.2159 | 2648.2636 | 1669.6919 | 1622.1416 | -1589.4009 | -1483.0276 | 2268.0025 | -2268.002 | 2268.0022 | -2194.0668
0.57 | 3004.2511 | 2918.0825 | 2855.4014 | 2654.7523 | 1712.4232 | 1663.307 | -1627.5788 | -1513.2088 | 2268.0025 | -2268.002 | 2268.0022 | -2181.2632
0.58 | 3026.9096 | 2939.4835 | 2872.5869 | 2661.241 | 1755.6076 | 1704.9004 | -1666.1004 | -1543.5198 | 2268.0025 | -2268.002 | 2268.0022 | -2167.8908
0.59 | 3049.5681 | 2960.8845 | 2889.7724 | 2667.7297 | 1799.2452 | 1746.9219 | -1704.9657 | -1573.9605 | 2268.0025 | -2268.002 | 2268.0022 | -2153.9336
0.6 | 3072.2265 | 2982.2855 | 2906.9579 | 2674.2184 | 1843.3359 | 1789.3713 | -1744.1747 | -1604.5311 | 2268.0025 | -2268.002 | 2268.0022 | -2139.3747
0.61 | 3097.4583 | 3007.8223 | 2915.7025 | 2677.4466 | 1889.4496 | 1834.7716 | -1778.5785 | -1633.2424 | 2268.0025 | -2268.002 | 2268.0022 | -2121.6125
0.62 | 3122.6901 | 3033.359 | 2924.4471 | 2680.6748 | 1936.0679 | 1880.6826 | -1813.1572 | -1662.0184 | 2268.0025 | -2268.002 | 2268.0022 | -2103.2623
0.63 | 3147.9219 | 3058.8958 | 2933.1918 | 2683.903 | 1983.1908 | 1927.1044 | -1847.9108 | -1690.8589 | 2268.0025 | -2268.002 | 2268.0022 | -2084.306
0.64 | 3173.1537 | 3084.4326 | 2941.9364 | 2687.1312 | 2030.8184 | 1974.0368 | -1882.8393 | -1719.764 | 2268.0025 | -2268.002 | 2260.5101 | -2064.7242
0.65 | 3198.3855 | 3109.9693 | 2950.6811 | 2690.3594 | 2078.9506 | 2021.4801 | -1917.9427 | -1748.7336 | 2268.0025 | -2268.002 | 2242.3235 | -2044.4962
0.66 | 3223.6174 | 3135.5061 | 2959.4257 | 2693.5876 | 2127.5875 | 2069.434 | -1953.221 | -1777.7678 | 2268.0025 | -2268.002 | 2223.3147 | -2023.5997
0.67 | 3248.8492 | 3161.0428 | 2968.1704 | 2696.8158 | 2176.7289 | 2117.8987 | -1988.6741 | -1806.8666 | 2268.0025 | -2268.002 | 2203.4542 | -2002.0112
0.68 | 3274.081 | 3186.5796 | 2976.915 | 2700.044 | 2226.3751 | 2166.8741 | -2024.3022 | -1836.0299 | 2268.0025 | -2268.002 | 2182.7101 | -1979.705
0.69 | 3299.3128 | 3212.1163 | 2985.6597 | 2703.2722 | 2276.5258 | 2216.3603 | -2060.1052 | -1865.2578 | 2268.0025 | -2268.002 | 2161.0484 | -1956.6538
0.7 | 3324.5446 | 3237.6531 | 2994.4043 | 2706.5004 | 2327.1812 | 2266.3572 | -2096.083 | -1894.5503 | 2268.0025 | -2268.002 | 2138.4324 | -1932.8279
0.71 | 3341.3867 | 3252.4317 | 2992.0192 | 2709.4395 | 2372.3846 | 2309.2265 | -2124.3336 | -1923.7021 | 2268.0025 | -2268.002 | 2106.9849 | -1907.9919
0.72 | 3358.2288 | 3267.2104 | 2989.634 | 2712.3786 | 2417.9248 | 2352.3915 | -2152.5365 | -1952.9126 | 2268.0025 | -2267.3593 | 2074.7285 | -1882.3204
0.73 | 3375.071 | 3281.989 | 2987.2489 | 2715.3177 | 2463.8018 | 2395.852 | -2180.6917 | -1982.182 | 2268.0025 | -2243.066 | 2041.6267 | -1855.7762
0.74 | 3391.9131 | 3296.7676 | 2984.8638 | 2718.2569 | 2510.0157 | 2439.6081 | -2208.7992 | -2011.5101 | 2268.0025 | -2217.4286 | 2007.6399 | -1828.3182
0.75 | 3408.7552 | 3311.5463 | 2982.4787 | 2721.196 | 2556.5664 | 2483.6597 | -2236.859 | -2040.897 | 2254.6796 | -2190.382 | 1972.7242 | -1799.9019
0.76 | 3425.5973 | 3326.3249 | 2980.0935 | 2724.1351 | 2603.454 | 2528.0069 | -2264.8711 | -2070.3427 | 2226.3747 | -2161.8553 | 1936.8315 | -1770.4782
0.77 | 3442.4394 | 3341.1035 | 2977.7084 | 2727.0742 | 2650.6784 | 2572.6497 | -2292.8355 | -2099.8471 | 2196.4274 | -2131.7707 | 1899.9086 | -1739.993
0.78 | 3459.2816 | 3355.8822 | 2975.3233 | 2730.0133 | 2698.2396 | 2617.5881 | -2320.7521 | -2129.4104 | 2164.7475 | -2100.0423 | 1861.8963 | -1708.3864
0.79 | 3476.1237 | 3370.6608 | 2972.9381 | 2732.9524 | 2746.1377 | 2662.822 | -2348.6211 | -2159.0324 | 2131.2352 | -2066.5752 | 1822.7287 | -1675.5918
0.8 | 3492.9658 | 3385.4394 | 2970.553 | 2735.8915 | 2794.3727 | 2708.3516 | -2376.4424 | -2188.7132 | 2095.7795 | -2031.2637 | 1782.3318 | -1641.5349
0.81 | 3496.5008 | 3394.3462 | 2967.6462 | 2740.5802 | 2832.1656 | 2749.4204 | -2403.7934 | -2219.87 | 2050.4525 | -1990.546 | 1740.3164 | -1607.1581
0.82 | 3500.0358 | 3403.2529 | 2964.7393 | 2745.2689 | 2870.0293 | 2790.6673 | -2431.0863 | -2251.1205 | 2003.2928 | -1947.8978 | 1696.9086 | -1571.2918
0.83 | 3503.5707 | 3412.1596 | 2961.8325 | 2749.9576 | 2907.9637 | 2832.0924 | -2458.321 | -2282.4648 | 1954.1635 | -1903.1777 | 1652.0017 | -1533.8257
0.84 | 3507.1057 | 3421.0663 | 2958.9257 | 2754.6463 | 2945.9688 | 2873.6957 | -2485.4976 | -2313.9029 | 1902.9079 | -1856.224 | 1605.4728 | -1494.6336
0.85 | 3510.6407 | 3429.973 | 2956.0188 | 2759.335 | 2984.0446 | 2915.477 | -2512.616 | -2345.4348 | 1849.3447 | -1806.8504 | 1557.1796 | -1453.5699
0.86 | 3514.1757 | 3438.8797 | 2953.112 | 2764.0237 | 3022.1911 | 2957.4365 | -2539.6763 | -2377.0604 | 1793.2629 | -1754.8398 | 1506.9554 | -1410.4648
0.87 | 3517.7107 | 3447.7864 | 2950.2052 | 2768.7124 | 3060.4083 | 2999.5742 | -2566.6785 | -2408.7798 | 1734.4133 | -1699.937 | 1454.6037 | -1365.1184
0.88 | 3521.2456 | 3456.6931 | 2947.2983 | 2773.4011 | 3098.6962 | 3041.8899 | -2593.6225 | -2440.593 | 1672.499 | -1641.8383 | 1399.8892 | -1317.2926
0.89 | 3524.7806 | 3465.5998 | 2944.3915 | 2778.0899 | 3137.0548 | 3084.3838 | -2620.5084 | -2472.5 | 1607.1608 | -1580.1767 | 1342.5263 | -1266.6993
0.9 | 3528.3156 | 3474.5065 | 2941.4847 | 2782.7786 | 3175.484 | 3127.0559 | -2647.3362 | -2504.5007 | 1537.9571 | -1514.5023 | 1282.1634 | -1212.9851
0.91 | 3531.647 | 3483.9868 | 2935.3257 | 2789.1351 | 3213.7988 | 3170.428 | -2671.1464 | -2538.113 | 1464.25 | -1444.4897 | 1217.0102 | -1156.3984
0.92 | 3534.9784 | 3493.4671 | 2929.1667 | 2795.4917 | 3252.1801 | 3213.9898 | -2694.8334 | -2571.8524 | 1385.4229 | -1369.1539 | 1147.9942 | -1095.6045
0.93 | 3538.3098 | 3502.9475 | 2923.0077 | 2801.8483 | 3290.6281 | 3257.7411 | -2718.3972 | -2605.7189 | 1300.5394 | -1287.5417 | 1074.3793 | -1029.846
0.94 | 3541.6412 | 3512.4278 | 2916.8488 | 2808.2049 | 3329.1427 | 3301.6821 | -2741.8378 | -2639.7126 | 1208.3174 | -1198.3506 | 995.1542 | -958.0877
0.95 | 3544.9725 | 3521.9081 | 2910.6898 | 2814.5615 | 3367.7239 | 3345.8127 | -2765.1553 | -2673.8334 | 1106.9173 | -1099.7154 | 908.8626 | -878.8465
0.96 | 3546.618 | 3528.1665 | 2902.6035 | 2825.7008 | 3404.7533 | 3387.0398 | -2786.4993 | -2712.6728 | 993.053 | -987.8866 | 812.729 | -791.1962
0.97 | 3548.2635 | 3534.4248 | 2894.5171 | 2836.8402 | 3441.8156 | 3428.3921 | -2807.6816 | -2751.735 | 862.6003 | -859.2361 | 703.6713 | -689.6498
0.98 | 3549.909 | 3540.6832 | 2886.4308 | 2847.9795 | 3478.9108 | 3469.8696 | -2828.7022 | -2791.0199 | 706.423 | -704.5871 | 574.3925 | -566.7408
0.99 | 3551.5545 | 3546.9416 | 2878.3445 | 2859.1188 | 3516.039 | 3511.4722 | -2849.561 | -2830.5276 | 501.0084 | -500.3577 | 406.0405 | -403.3283
1 | 3553.2 | 3553.2 | 2870.2582 | 2870.2582 | 3553.2 | 3553.2 | -2870.2582 | -2870.2582 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_35C_1.0pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 35 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1490 |  | VDC
Nom. Battery Voltage** |  |  |  | 1291.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1159 |  | VDC |  | Please select:
AC Voltage |  |  |  | 1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @35°C, 1159Vdc min. battery voltage and 1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2520.0028 | 2520.0022 | 2520.0024 | 2520.0019 | 0 | 0 | 0 | 0 | 2520.0028 | -2520.0022 | 2520.0024 | -2520.0019
0.01 | 2520.0028 | 2520.0022 | 2520.0024 | 2520.0019 | 0.0252 | 0.0252 | -0.0252 | -0.0252 | 2520.0028 | -2520.0022 | 2520.0024 | -2520.0019
0.05 | 2533.7727 | 2531.0208 | 2531.9559 | 2529.4542 | 126.6886 | 126.551 | -126.5978 | -126.4727 | 2520.0028 | -2520.0022 | 2520.0024 | -2520.0022
0.1 | 2547.5453 | 2542.0416 | 2543.9119 | 2538.9085 | 254.7545 | 254.2042 | -254.3912 | -253.8908 | 2520.0028 | -2520.0022 | 2520.0024 | -2520.0022
0.15 | 2588.4523 | 2575.523 | 2578.5365 | 2565.7676 | 388.2678 | 386.3284 | -386.7805 | -384.8651 | 2520.0028 | -2520.0022 | 2520.0024 | -2520.0022
0.2 | 2629.3593 | 2609.0044 | 2613.1612 | 2592.6268 | 525.8719 | 521.8009 | -522.6322 | -518.5254 | 2520.0028 | -2520.0022 | 2520.0024 | -2520.0022
0.25 | 2696.0473 | 2665.0348 | 2668.1752 | 2635.1444 | 674.0118 | 666.2587 | -667.0438 | -658.7861 | 2520.0028 | -2520.0022 | 2520.0024 | -2520.0022
0.3 | 2762.7353 | 2721.0652 | 2723.1893 | 2677.662 | 828.8206 | 816.3196 | -816.9568 | -803.2986 | 2520.0028 | -2520.0022 | 2520.0024 | -2520.0022
0.35 | 2853.7234 | 2799.1147 | 2795.2065 | 2734.1038 | 998.8032 | 979.6902 | -978.3223 | -956.9363 | 2520.0028 | -2520.0022 | 2520.0024 | -2520.0022
0.4 | 2944.7116 | 2877.1643 | 2867.2238 | 2790.5457 | 1177.8846 | 1150.8657 | -1146.8895 | -1116.2183 | 2520.0028 | -2520.0022 | 2520.0024 | -2520.0022
0.45 | 3053.268 | 2976.5129 | 2953.1136 | 2844.9014 | 1373.9706 | 1339.4308 | -1328.9011 | -1280.2056 | 2520.0028 | -2520.0022 | 2520.0024 | -2520.0022
0.5 | 3161.8244 | 3075.8614 | 3039.0034 | 2899.2571 | 1580.9122 | 1537.9307 | -1519.5017 | -1449.6286 | 2520.0028 | -2520.0022 | 2520.0024 | -2510.8303
0.51 | 3187.0004 | 3099.6404 | 3058.0984 | 2906.4668 | 1625.3702 | 1580.8166 | -1559.6302 | -1482.2981 | 2520.0028 | -2520.0022 | 2520.0024 | -2500.0683
0.52 | 3212.1765 | 3123.4193 | 3077.1933 | 2913.6765 | 1670.3318 | 1624.178 | -1600.1405 | -1515.1118 | 2520.0028 | -2520.0022 | 2520.0024 | -2488.7641
0.53 | 3237.3526 | 3147.1982 | 3096.2883 | 2920.8861 | 1715.7969 | 1668.015 | -1641.0328 | -1548.0696 | 2520.0028 | -2520.0022 | 2520.0024 | -2476.9045
0.54 | 3262.5286 | 3170.9771 | 3115.3833 | 2928.0958 | 1761.7655 | 1712.3276 | -1682.307 | -1581.1717 | 2520.0028 | -2520.0022 | 2520.0024 | -2464.4758
0.55 | 3287.7047 | 3194.756 | 3134.4783 | 2935.3055 | 1808.2376 | 1757.1158 | -1723.9631 | -1614.418 | 2520.0028 | -2520.0022 | 2520.0024 | -2451.4634
0.56 | 3312.8808 | 3218.5349 | 3153.5733 | 2942.5151 | 1855.2132 | 1802.3796 | -1766.001 | -1647.8085 | 2520.0028 | -2520.0022 | 2520.0024 | -2437.852
0.57 | 3338.0568 | 3242.3138 | 3172.6682 | 2949.7248 | 1902.6924 | 1848.1189 | -1808.4209 | -1681.3431 | 2520.0028 | -2520.0022 | 2520.0024 | -2423.6257
0.58 | 3363.2329 | 3266.0928 | 3191.7632 | 2956.9345 | 1950.6751 | 1894.3338 | -1851.2227 | -1715.022 | 2520.0028 | -2520.0022 | 2520.0024 | -2408.7675
0.59 | 3388.409 | 3289.8717 | 3210.8582 | 2964.1441 | 1999.1613 | 1941.0243 | -1894.4063 | -1748.845 | 2520.0028 | -2520.0022 | 2520.0024 | -2393.2596
0.6 | 3413.585 | 3313.6506 | 3229.9532 | 2971.3538 | 2048.151 | 1988.1904 | -1937.9719 | -1782.8123 | 2520.0028 | -2520.0022 | 2520.0024 | -2377.083
0.61 | 3441.6204 | 3342.0248 | 3239.6694 | 2974.9407 | 2099.3884 | 2038.6351 | -1976.1984 | -1814.7138 | 2520.0028 | -2520.0022 | 2520.0024 | -2357.3472
0.62 | 3469.6557 | 3370.3989 | 3249.3857 | 2978.5276 | 2151.1865 | 2089.6473 | -2014.6191 | -1846.6871 | 2520.0028 | -2520.0022 | 2520.0024 | -2336.9581
0.63 | 3497.691 | 3398.7731 | 3259.102 | 2982.1145 | 2203.5454 | 2141.2271 | -2053.2343 | -1878.7321 | 2520.0028 | -2520.0022 | 2520.0024 | -2315.8956
0.64 | 3525.7264 | 3427.1473 | 3268.8183 | 2985.7014 | 2256.4649 | 2193.3743 | -2092.0437 | -1910.8489 | 2520.0028 | -2520.0022 | 2511.6779 | -2294.138
0.65 | 3553.7617 | 3455.5215 | 3278.5345 | 2989.2883 | 2309.9451 | 2246.0889 | -2131.0474 | -1943.0374 | 2520.0028 | -2520.0022 | 2491.4705 | -2271.6624
0.66 | 3581.7971 | 3483.8956 | 3288.2508 | 2992.8751 | 2363.9861 | 2299.3711 | -2170.2455 | -1975.2976 | 2520.0028 | -2520.0022 | 2470.3497 | -2248.4441
0.67 | 3609.8324 | 3512.2698 | 3297.9671 | 2996.462 | 2418.5877 | 2353.2208 | -2209.6379 | -2007.6296 | 2520.0028 | -2520.0022 | 2448.2825 | -2224.4568
0.68 | 3637.8677 | 3540.644 | 3307.6834 | 3000.0489 | 2473.7501 | 2407.6379 | -2249.2247 | -2040.0333 | 2520.0028 | -2520.0022 | 2425.2335 | -2199.6722
0.69 | 3665.9031 | 3569.0182 | 3317.3996 | 3003.6358 | 2529.4731 | 2462.6225 | -2289.0057 | -2072.5087 | 2520.0028 | -2520.0022 | 2401.1649 | -2174.0597
0.7 | 3693.9384 | 3597.3923 | 3327.1159 | 3007.2227 | 2585.7569 | 2518.1746 | -2328.9811 | -2105.0559 | 2520.0028 | -2520.0022 | 2376.036 | -2147.5866
0.71 | 3712.6519 | 3613.813 | 3324.4658 | 3010.4884 | 2635.9828 | 2565.8073 | -2360.3707 | -2137.4467 | 2520.0028 | -2520.0022 | 2341.0944 | -2119.991
0.72 | 3731.3654 | 3630.2337 | 3321.8156 | 3013.754 | 2686.5831 | 2613.7683 | -2391.7072 | -2169.9029 | 2520.0028 | -2519.2881 | 2305.2539 | -2091.4671
0.73 | 3750.0788 | 3646.6544 | 3319.1655 | 3017.0197 | 2737.5576 | 2662.0577 | -2422.9908 | -2202.4244 | 2520.0028 | -2492.2956 | 2268.4742 | -2061.9735
0.74 | 3768.7923 | 3663.0752 | 3316.5153 | 3020.2854 | 2788.9063 | 2710.6756 | -2454.2213 | -2235.0112 | 2520.0028 | -2463.8095 | 2230.711 | -2031.4647
0.75 | 3787.5058 | 3679.4959 | 3313.8652 | 3023.5511 | 2840.6293 | 2759.6219 | -2485.3989 | -2267.6633 | 2505.1996 | -2433.7577 | 2191.9158 | -1999.8911
0.76 | 3806.2192 | 3695.9166 | 3311.215 | 3026.8167 | 2892.7266 | 2808.8966 | -2516.5234 | -2300.3807 | 2473.7497 | -2402.0614 | 2152.035 | -1967.198
0.77 | 3824.9327 | 3712.3373 | 3308.5649 | 3030.0824 | 2945.1982 | 2858.4997 | -2547.595 | -2333.1635 | 2440.4749 | -2368.6341 | 2111.0096 | -1933.3256
0.78 | 3843.6462 | 3728.758 | 3305.9147 | 3033.3481 | 2998.044 | 2908.4312 | -2578.6135 | -2366.0115 | 2405.275 | -2333.3804 | 2068.7737 | -1898.2071
0.79 | 3862.3597 | 3745.1787 | 3303.2646 | 3036.6138 | 3051.2641 | 2958.6912 | -2609.579 | -2398.9249 | 2368.0391 | -2296.1947 | 2025.2541 | -1861.7687
0.8 | 3881.0731 | 3761.5994 | 3300.6144 | 3039.8794 | 3104.8585 | 3009.2795 | -2640.4916 | -2431.9036 | 2328.6439 | -2256.9596 | 1980.3687 | -1823.9277
0.81 | 3885.0009 | 3771.4957 | 3297.3846 | 3045.0891 | 3146.8507 | 3054.9115 | -2670.8816 | -2466.5222 | 2278.2806 | -2211.7178 | 1933.6849 | -1785.7312
0.82 | 3888.9286 | 3781.3921 | 3294.1548 | 3050.2988 | 3188.9215 | 3100.7415 | -2701.207 | -2501.245 | 2225.8809 | -2164.3309 | 1885.4541 | -1745.8798
0.83 | 3892.8564 | 3791.2884 | 3290.925 | 3055.5085 | 3231.0708 | 3146.7694 | -2731.4678 | -2536.072 | 2171.2928 | -2114.6419 | 1835.5575 | -1704.2508
0.84 | 3896.7841 | 3801.1848 | 3287.6952 | 3060.7181 | 3273.2987 | 3192.9952 | -2761.664 | -2571.0032 | 2114.3421 | -2062.4711 | 1783.8587 | -1660.704
0.85 | 3900.7119 | 3811.0811 | 3284.4654 | 3065.9278 | 3315.6051 | 3239.4189 | -2791.7956 | -2606.0386 | 2054.8275 | -2007.6115 | 1730.1995 | -1615.0777
0.86 | 3904.6397 | 3820.9774 | 3281.2356 | 3071.1375 | 3357.9901 | 3286.0406 | -2821.8626 | -2641.1782 | 1992.5143 | -1949.822 | 1674.3949 | -1567.1831
0.87 | 3908.5674 | 3830.8738 | 3278.0058 | 3076.3472 | 3400.4536 | 3332.8602 | -2851.865 | -2676.422 | 1927.1259 | -1888.8189 | 1616.2264 | -1516.7983
0.88 | 3912.4952 | 3840.7701 | 3274.7759 | 3081.5568 | 3442.9957 | 3379.8777 | -2881.8028 | -2711.77 | 1858.3322 | -1824.2647 | 1555.4324 | -1463.6584
0.89 | 3916.4229 | 3850.6665 | 3271.5461 | 3086.7665 | 3485.6164 | 3427.0932 | -2911.6761 | -2747.2222 | 1785.7342 | -1755.7519 | 1491.6959 | -1407.4437
0.9 | 3920.3507 | 3860.5628 | 3268.3163 | 3091.9762 | 3528.3156 | 3474.5065 | -2941.4847 | -2782.7786 | 1708.8412 | -1682.7803 | 1424.6261 | -1347.7612
0.91 | 3924.0522 | 3871.0965 | 3261.473 | 3099.0391 | 3570.8875 | 3522.6978 | -2967.9404 | -2820.1255 | 1626.9444 | -1604.9885 | 1352.2336 | -1284.8872
0.92 | 3927.7538 | 3881.6302 | 3254.6297 | 3106.1019 | 3613.5335 | 3571.0997 | -2994.2593 | -2857.6138 | 1539.3588 | -1521.2821 | 1275.5491 | -1217.3384
0.93 | 3931.4553 | 3892.1638 | 3247.7864 | 3113.1648 | 3656.2534 | 3619.7124 | -3020.4413 | -2895.2433 | 1445.0438 | -1430.6019 | 1193.7548 | -1144.2734
0.94 | 3935.1568 | 3902.6975 | 3240.9431 | 3120.2277 | 3699.0474 | 3668.5357 | -3046.4865 | -2933.014 | 1342.5749 | -1331.5006 | 1105.7269 | -1064.5419
0.95 | 3938.8584 | 3913.2312 | 3234.0998 | 3127.2905 | 3741.9155 | 3717.5696 | -3072.3948 | -2970.926 | 1229.9081 | -1221.9061 | 1009.8473 | -976.4962
0.96 | 3940.6867 | 3920.185 | 3225.1149 | 3139.6676 | 3783.0592 | 3763.3776 | -3096.1104 | -3014.0809 | 1103.3923 | -1097.6518 | 903.0322 | -879.1069
0.97 | 3942.515 | 3927.1387 | 3216.1301 | 3152.0446 | 3824.2396 | 3809.3246 | -3119.6462 | -3057.4833 | 958.4448 | -954.7067 | 781.857 | -766.2775
0.98 | 3944.3434 | 3934.0925 | 3207.1453 | 3164.4217 | 3865.4565 | 3855.4106 | -3143.0024 | -3101.1332 | 784.9144 | -782.8745 | 638.2139 | -629.712
0.99 | 3946.1717 | 3941.0462 | 3198.1605 | 3176.7987 | 3906.71 | 3901.6358 | -3166.1789 | -3145.0307 | 556.676 | -555.953 | 451.1561 | -448.1426
1 | 3948 | 3948 | 3189.1757 | 3189.1757 | 3948 | 3948 | -3189.1757 | -3189.1757 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_35C_1.1pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 35 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1490 |  | VDC
Nom. Battery Voltage** |  |  |  | 1291.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1159 |  | VDC |  | Please select:
AC Voltage |  |  |  | 1.1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @35°C, 1159Vdc min. battery voltage and 1.1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2520.003 | 2520.0023 | 2520.0029 | 2520.0022 | 0 | 0 | 0 | 0 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0022
0.01 | 2520.003 | 2520.0023 | 2520.0029 | 2520.0022 | 0.0252 | 0.0252 | -0.0252 | -0.0252 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0022
0.05 | 2534.8892 | 2531.6417 | 2534.6203 | 2531.1504 | 126.7445 | 126.5821 | -126.731 | -126.5575 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.1 | 2549.7784 | 2543.2833 | 2549.2407 | 2542.3009 | 254.9778 | 254.3283 | -254.9241 | -254.2301 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.15 | 2594.2669 | 2578.573 | 2591.7118 | 2574.2977 | 389.14 | 386.7859 | -388.7568 | -386.1447 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.2 | 2638.7555 | 2613.8626 | 2634.1829 | 2606.2945 | 527.7511 | 522.7725 | -526.8366 | -521.2589 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.25 | 2709.7023 | 2673.4337 | 2700.8214 | 2657.0648 | 677.4256 | 668.3584 | -675.2054 | -664.2662 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.3 | 2780.6492 | 2733.0049 | 2767.46 | 2707.8352 | 834.1948 | 819.9015 | -830.238 | -812.3506 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.35 | 2875.1122 | 2815.3261 | 2853.3735 | 2773.9995 | 1006.2893 | 985.3641 | -998.6807 | -970.8998 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.4 | 2969.5752 | 2897.6473 | 2939.287 | 2840.1637 | 1187.8301 | 1159.0589 | -1175.7148 | -1136.0655 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.45 | 3082.6192 | 3001.8228 | 3040.9395 | 2920.0913 | 1387.1786 | 1350.8203 | -1368.4228 | -1314.0411 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.5 | 3195.6631 | 3105.9984 | 3142.592 | 3000.0189 | 1597.8315 | 1552.9992 | -1571.296 | -1500.0094 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.51 | 3221.5112 | 3130.9812 | 3164.942 | 3019.5431 | 1642.9707 | 1596.8004 | -1614.1204 | -1539.967 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.52 | 3247.3594 | 3155.9641 | 3187.2921 | 3039.0673 | 1688.6269 | 1641.1013 | -1657.3919 | -1580.315 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.53 | 3273.2076 | 3180.9469 | 3209.6421 | 3058.5916 | 1734.8 | 1685.9019 | -1701.1103 | -1621.0535 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.54 | 3299.0558 | 3205.9297 | 3231.9922 | 3078.1158 | 1781.4901 | 1731.2021 | -1745.2758 | -1662.1825 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.55 | 3324.9039 | 3230.9126 | 3254.3423 | 3097.6401 | 1828.6972 | 1777.0019 | -1789.8882 | -1703.702 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.56 | 3350.7521 | 3255.8954 | 3276.6923 | 3117.1643 | 1876.4212 | 1823.3014 | -1834.9477 | -1745.612 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.57 | 3376.6003 | 3280.8783 | 3299.0424 | 3136.6885 | 1924.6621 | 1870.1006 | -1880.4542 | -1787.9125 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.58 | 3402.4484 | 3305.8611 | 3321.3925 | 3156.2128 | 1973.4201 | 1917.3994 | -1926.4076 | -1830.6034 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.59 | 3428.2966 | 3330.8439 | 3343.7425 | 3175.737 | 2022.695 | 1965.1979 | -1972.8081 | -1873.6848 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.6 | 3454.1448 | 3355.8268 | 3366.0926 | 3195.2613 | 2072.4869 | 2013.4961 | -2019.6555 | -1917.1568 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.61 | 3482.827 | 3385.4275 | 3390.488 | 3205.4109 | 2124.5244 | 2065.1108 | -2068.1977 | -1955.3006 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.62 | 3511.5091 | 3415.0282 | 3414.8834 | 3215.5605 | 2177.1357 | 2117.3175 | -2117.2277 | -1993.6475 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.63 | 3540.1913 | 3444.6289 | 3439.2788 | 3225.7101 | 2230.3205 | 2170.1162 | -2166.7456 | -2032.1974 | 2520.003 | -2520.0023 | 2520.0029 | -2505.0708
0.64 | 3568.8735 | 3474.2296 | 3463.6741 | 3235.8598 | 2284.079 | 2223.5069 | -2216.7515 | -2070.9503 | 2520.003 | -2520.0023 | 2520.0029 | -2486.3535
0.65 | 3597.5557 | 3503.8303 | 3488.0695 | 3246.0094 | 2338.4112 | 2277.4897 | -2267.2452 | -2109.9061 | 2520.003 | -2520.0023 | 2520.0029 | -2466.7536
0.66 | 3626.2379 | 3533.431 | 3512.4649 | 3256.159 | 2393.317 | 2332.0644 | -2318.2269 | -2149.065 | 2520.003 | -2520.0023 | 2520.0029 | -2446.2403
0.67 | 3654.9201 | 3563.0317 | 3536.8603 | 3266.3087 | 2448.7964 | 2387.2312 | -2369.6964 | -2188.4268 | 2520.003 | -2520.0023 | 2520.0029 | -2424.7805
0.68 | 3683.6022 | 3592.6324 | 3561.2557 | 3276.4583 | 2504.8495 | 2442.99 | -2421.6539 | -2227.9916 | 2520.003 | -2520.0023 | 2520.0029 | -2402.3389
0.69 | 3712.2844 | 3622.2331 | 3585.6511 | 3286.6079 | 2561.4763 | 2499.3408 | -2474.0993 | -2267.7595 | 2520.003 | -2520.0023 | 2520.0029 | -2378.8776
0.7 | 3740.9666 | 3651.8338 | 3610.0465 | 3296.7576 | 2618.6766 | 2556.2836 | -2527.0325 | -2307.7303 | 2520.003 | -2520.0023 | 2520.0029 | -2354.3558
0.71 | 3761.67 | 3674.4868 | 3614.4749 | 3300.6396 | 2670.7857 | 2608.8857 | -2566.2772 | -2343.4541 | 2520.003 | -2520.0023 | 2520.0029 | -2324.316
0.72 | 3782.3733 | 3697.1399 | 3618.9033 | 3304.5217 | 2723.3088 | 2661.9407 | -2605.6104 | -2379.2556 | 2520.003 | -2520.0023 | 2511.425 | -2293.2524
0.73 | 3803.0766 | 3719.793 | 3623.3317 | 3308.4038 | 2776.2459 | 2715.4489 | -2645.0321 | -2415.1348 | 2520.003 | -2520.0023 | 2476.3557 | -2261.1191
0.74 | 3823.78 | 3742.446 | 3627.7601 | 3312.2859 | 2829.5972 | 2769.4101 | -2684.5425 | -2451.0916 | 2520.003 | -2517.1949 | 2440.0564 | -2227.8662
0.75 | 3844.4833 | 3765.0991 | 3632.1885 | 3316.168 | 2883.3625 | 2823.8243 | -2724.1414 | -2487.126 | 2520.003 | -2490.379 | 2402.4669 | -2193.4389
0.76 | 3865.1866 | 3787.7522 | 3636.6169 | 3320.0501 | 2937.5419 | 2878.6916 | -2763.8288 | -2523.238 | 2512.074 | -2461.7475 | 2363.5212 | -2157.7771
0.77 | 3885.89 | 3810.4052 | 3639.4214 | 3323.9321 | 2992.1353 | 2934.012 | -2802.3545 | -2559.4278 | 2479.3683 | -2431.2058 | 2322.1106 | -2120.8146
0.78 | 3906.5933 | 3833.0583 | 3636.5062 | 3327.8142 | 3047.1428 | 2989.7855 | -2836.4748 | -2595.6951 | 2444.6661 | -2398.6494 | 2275.6511 | -2082.478
0.79 | 3927.2967 | 3855.7114 | 3633.591 | 3331.6963 | 3102.5644 | 3046.012 | -2870.5369 | -2632.0401 | 2407.8525 | -2363.963 | 2227.7795 | -2042.6858
0.8 | 3948 | 3878.3644 | 3630.6759 | 3335.5784 | 3158.4 | 3102.6915 | -2904.5407 | -2668.4627 | 2368.8 | -2327.0187 | 2178.4055 | -2001.347
0.81 | 3948 | 3885.328 | 3627.1231 | 3341.2267 | 3197.88 | 3147.1157 | -2937.9697 | -2706.3936 | 2315.2252 | -2278.4724 | 2127.0533 | -1959.3951
0.82 | 3948 | 3892.2915 | 3623.5703 | 3346.8749 | 3237.36 | 3191.6791 | -2971.3276 | -2744.4374 | 2259.6912 | -2227.8057 | 2073.9995 | -1915.6291
0.83 | 3948 | 3899.2551 | 3620.0175 | 3352.5232 | 3276.84 | 3236.3817 | -3004.6145 | -2782.5942 | 2202.0499 | -2174.8617 | 2019.1132 | -1869.9147
0.84 | 3948 | 3906.2187 | 3616.4647 | 3358.1714 | 3316.32 | 3281.2237 | -3037.8304 | -2820.864 | 2142.1311 | -2119.4611 | 1962.2446 | -1822.0981
0.85 | 3948 | 3913.1822 | 3612.9119 | 3363.8197 | 3355.8 | 3326.2049 | -3070.9751 | -2859.2467 | 2079.7381 | -2061.3966 | 1903.2195 | -1772.002
0.86 | 3948 | 3920.1458 | 3609.3591 | 3369.4679 | 3395.28 | 3371.3254 | -3104.0488 | -2897.7424 | 2014.6408 | -2000.427 | 1841.8344 | -1719.4194
0.87 | 3948 | 3927.1093 | 3605.8063 | 3375.1162 | 3434.76 | 3416.5851 | -3137.0515 | -2936.3511 | 1946.5682 | -1936.268 | 1777.849 | -1664.1068
0.88 | 3948 | 3934.0729 | 3602.2535 | 3380.7644 | 3474.24 | 3461.9841 | -3169.9831 | -2975.0727 | 1875.1961 | -1868.5811 | 1710.9756 | -1605.7741
0.89 | 3948 | 3941.0364 | 3598.7007 | 3386.4127 | 3513.72 | 3507.5224 | -3202.8437 | -3013.9073 | 1800.1322 | -1796.957 | 1640.8655 | -1544.0705
0.9 | 3948 | 3948 | 3595.1479 | 3392.0609 | 3553.2 | 3553.2 | -3235.6332 | -3052.8548 | 1720.8933 | -1720.8933 | 1567.0887 | -1478.5651
0.91 | 3948 | 3948 | 3587.6203 | 3401.425 | 3592.68 | 3592.68 | -3264.7345 | -3095.2967 | 1636.8734 | -1636.8734 | 1487.457 | -1410.2589
0.92 | 3948 | 3948 | 3580.0927 | 3410.789 | 3632.16 | 3632.16 | -3293.6852 | -3137.9259 | 1547.2937 | -1547.2937 | 1403.104 | -1336.7508
0.93 | 3948 | 3948 | 3572.565 | 3420.1531 | 3671.64 | 3671.64 | -3322.4855 | -3180.7424 | 1451.125 | -1451.125 | 1313.1303 | -1257.1098
0.94 | 3948 | 3948 | 3565.0374 | 3429.5172 | 3711.12 | 3711.12 | -3351.1351 | -3223.7462 | 1346.9567 | -1346.9567 | 1216.2996 | -1170.0636
0.95 | 3948 | 3948 | 3557.5097 | 3438.8813 | 3750.6 | 3750.6 | -3379.6342 | -3266.9372 | 1232.7626 | -1232.7626 | 1110.8321 | -1073.7903
0.96 | 3948 | 3948 | 3547.6264 | 3453.6343 | 3790.08 | 3790.08 | -3405.7214 | -3315.489 | 1105.44 | -1105.44 | 993.3354 | -967.0176
0.97 | 3948 | 3948 | 3537.7432 | 3467.2491 | 3829.56 | 3829.56 | -3431.6109 | -3363.2316 | 959.7782 | -959.7782 | 860.0428 | -842.9053
0.98 | 3948 | 3948 | 3527.8599 | 3480.8638 | 3869.04 | 3869.04 | -3457.3027 | -3411.2466 | 785.6421 | -785.6421 | 702.0353 | -692.6832
0.99 | 3948 | 3948 | 3517.9766 | 3494.4786 | 3908.52 | 3908.52 | -3482.7968 | -3459.5338 | 556.9339 | -556.9339 | 496.2717 | -492.9569
1 | 3948 | 3948 | 3508.0933 | 3508.0933 | 3948 | 3948 | -3508.0933 | -3508.0933 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_40C_0.9pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 40 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1490 |  | VDC
Nom. Battery Voltage** |  |  |  | 1291.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1159 |  | VDC |  | Please select:
AC Voltage |  |  |  | 0.9 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @40°C, 1159Vdc min. battery voltage and 0.9pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2268.0023 | 2268.0018 | 2268.002 | 2268.0016 | 0 | 0 | 0 | 0 | 2268.0023 | -2268.0018 | 2268.002 | -2268.0016
0.01 | 2268.0023 | 2268.0018 | 2268.002 | 2268.0016 | 0.02268 | 0.02268 | -0.02268 | -0.02268 | 2268.0023 | -2268.0018 | 2268.002 | -2268.0016
0.05 | 2279.4791 | 2277.1956 | 2277.9591 | 2275.848 | 113.974 | 113.8598 | -113.898 | -113.7924 | 2268.0023 | -2268.0018 | 2268.002 | -2268.0018
0.1 | 2290.9582 | 2286.3912 | 2287.9182 | 2283.696 | 229.0958 | 228.6391 | -228.7918 | -228.3696 | 2268.0023 | -2268.0018 | 2268.002 | -2268.0018
0.15 | 2325.1558 | 2314.3147 | 2316.8429 | 2306.0891 | 348.7734 | 347.1472 | -347.5264 | -345.9134 | 2268.0023 | -2268.0018 | 2268.002 | -2268.0018
0.2 | 2359.3534 | 2342.2383 | 2345.7675 | 2328.4821 | 471.8707 | 468.4477 | -469.1535 | -465.6964 | 2268.0023 | -2268.0018 | 2268.002 | -2268.0018
0.25 | 2414.8781 | 2389.2624 | 2391.9273 | 2363.9093 | 603.7195 | 597.3156 | -597.9818 | -590.9773 | 2268.0023 | -2268.0018 | 2268.002 | -2268.0018
0.3 | 2470.4028 | 2436.2866 | 2438.087 | 2399.3366 | 741.1209 | 730.886 | -731.4261 | -719.801 | 2268.0023 | -2268.0018 | 2268.002 | -2268.0018
0.35 | 2547.8189 | 2501.6877 | 2498.3736 | 2446.5119 | 891.7366 | 875.5907 | -874.4308 | -856.2791 | 2268.0023 | -2268.0018 | 2268.002 | -2268.0018
0.4 | 2625.2349 | 2567.0887 | 2558.6603 | 2493.6872 | 1050.094 | 1026.8355 | -1023.4641 | -997.4749 | 2268.0023 | -2268.0018 | 2268.002 | -2268.0018
0.45 | 2717.0596 | 2651.2072 | 2630.505 | 2532.2059 | 1222.6768 | 1193.0432 | -1183.7272 | -1139.4927 | 2268.0023 | -2268.0018 | 2268.002 | -2261.3322
0.5 | 2808.8844 | 2735.3257 | 2702.3497 | 2570.7247 | 1404.4422 | 1367.6628 | -1351.1749 | -1285.3623 | 2268.0023 | -2268.0018 | 2268.002 | -2226.3129
0.51 | 2830.3309 | 2755.4933 | 2718.5209 | 2572.0062 | 1443.4688 | 1405.3016 | -1386.4457 | -1311.7231 | 2268.0023 | -2268.0018 | 2268.002 | -2212.3739
0.52 | 2851.7775 | 2775.6609 | 2734.6921 | 2573.2876 | 1482.9243 | 1443.3437 | -1422.0399 | -1338.1096 | 2268.0023 | -2268.0018 | 2268.002 | -2198.0155
0.53 | 2873.2241 | 2795.8286 | 2750.8634 | 2574.5691 | 1522.8088 | 1481.7891 | -1457.9576 | -1364.5216 | 2268.0023 | -2268.0018 | 2268.002 | -2183.2285
0.54 | 2894.6706 | 2815.9962 | 2767.0346 | 2575.8506 | 1563.1221 | 1520.6379 | -1494.1987 | -1390.9593 | 2268.0023 | -2268.0018 | 2268.002 | -2168.0033
0.55 | 2916.1172 | 2836.1638 | 2783.2058 | 2577.1321 | 1603.8645 | 1559.8901 | -1530.7632 | -1417.4226 | 2268.0023 | -2268.0018 | 2268.002 | -2152.3296
0.56 | 2937.5638 | 2856.3314 | 2799.377 | 2578.4136 | 1645.0357 | 1599.5456 | -1567.6511 | -1443.9116 | 2268.0023 | -2268.0018 | 2268.002 | -2136.1966
0.57 | 2959.0103 | 2876.499 | 2815.5482 | 2579.695 | 1686.6359 | 1639.6044 | -1604.8625 | -1470.4262 | 2268.0023 | -2268.0018 | 2268.002 | -2119.5927
0.58 | 2980.4569 | 2896.6667 | 2831.7194 | 2580.9765 | 1728.665 | 1680.0667 | -1642.3973 | -1496.9664 | 2268.0023 | -2268.0018 | 2268.002 | -2102.506
0.59 | 3001.9035 | 2916.8343 | 2847.8907 | 2582.258 | 1771.1231 | 1720.9322 | -1680.2555 | -1523.5322 | 2268.0023 | -2268.0018 | 2268.002 | -2084.9235
0.6 | 3023.3501 | 2937.0019 | 2864.0619 | 2583.5395 | 1814.01 | 1762.2011 | -1718.4371 | -1550.1237 | 2268.0023 | -2268.0018 | 2268.002 | -2066.8316
0.61 | 3047.439 | 2961.1389 | 2866.719 | 2585.687 | 1858.9378 | 1806.2948 | -1748.6986 | -1577.2691 | 2268.0023 | -2268.0018 | 2268.002 | -2048.902
0.62 | 3071.5279 | 2985.276 | 2869.3761 | 2587.8345 | 1904.3473 | 1850.8711 | -1779.0132 | -1604.4574 | 2268.0023 | -2268.0018 | 2251.3177 | -2030.4196
0.63 | 3095.6168 | 3009.413 | 2872.0332 | 2589.9819 | 1950.2386 | 1895.9302 | -1809.3809 | -1631.6886 | 2268.0023 | -2268.0018 | 2230.407 | -2011.3674
0.64 | 3119.7058 | 3033.5501 | 2874.6903 | 2592.1294 | 1996.6117 | 1941.472 | -1839.8018 | -1658.9628 | 2268.0023 | -2268.0018 | 2208.8399 | -1991.7272
0.65 | 3143.7947 | 3057.6871 | 2877.3475 | 2594.2769 | 2043.4665 | 1987.4966 | -1870.2759 | -1686.28 | 2268.0023 | -2268.0018 | 2186.5948 | -1971.4798
0.66 | 3167.8836 | 3081.8242 | 2880.0046 | 2596.4244 | 2090.8032 | 2034.004 | -1900.803 | -1713.6401 | 2268.0023 | -2268.0018 | 2163.6484 | -1950.6043
0.67 | 3191.9725 | 3105.9612 | 2882.6617 | 2598.5719 | 2138.6216 | 2080.994 | -1931.3833 | -1741.0431 | 2268.0023 | -2268.0018 | 2139.9759 | -1929.0787
0.68 | 3216.0615 | 3130.0983 | 2885.3188 | 2600.7193 | 2186.9218 | 2128.4668 | -1962.0168 | -1768.4892 | 2268.0023 | -2268.0018 | 2115.5507 | -1906.8789
0.69 | 3240.1504 | 3154.2353 | 2887.9759 | 2602.8668 | 2235.7038 | 2176.4224 | -1992.7034 | -1795.9781 | 2268.0023 | -2268.0018 | 2090.344 | -1883.9794
0.7 | 3264.2393 | 3178.3723 | 2890.6331 | 2605.0143 | 2284.9675 | 2224.8606 | -2023.4431 | -1823.51 | 2268.0023 | -2268.0018 | 2064.3249 | -1860.3523
0.71 | 3274.6636 | 3186.327 | 2887.4098 | 2607.8757 | 2325.0111 | 2262.2922 | -2050.061 | -1851.5918 | 2268.0023 | -2243.8168 | 2033.3188 | -1836.4705
0.72 | 3285.0878 | 3194.2816 | 2884.1865 | 2610.7371 | 2365.2632 | 2299.8828 | -2076.6143 | -1879.7307 | 2268.0023 | -2216.7486 | 2001.5507 | -1811.7839
0.73 | 3295.5121 | 3202.2362 | 2880.9633 | 2613.5986 | 2405.7238 | 2337.6325 | -2103.1032 | -1907.9269 | 2252.3083 | -2188.5592 | 1968.9861 | -1786.2565
0.74 | 3305.9363 | 3210.1909 | 2877.74 | 2616.46 | 2446.3929 | 2375.5412 | -2129.5276 | -1936.1804 | 2223.5955 | -2159.1964 | 1935.5877 | -1759.849
0.75 | 3316.3606 | 3218.1455 | 2874.5168 | 2619.3214 | 2487.2704 | 2413.6091 | -2155.8876 | -1964.491 | 2193.5663 | -2128.6032 | 1901.3141 | -1732.5183
0.76 | 3326.7848 | 3226.1001 | 2871.2935 | 2622.1828 | 2528.3565 | 2451.8361 | -2182.1831 | -1992.8589 | 2162.1542 | -2096.7169 | 1866.1199 | -1704.2171
0.77 | 3337.2091 | 3234.0548 | 2868.0703 | 2625.0442 | 2569.651 | 2490.2222 | -2208.4141 | -2021.2841 | 2129.2859 | -2063.4689 | 1829.9547 | -1674.8934
0.78 | 3347.6333 | 3242.0094 | 2864.847 | 2627.9056 | 2611.154 | 2528.7673 | -2234.5807 | -2049.7664 | 2094.8804 | -2028.7831 | 1792.7626 | -1644.4895
0.79 | 3358.0576 | 3249.964 | 2861.6238 | 2630.7671 | 2652.8655 | 2567.4716 | -2260.6828 | -2078.306 | 2058.8481 | -1992.5752 | 1754.4811 | -1612.9413
0.8 | 3368.4819 | 3257.9187 | 2858.4005 | 2633.6285 | 2694.7855 | 2606.3349 | -2286.7204 | -2106.9028 | 2021.0891 | -1954.7512 | 1715.0403 | -1580.1771
0.81 | 3373.3153 | 3268.1462 | 2855.6651 | 2638.0785 | 2732.3854 | 2647.1984 | -2313.0887 | -2136.8436 | 1978.2129 | -1916.5386 | 1674.6473 | -1547.0481
0.82 | 3378.1487 | 3278.3737 | 2852.9297 | 2642.5286 | 2770.0819 | 2688.2664 | -2339.4023 | -2166.8734 | 1933.5291 | -1876.4215 | 1632.9129 | -1512.4869
0.83 | 3382.9821 | 3288.6012 | 2850.1943 | 2646.9786 | 2807.8752 | 2729.539 | -2365.6612 | -2196.9922 | 1886.9036 | -1834.2614 | 1589.734 | -1476.3878
0.84 | 3387.8156 | 3298.8288 | 2847.4589 | 2651.4286 | 2845.7651 | 2771.0162 | -2391.8654 | -2227.2 | 1838.1826 | -1789.8996 | 1544.9924 | -1438.6291
0.85 | 3392.649 | 3309.0563 | 2844.7235 | 2655.8787 | 2883.7516 | 2812.6979 | -2418.0149 | -2257.4969 | 1787.1888 | -1743.1536 | 1498.5511 | -1399.0709
0.86 | 3397.4824 | 3319.2838 | 2841.988 | 2660.3287 | 2921.8349 | 2854.5841 | -2444.1097 | -2287.8827 | 1733.715 | -1693.8107 | 1450.2495 | -1357.5499
0.87 | 3402.3159 | 3329.5114 | 2839.2526 | 2664.7787 | 2960.0148 | 2896.6749 | -2470.1498 | -2318.3575 | 1677.5177 | -1641.6213 | 1399.8984 | -1313.8737
0.88 | 3407.1493 | 3339.7389 | 2836.5172 | 2669.2288 | 2998.2914 | 2938.9702 | -2496.1352 | -2348.9213 | 1618.3062 | -1586.2881 | 1347.271 | -1267.8134
0.89 | 3411.9827 | 3349.9664 | 2833.7818 | 2673.6788 | 3036.6646 | 2981.4701 | -2522.0658 | -2379.5741 | 1555.7294 | -1527.4524 | 1292.0926 | -1219.092
0.9 | 3416.8161 | 3360.1939 | 2831.0464 | 2678.1289 | 3075.1345 | 3024.1745 | -2547.9418 | -2410.316 | 1489.3556 | -1464.6746 | 1234.0245 | -1167.3693
0.91 | 3421.4129 | 3369.1935 | 2825.1938 | 2684.48 | 3113.4858 | 3065.9661 | -2570.9263 | -2442.8768 | 1418.546 | -1396.8954 | 1171.3486 | -1113.0075
0.92 | 3426.0097 | 3378.193 | 2819.3411 | 2690.8311 | 3151.9289 | 3107.9376 | -2593.7939 | -2475.5646 | 1342.7161 | -1323.9759 | 1104.9516 | -1054.5861
0.93 | 3430.6065 | 3387.1926 | 2813.4885 | 2697.1822 | 3190.464 | 3150.0891 | -2616.5443 | -2508.3794 | 1260.9521 | -1244.9949 | 1034.1245 | -991.375
0.94 | 3435.2032 | 3396.1921 | 2807.6359 | 2703.5333 | 3229.091 | 3192.4206 | -2639.1777 | -2541.3213 | 1172.0035 | -1158.694 | 957.8936 | -922.3765
0.95 | 3439.8 | 3405.1917 | 2801.7832 | 2709.8844 | 3267.81 | 3234.9321 | -2661.6941 | -2574.3902 | 1074.0772 | -1063.2708 | 874.8565 | -846.1611
0.96 | 3439.8 | 3412.1133 | 2794.0539 | 2720.5349 | 3302.208 | 3275.6288 | -2682.2918 | -2611.7135 | 963.144 | -955.3917 | 782.3351 | -761.7498
0.97 | 3439.8 | 3419.035 | 2786.3246 | 2731.1853 | 3336.606 | 3316.464 | -2702.7349 | -2649.2497 | 836.2323 | -831.1842 | 677.3692 | -663.9646
0.98 | 3439.8 | 3425.9567 | 2778.5953 | 2741.8357 | 3371.004 | 3357.4375 | -2723.0234 | -2686.999 | 684.5116 | -681.7568 | 552.9335 | -545.6184
0.99 | 3439.8 | 3432.8783 | 2770.8659 | 2752.4862 | 3405.402 | 3398.5496 | -2743.1573 | -2724.9613 | 485.2435 | -484.2671 | 390.8787 | -388.286
1 | 3439.8 | 3439.8 | 2763.1366 | 2763.1366 | 3439.8 | 3439.8 | -2763.1366 | -2763.1366 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_40C_1.0pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 40 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1490 |  | VDC
Nom. Battery Voltage** |  |  |  | 1291.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1159 |  | VDC |  | Please select:
AC Voltage |  |  |  | 1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @40°C, 1159Vdc min. battery voltage and 1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2520.0026 | 2520.002 | 2520.0022 | 2520.0017 | 0 | 0 | 0 | 0 | 2520.0026 | -2520.002 | 2520.0022 | -2520.0017
0.01 | 2520.0026 | 2520.002 | 2520.0022 | 2520.0017 | 0.0252 | 0.0252 | -0.0252 | -0.0252 | 2520.0026 | -2520.002 | 2520.0022 | -2520.0017
0.05 | 2532.7546 | 2530.2173 | 2531.0657 | 2528.72 | 126.6377 | 126.5109 | -126.5533 | -126.436 | 2520.0026 | -2520.002 | 2520.0022 | -2520.002
0.1 | 2545.5091 | 2540.4347 | 2542.1313 | 2537.44 | 254.5509 | 254.0435 | -254.2131 | -253.744 | 2520.0026 | -2520.002 | 2520.0022 | -2520.002
0.15 | 2583.5065 | 2571.4608 | 2574.2699 | 2562.3212 | 387.526 | 385.7191 | -386.1405 | -384.3482 | 2520.0026 | -2520.002 | 2520.0022 | -2520.002
0.2 | 2621.5038 | 2602.487 | 2606.4084 | 2587.2024 | 524.3008 | 520.4974 | -521.2817 | -517.4405 | 2520.0026 | -2520.002 | 2520.0022 | -2520.002
0.25 | 2683.1979 | 2654.736 | 2657.6969 | 2626.5659 | 670.7995 | 663.684 | -664.4242 | -656.6415 | 2520.0026 | -2520.002 | 2520.0022 | -2520.002
0.3 | 2744.8921 | 2706.9851 | 2708.9855 | 2665.9295 | 823.4676 | 812.0955 | -812.6957 | -799.7789 | 2520.0026 | -2520.002 | 2520.0022 | -2520.002
0.35 | 2830.9098 | 2779.653 | 2775.9707 | 2718.3465 | 990.8184 | 972.8785 | -971.5897 | -951.4213 | 2520.0026 | -2520.002 | 2520.0022 | -2520.002
0.4 | 2916.9276 | 2852.3208 | 2842.9559 | 2770.7635 | 1166.7711 | 1140.9283 | -1137.1823 | -1108.3054 | 2520.0026 | -2520.002 | 2520.0022 | -2520.002
0.45 | 3018.9551 | 2945.7858 | 2922.7833 | 2813.5621 | 1358.5298 | 1325.6036 | -1315.2525 | -1266.103 | 2520.0026 | -2520.002 | 2520.0022 | -2512.5913
0.5 | 3120.9826 | 3039.2508 | 3002.6108 | 2856.3607 | 1560.4913 | 1519.6254 | -1501.3054 | -1428.1804 | 2520.0026 | -2520.002 | 2520.0022 | -2473.681
0.51 | 3144.8121 | 3061.6592 | 3020.5788 | 2857.7846 | 1603.8542 | 1561.4462 | -1540.4952 | -1457.4702 | 2520.0026 | -2520.002 | 2520.0022 | -2458.1932
0.52 | 3168.6417 | 3084.0677 | 3038.5468 | 2859.2085 | 1647.6937 | 1603.7152 | -1580.0443 | -1486.7884 | 2520.0026 | -2520.002 | 2520.0022 | -2442.2394
0.53 | 3192.4712 | 3106.4762 | 3056.5148 | 2860.6324 | 1692.0097 | 1646.4324 | -1619.9529 | -1516.1351 | 2520.0026 | -2520.002 | 2520.0022 | -2425.8095
0.54 | 3216.3007 | 3128.8846 | 3074.4829 | 2862.0562 | 1736.8024 | 1689.5977 | -1660.2207 | -1545.5104 | 2520.0026 | -2520.002 | 2520.0022 | -2408.8926
0.55 | 3240.1302 | 3151.2931 | 3092.4509 | 2863.4801 | 1782.0716 | 1733.2112 | -1700.848 | -1574.914 | 2520.0026 | -2520.002 | 2520.0022 | -2391.4774
0.56 | 3263.9597 | 3173.7016 | 3110.4189 | 2864.904 | 1827.8175 | 1777.2729 | -1741.8346 | -1604.3462 | 2520.0026 | -2520.002 | 2520.0022 | -2373.5517
0.57 | 3287.7893 | 3196.11 | 3128.3869 | 2866.3278 | 1874.0399 | 1821.7827 | -1783.1805 | -1633.8069 | 2520.0026 | -2520.002 | 2520.0022 | -2355.103
0.58 | 3311.6188 | 3218.5185 | 3146.3549 | 2867.7517 | 1920.7389 | 1866.7407 | -1824.8859 | -1663.296 | 2520.0026 | -2520.002 | 2520.0022 | -2336.1178
0.59 | 3335.4483 | 3240.927 | 3164.3229 | 2869.1756 | 1967.9145 | 1912.1469 | -1866.9505 | -1692.8136 | 2520.0026 | -2520.002 | 2520.0022 | -2316.5817
0.6 | 3359.2778 | 3263.3354 | 3182.291 | 2870.5994 | 2015.5667 | 1958.0013 | -1909.3746 | -1722.3597 | 2520.0026 | -2520.002 | 2520.0022 | -2296.4795
0.61 | 3386.0433 | 3290.1544 | 3185.2433 | 2872.9855 | 2065.4864 | 2006.9942 | -1942.9984 | -1752.5212 | 2520.0026 | -2520.002 | 2520.0022 | -2276.5578
0.62 | 3412.8088 | 3316.9733 | 3188.1957 | 2875.3716 | 2115.9414 | 2056.5235 | -1976.6813 | -1782.7304 | 2520.0026 | -2520.002 | 2501.4641 | -2256.0218
0.63 | 3439.5743 | 3343.7923 | 3191.148 | 2877.7577 | 2166.9318 | 2106.5891 | -2010.4233 | -1812.9874 | 2520.0026 | -2520.002 | 2478.23 | -2234.8526
0.64 | 3466.3397 | 3370.6112 | 3194.1004 | 2880.1438 | 2218.4574 | 2157.1912 | -2044.2242 | -1843.292 | 2520.0026 | -2520.002 | 2454.2666 | -2213.0302
0.65 | 3493.1052 | 3397.4301 | 3197.0527 | 2882.5299 | 2270.5184 | 2208.3296 | -2078.0843 | -1873.6444 | 2520.0026 | -2520.002 | 2429.5497 | -2190.5331
0.66 | 3519.8707 | 3424.2491 | 3200.0051 | 2884.916 | 2323.1146 | 2260.0044 | -2112.0034 | -1904.0445 | 2520.0026 | -2520.002 | 2404.0537 | -2167.3381
0.67 | 3546.6361 | 3451.068 | 3202.9574 | 2887.3021 | 2376.2462 | 2312.2156 | -2145.9815 | -1934.4924 | 2520.0026 | -2520.002 | 2377.751 | -2143.4207
0.68 | 3573.4016 | 3477.887 | 3205.9098 | 2889.6882 | 2429.9131 | 2364.9631 | -2180.0187 | -1964.988 | 2520.0026 | -2520.002 | 2350.6119 | -2118.7544
0.69 | 3600.1671 | 3504.7059 | 3208.8622 | 2892.0743 | 2484.1153 | 2418.2471 | -2214.1149 | -1995.5312 | 2520.0026 | -2520.002 | 2322.6045 | -2093.3104
0.7 | 3626.9326 | 3531.5248 | 3211.8145 | 2894.4603 | 2538.8528 | 2472.0674 | -2248.2702 | -2026.1222 | 2520.0026 | -2520.002 | 2293.6943 | -2067.0581
0.71 | 3638.5151 | 3540.3633 | 3208.2331 | 2897.6397 | 2583.3457 | 2513.658 | -2277.8455 | -2057.3242 | 2520.0026 | -2493.1298 | 2259.2431 | -2040.5227
0.72 | 3650.0976 | 3549.2018 | 3204.6517 | 2900.819 | 2628.0702 | 2555.4253 | -2307.3492 | -2088.5897 | 2520.0026 | -2463.054 | 2223.9452 | -2013.0932
0.73 | 3661.6801 | 3558.0403 | 3201.0703 | 2903.9984 | 2673.0265 | 2597.3694 | -2336.7813 | -2119.9188 | 2502.5648 | -2431.7325 | 2187.7624 | -1984.7294
0.74 | 3673.2626 | 3566.8788 | 3197.4889 | 2907.1778 | 2718.2143 | 2639.4903 | -2366.1418 | -2151.3115 | 2470.6616 | -2399.1071 | 2150.653 | -1955.3877
0.75 | 3684.8451 | 3575.7172 | 3193.9075 | 2910.3571 | 2763.6338 | 2681.7879 | -2395.4306 | -2182.7678 | 2437.2959 | -2365.1146 | 2112.5713 | -1925.0203
0.76 | 3696.4276 | 3584.5557 | 3190.3261 | 2913.5365 | 2809.285 | 2724.2623 | -2424.6479 | -2214.2877 | 2402.3936 | -2329.6855 | 2073.4666 | -1893.5746
0.77 | 3708.0101 | 3593.3942 | 3186.7447 | 2916.7158 | 2855.1678 | 2766.9135 | -2453.7935 | -2245.8712 | 2365.8732 | -2292.7432 | 2033.283 | -1860.9927
0.78 | 3719.5926 | 3602.2327 | 3183.1633 | 2919.8952 | 2901.2822 | 2809.7415 | -2482.8674 | -2277.5182 | 2327.6449 | -2254.2034 | 1991.9584 | -1827.2106
0.79 | 3731.1751 | 3611.0711 | 3179.5819 | 2923.0745 | 2947.6283 | 2852.7462 | -2511.8697 | -2309.2289 | 2287.609 | -2213.9724 | 1949.4234 | -1792.157
0.8 | 3742.7576 | 3619.9096 | 3176.0006 | 2926.2539 | 2994.2061 | 2895.9277 | -2540.8004 | -2341.0031 | 2245.6546 | -2171.9458 | 1905.6003 | -1755.7523
0.81 | 3748.1281 | 3631.2735 | 3172.9612 | 2931.1983 | 3035.9838 | 2941.3316 | -2570.0986 | -2374.2707 | 2198.0143 | -2129.4873 | 1860.7192 | -1718.9423
0.82 | 3753.4986 | 3642.6375 | 3169.9219 | 2936.1428 | 3077.8688 | 2986.9627 | -2599.3359 | -2407.6371 | 2148.3657 | -2084.9128 | 1814.3476 | -1680.5411
0.83 | 3758.869 | 3654.0014 | 3166.8825 | 2941.0873 | 3119.8613 | 3032.8211 | -2628.5125 | -2441.1025 | 2096.5595 | -2038.0682 | 1766.3711 | -1640.4308
0.84 | 3764.2395 | 3665.3653 | 3163.8432 | 2946.0318 | 3161.9612 | 3078.9069 | -2657.6283 | -2474.6667 | 2042.4252 | -1988.7774 | 1716.6583 | -1598.4768
0.85 | 3769.61 | 3676.7292 | 3160.8038 | 2950.9763 | 3204.1685 | 3125.2198 | -2686.6833 | -2508.3298 | 1985.7653 | -1936.8373 | 1665.0567 | -1554.5232
0.86 | 3774.9805 | 3688.0931 | 3157.7645 | 2955.9208 | 3246.4832 | 3171.7601 | -2715.6775 | -2542.0919 | 1926.35 | -1882.0119 | 1611.3884 | -1508.3887
0.87 | 3780.351 | 3699.4571 | 3154.7251 | 2960.8653 | 3288.9053 | 3218.5276 | -2744.6109 | -2575.9528 | 1863.9085 | -1824.0237 | 1555.4427 | -1459.8597
0.88 | 3785.7214 | 3710.821 | 3151.6858 | 2965.8098 | 3331.4349 | 3265.5225 | -2773.4835 | -2609.9126 | 1798.1181 | -1762.5423 | 1496.9678 | -1408.6816
0.89 | 3791.0919 | 3722.1849 | 3148.6465 | 2970.7542 | 3374.0718 | 3312.7446 | -2802.2953 | -2643.9713 | 1728.5883 | -1697.1694 | 1435.6585 | -1354.5467
0.9 | 3796.4624 | 3733.5488 | 3145.6071 | 2975.6987 | 3416.8161 | 3360.1939 | -2831.0464 | -2678.1289 | 1654.8396 | -1627.4162 | 1371.1384 | -1297.077
0.91 | 3801.5699 | 3743.5483 | 3139.1042 | 2982.7555 | 3459.4286 | 3406.629 | -2856.5848 | -2714.3075 | 1576.1622 | -1552.106 | 1301.4985 | -1236.675
0.92 | 3806.6774 | 3753.5478 | 3132.6013 | 2989.8123 | 3502.1432 | 3453.264 | -2881.9932 | -2750.6273 | 1491.9068 | -1471.0843 | 1227.7239 | -1171.7623
0.93 | 3811.785 | 3763.5473 | 3126.0983 | 2996.8691 | 3544.96 | 3500.099 | -2907.2715 | -2787.0883 | 1401.0578 | -1383.3276 | 1149.0272 | -1101.5278
0.94 | 3816.8925 | 3773.5468 | 3119.5954 | 3003.9259 | 3587.8789 | 3547.134 | -2932.4197 | -2823.6904 | 1302.2262 | -1287.4377 | 1064.3262 | -1024.8627
0.95 | 3822 | 3783.5463 | 3113.0925 | 3010.9827 | 3630.9 | 3594.369 | -2957.4379 | -2860.4336 | 1193.4191 | -1181.412 | 972.0628 | -940.179
0.96 | 3822 | 3791.237 | 3104.5044 | 3022.8165 | 3669.12 | 3639.5876 | -2980.3242 | -2901.9039 | 1070.16 | -1061.5464 | 869.2612 | -846.3886
0.97 | 3822 | 3798.9278 | 3095.9162 | 3034.6503 | 3707.34 | 3684.9599 | -3003.0387 | -2943.6108 | 929.147 | -923.538 | 752.6324 | -737.7384
0.98 | 3822 | 3806.6185 | 3087.3281 | 3046.4842 | 3745.56 | 3730.4862 | -3025.5815 | -2985.5545 | 760.5684 | -757.5075 | 614.3705 | -606.2427
0.99 | 3822 | 3814.3093 | 3078.7399 | 3058.318 | 3783.78 | 3776.1662 | -3047.9525 | -3027.7348 | 539.1594 | -538.0745 | 434.3097 | -431.4288
1 | 3822 | 3822 | 3070.1518 | 3070.1518 | 3822 | 3822 | -3070.1518 | -3070.1518 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_40C_1.1pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 40 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1490 |  | VDC
Nom. Battery Voltage** |  |  |  | 1291.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1159 |  | VDC |  | Please select:
AC Voltage |  |  |  | 1.1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @40°C, 1159Vdc min. battery voltage and 1.1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2520.0028 | 2520.0022 | 2520.0027 | 2520.0021 | 0 | 0 | 0 | 0 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0021
0.01 | 2520.0028 | 2520.0022 | 2520.0027 | 2520.0021 | 0.0252 | 0.0252 | -0.0252 | -0.0252 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0021
0.05 | 2533.7694 | 2530.9019 | 2533.5809 | 2530.4204 | 126.6885 | 126.5451 | -126.679 | -126.521 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0022
0.1 | 2547.5388 | 2541.8037 | 2547.1617 | 2540.8408 | 254.7539 | 254.1804 | -254.7162 | -254.0841 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0022
0.15 | 2588.7577 | 2574.894 | 2586.6982 | 2570.5942 | 388.3137 | 386.2341 | -388.0047 | -385.5891 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0022
0.2 | 2629.9766 | 2607.9842 | 2626.2347 | 2600.3476 | 525.9953 | 521.5968 | -525.2469 | -520.0695 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0022
0.25 | 2696.1138 | 2663.435 | 2688.245 | 2647.6824 | 674.0284 | 665.8588 | -672.0613 | -661.9206 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0022
0.3 | 2762.2509 | 2718.8858 | 2750.2553 | 2695.0171 | 828.6753 | 815.6658 | -825.0766 | -808.5051 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0022
0.35 | 2851.1411 | 2795.86 | 2829.8763 | 2756.9152 | 997.8994 | 978.551 | -990.4567 | -964.9203 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0022
0.4 | 2940.0313 | 2872.8342 | 2909.4972 | 2818.8134 | 1176.0125 | 1149.1337 | -1163.7989 | -1127.5254 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0022
0.45 | 3046.6868 | 2971.295 | 3004.759 | 2893.4466 | 1371.009 | 1337.0828 | -1352.1415 | -1302.051 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0022
0.5 | 3153.3422 | 3069.7559 | 3100.0207 | 2968.0798 | 1576.6711 | 1534.8779 | -1550.0104 | -1484.0399 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0022
0.51 | 3177.9388 | 3093.2171 | 3121.3805 | 2986.5065 | 1620.7488 | 1577.5407 | -1591.9041 | -1523.1183 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0022
0.52 | 3202.5354 | 3116.6783 | 3142.7403 | 3004.9331 | 1665.3184 | 1620.6727 | -1634.2249 | -1562.5652 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0022
0.53 | 3227.1319 | 3140.1394 | 3164.1001 | 3023.3598 | 1710.3799 | 1664.2739 | -1676.973 | -1602.3807 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0022
0.54 | 3251.7285 | 3163.6006 | 3185.4598 | 3041.7865 | 1755.9334 | 1708.3443 | -1720.1483 | -1642.5647 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0022
0.55 | 3276.3251 | 3187.0618 | 3206.8196 | 3060.2131 | 1801.9788 | 1752.884 | -1763.7508 | -1683.1172 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0022
0.56 | 3300.9217 | 3210.523 | 3228.1794 | 3078.6398 | 1848.5162 | 1797.8929 | -1807.7805 | -1724.0383 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0022
0.57 | 3325.5183 | 3233.9842 | 3249.5392 | 3097.0665 | 1895.5454 | 1843.371 | -1852.2373 | -1765.3279 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0022
0.58 | 3350.1149 | 3257.4454 | 3270.899 | 3115.4931 | 1943.0666 | 1889.3183 | -1897.1214 | -1806.986 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0022
0.59 | 3374.7115 | 3280.9066 | 3292.2587 | 3133.9198 | 1991.0798 | 1935.7349 | -1942.4327 | -1849.0127 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0022
0.6 | 3399.3081 | 3304.3678 | 3313.6185 | 3152.3465 | 2039.5848 | 1982.6207 | -1988.1711 | -1891.4079 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0022
0.61 | 3426.9118 | 3332.067 | 3336.6307 | 3155.3327 | 2090.4162 | 2032.5608 | -2035.3447 | -1924.7529 | 2520.0028 | -2520.0022 | 2520.0027 | -2500.2901
0.62 | 3454.5156 | 3359.7662 | 3359.6429 | 3158.3189 | 2141.7997 | 2083.055 | -2082.9786 | -1958.1577 | 2520.0028 | -2520.0022 | 2520.0027 | -2478.0227
0.63 | 3482.1193 | 3387.4654 | 3382.6551 | 3161.305 | 2193.7352 | 2134.1032 | -2131.0727 | -1991.6222 | 2520.0028 | -2520.0022 | 2520.0027 | -2455.0541
0.64 | 3509.7231 | 3415.1646 | 3405.6673 | 3164.2912 | 2246.2228 | 2185.7053 | -2179.6271 | -2025.1464 | 2520.0028 | -2520.0022 | 2520.0027 | -2431.362
0.65 | 3537.3268 | 3442.8638 | 3428.6795 | 3167.2774 | 2299.2624 | 2237.8615 | -2228.6417 | -2058.7303 | 2520.0028 | -2520.0022 | 2520.0027 | -2406.9225
0.66 | 3564.9306 | 3470.563 | 3451.6917 | 3170.2636 | 2352.8542 | 2290.5716 | -2278.1165 | -2092.374 | 2520.0028 | -2520.0022 | 2520.0027 | -2381.71
0.67 | 3592.5343 | 3498.2622 | 3474.7039 | 3173.2498 | 2406.998 | 2343.8357 | -2328.0516 | -2126.0774 | 2520.0028 | -2520.0022 | 2520.0027 | -2355.6972
0.68 | 3620.1381 | 3525.9614 | 3497.7161 | 3176.236 | 2461.6939 | 2397.6538 | -2378.447 | -2159.8405 | 2520.0028 | -2520.0022 | 2520.0027 | -2328.8547
0.69 | 3647.7418 | 3553.6606 | 3520.7283 | 3179.2222 | 2516.9419 | 2452.0258 | -2429.3026 | -2193.6633 | 2520.0028 | -2520.0022 | 2520.0027 | -2301.1508
0.7 | 3675.3456 | 3581.3598 | 3532.996 | 3182.2083 | 2572.7419 | 2506.9519 | -2473.0972 | -2227.5458 | 2520.0028 | -2520.0022 | 2520.0027 | -2272.5513
0.71 | 3690.011 | 3596.963 | 3529.0564 | 3185.5568 | 2619.9078 | 2553.8437 | -2505.6301 | -2261.7453 | 2520.0028 | -2520.0022 | 2485.1675 | -2243.2744
0.72 | 3704.6765 | 3612.5661 | 3525.1169 | 3188.9053 | 2667.3671 | 2601.0476 | -2538.0842 | -2296.0118 | 2520.0028 | -2507.0272 | 2446.3397 | -2213.0175
0.73 | 3719.3419 | 3628.1693 | 3521.1774 | 3192.2537 | 2715.1196 | 2648.5636 | -2570.4595 | -2330.3452 | 2520.0028 | -2479.6619 | 2406.5386 | -2181.7367
0.74 | 3734.0074 | 3643.7724 | 3517.2378 | 3195.6022 | 2763.1654 | 2696.3916 | -2602.756 | -2364.7456 | 2511.519 | -2450.8264 | 2365.7183 | -2149.384
0.75 | 3748.6728 | 3659.3756 | 3513.2983 | 3198.9506 | 2811.5046 | 2744.5317 | -2634.9737 | -2399.213 | 2479.514 | -2420.4494 | 2323.8284 | -2115.907
0.76 | 3763.3382 | 3674.9787 | 3509.3588 | 3202.2991 | 2860.1371 | 2792.9838 | -2667.1127 | -2433.7473 | 2445.8803 | -2388.4535 | 2280.8132 | -2081.2481
0.77 | 3778.0037 | 3690.5819 | 3505.4192 | 3205.6476 | 2909.0628 | 2841.748 | -2699.1728 | -2468.3486 | 2410.5321 | -2354.7532 | 2236.6113 | -2045.3438
0.78 | 3792.6691 | 3706.185 | 3501.4797 | 3208.996 | 2958.2819 | 2890.8243 | -2731.1541 | -2503.0169 | 2373.3746 | -2319.2546 | 2191.1543 | -2008.124
0.79 | 3807.3346 | 3721.7881 | 3497.5401 | 3212.3445 | 3007.7943 | 2940.2126 | -2763.0567 | -2537.7521 | 2334.3029 | -2281.8538 | 2144.3658 | -1969.5104
0.8 | 3822 | 3737.3913 | 3493.6006 | 3215.693 | 3057.6 | 2989.913 | -2794.8805 | -2572.5544 | 2293.2 | -2242.4348 | 2096.1604 | -1929.4158
0.81 | 3822 | 3745.8522 | 3490.2573 | 3221.4803 | 3095.82 | 3034.1402 | -2827.1084 | -2609.3991 | 2241.335 | -2196.6796 | 2046.7912 | -1889.1723
0.82 | 3822 | 3754.313 | 3486.9141 | 3227.2677 | 3134.04 | 3078.5367 | -2859.2695 | -2646.3595 | 2187.5734 | -2148.8318 | 1995.7824 | -1847.1703
0.83 | 3822 | 3762.7739 | 3483.5708 | 3233.0551 | 3172.26 | 3123.1023 | -2891.3637 | -2683.4357 | 2131.7717 | -2098.7375 | 1943.0082 | -1803.2798
0.84 | 3822 | 3771.2348 | 3480.2275 | 3238.8424 | 3210.48 | 3167.8372 | -2923.3911 | -2720.6276 | 2073.7652 | -2046.2207 | 1888.3241 | -1757.3519
0.85 | 3822 | 3779.6956 | 3476.8842 | 3244.6298 | 3248.7 | 3212.7413 | -2955.3516 | -2757.9353 | 2013.3634 | -1991.0782 | 1831.5624 | -1709.2148
0.86 | 3822 | 3788.1565 | 3473.5409 | 3250.4172 | 3286.92 | 3257.8146 | -2987.2452 | -2795.3588 | 1950.3438 | -1933.0737 | 1772.5272 | -1658.6685
0.87 | 3822 | 3796.6174 | 3470.1977 | 3256.2046 | 3325.14 | 3303.0571 | -3019.072 | -2832.898 | 1884.4437 | -1871.9287 | 1710.9869 | -1605.4773
0.88 | 3822 | 3805.0783 | 3466.8544 | 3261.9919 | 3363.36 | 3348.4689 | -3050.8319 | -2870.5529 | 1815.3494 | -1807.312 | 1646.6646 | -1549.3603
0.89 | 3822 | 3813.5391 | 3463.5111 | 3267.7793 | 3401.58 | 3394.0498 | -3082.5249 | -2908.3236 | 1742.6811 | -1738.8233 | 1579.2243 | -1489.9784
0.9 | 3822 | 3822 | 3460.1678 | 3273.2686 | 3439.8 | 3439.8 | -3114.151 | -2945.9417 | 1665.9712 | -1665.9712 | 1508.2522 | -1426.7847
0.91 | 3822 | 3822 | 3453.0146 | 3281.0311 | 3478.02 | 3478.02 | -3142.2433 | -2985.7383 | 1584.6327 | -1584.6327 | 1431.6483 | -1360.3425
0.92 | 3822 | 3822 | 3445.8614 | 3288.7935 | 3516.24 | 3516.24 | -3170.1925 | -3025.6901 | 1497.912 | -1497.912 | 1350.4963 | -1288.9386
0.93 | 3822 | 3822 | 3438.7082 | 3296.556 | 3554.46 | 3554.46 | -3197.9986 | -3065.7971 | 1404.8125 | -1404.8125 | 1263.9299 | -1211.6805
0.94 | 3822 | 3822 | 3431.555 | 3304.3185 | 3592.68 | 3592.68 | -3225.6617 | -3106.0594 | 1303.9687 | -1303.9687 | 1170.7589 | -1127.349
0.95 | 3822 | 3822 | 3424.4017 | 3312.081 | 3630.9 | 3630.9 | -3253.1817 | -3146.4769 | 1193.4191 | -1193.4191 | 1069.2691 | -1034.197
0.96 | 3822 | 3822 | 3414.9548 | 3325.0982 | 3669.12 | 3669.12 | -3278.3566 | -3192.0942 | 1070.16 | -1070.16 | 956.1873 | -931.0275
0.97 | 3822 | 3822 | 3405.5078 | 3338.1154 | 3707.34 | 3707.34 | -3303.3426 | -3237.9719 | 929.147 | -929.147 | 827.8957 | -811.5123
0.98 | 3822 | 3822 | 3396.0609 | 3351.1326 | 3745.56 | 3745.56 | -3328.1397 | -3284.1099 | 760.5684 | -760.5684 | 675.8076 | -666.867
0.99 | 3822 | 3822 | 3386.6139 | 3364.1498 | 3783.78 | 3783.78 | -3352.7478 | -3330.5083 | 539.1594 | -539.1594 | 477.7407 | -474.5717
1 | 3822 | 3822 | 3377.167 | 3377.167 | 3822 | 3822 | -3377.167 | -3377.167 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_50C_0.9pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 50 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1490 |  | VDC
Nom. Battery Voltage** |  |  |  | 1291.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1159 |  | VDC |  | Please select:
AC Voltage |  |  |  | 0.9 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @50°C, 1159Vdc min. battery voltage and 0.9pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2268.002 | 2268.0016 | 2268.0017 | 2268.0014 | 0 | 0 | 0 | 0 | 2268.002 | -2268.0016 | 2268.0017 | -2268.0014
0.01 | 2268.002 | 2268.0016 | 2268.0017 | 2268.0014 | 0.02268 | 0.02268 | -0.02268 | -0.02268 | 2268.002 | -2268.0016 | 2268.0017 | -2268.0014
0.05 | 2278.0764 | 2275.9735 | 2276.6063 | 2274.7958 | 113.9038 | 113.7987 | -113.8303 | -113.7398 | 2268.002 | -2268.0016 | 2268.0017 | -2268.0016
0.1 | 2288.1528 | 2283.947 | 2285.2125 | 2281.5915 | 228.8153 | 228.3947 | -228.5213 | -228.1592 | 2268.002 | -2268.0016 | 2268.0017 | -2268.0016
0.15 | 2318.2457 | 2308.3991 | 2310.2798 | 2300.949 | 347.7369 | 346.2599 | -346.542 | -345.1424 | 2268.002 | -2268.0016 | 2268.0017 | -2268.0016
0.2 | 2348.3387 | 2332.8511 | 2335.347 | 2320.3065 | 469.6677 | 466.5702 | -467.0694 | -464.0613 | 2268.002 | -2268.0016 | 2268.0017 | -2268.0016
0.25 | 2397.4832 | 2374.1033 | 2375.1156 | 2351.0024 | 599.3708 | 593.5258 | -593.7789 | -587.7506 | 2268.002 | -2268.0016 | 2268.0017 | -2268.0016
0.3 | 2446.6278 | 2415.3556 | 2414.8842 | 2381.6982 | 733.9883 | 724.6067 | -724.4653 | -714.5095 | 2268.002 | -2268.0016 | 2268.0017 | -2268.0016
0.35 | 2515.2451 | 2473.1022 | 2467.6098 | 2392.4681 | 880.3358 | 865.5858 | -863.6634 | -837.3638 | 2268.002 | -2268.0016 | 2268.0017 | -2241.1437
0.4 | 2583.8624 | 2530.8488 | 2520.3355 | 2403.238 | 1033.545 | 1012.3395 | -1008.1342 | -961.2952 | 2268.002 | -2268.0016 | 2268.0017 | -2202.604
0.45 | 2666.1871 | 2604.3965 | 2584.0455 | 2393.6155 | 1199.7842 | 1171.9784 | -1162.8205 | -1077.127 | 2268.002 | -2268.0016 | 2268.0017 | -2137.567
0.5 | 2748.5118 | 2677.9442 | 2647.7556 | 2383.993 | 1374.2559 | 1338.9721 | -1323.8778 | -1191.9965 | 2268.002 | -2268.0016 | 2268.0017 | -2064.5985
0.51 | 2767.7404 | 2696.1324 | 2653.9461 | 2384.9876 | 1411.5476 | 1375.0275 | -1353.5125 | -1216.3437 | 2268.002 | -2268.0016 | 2268.0017 | -2051.5052
0.52 | 2786.969 | 2714.3205 | 2660.1366 | 2385.9821 | 1449.2239 | 1411.4467 | -1383.271 | -1240.7107 | 2268.002 | -2268.0016 | 2268.0017 | -2038.0254
0.53 | 2806.1976 | 2732.5087 | 2666.327 | 2386.9767 | 1487.2847 | 1448.2296 | -1413.1533 | -1265.0977 | 2268.002 | -2268.0016 | 2261.039 | -2024.1506
0.54 | 2825.4261 | 2750.6968 | 2672.5175 | 2387.9713 | 1525.7301 | 1485.3763 | -1443.1594 | -1289.5045 | 2268.002 | -2268.0016 | 2249.3645 | -2009.8719
0.55 | 2844.6547 | 2768.8849 | 2678.708 | 2388.9659 | 1564.5601 | 1522.8867 | -1473.2894 | -1313.9313 | 2268.002 | -2268.0016 | 2237.1622 | -1995.1799
0.56 | 2863.8833 | 2787.0731 | 2684.8984 | 2389.9605 | 1603.7746 | 1560.7609 | -1503.5431 | -1338.3779 | 2268.002 | -2268.0016 | 2224.4185 | -1980.0646
0.57 | 2883.1119 | 2805.2612 | 2691.0889 | 2390.9551 | 1643.3738 | 1598.9989 | -1533.9207 | -1362.8444 | 2268.002 | -2268.0016 | 2211.1189 | -1964.5156
0.58 | 2902.3404 | 2823.4494 | 2697.2794 | 2391.9497 | 1683.3575 | 1637.6006 | -1564.422 | -1387.3308 | 2268.002 | -2268.0016 | 2197.2482 | -1948.5216
0.59 | 2921.569 | 2841.6375 | 2703.4698 | 2392.9443 | 1723.7257 | 1676.5661 | -1595.0472 | -1411.8371 | 2268.002 | -2268.0016 | 2182.7903 | -1932.071
0.6 | 2940.7976 | 2859.8257 | 2709.6603 | 2393.9389 | 1764.4786 | 1715.8954 | -1625.7962 | -1436.3633 | 2268.002 | -2268.0016 | 2167.7283 | -1915.1511
0.61 | 2960.721 | 2870.6848 | 2707.2455 | 2395.8834 | 1806.0398 | 1751.1177 | -1651.4198 | -1461.4889 | 2268.002 | -2268.0016 | 2145.2252 | -1898.5014
0.62 | 2980.6444 | 2881.5439 | 2704.8307 | 2397.828 | 1847.9995 | 1786.5572 | -1676.9951 | -1486.6534 | 2268.002 | -2260.8645 | 2122.2151 | -1881.3402
0.63 | 3000.5678 | 2892.403 | 2702.4159 | 2399.7726 | 1890.3577 | 1822.2139 | -1702.522 | -1511.8567 | 2268.002 | -2246.2261 | 2098.6831 | -1863.6517
0.64 | 3020.4912 | 2903.2621 | 2700.0011 | 2401.7172 | 1933.1144 | 1858.0877 | -1728.0007 | -1537.099 | 2268.002 | -2230.7937 | 2074.6131 | -1845.4192
0.65 | 3040.4146 | 2914.1212 | 2697.5863 | 2403.6617 | 1976.2695 | 1894.1788 | -1753.4311 | -1562.3801 | 2268.002 | -2214.5404 | 2049.9881 | -1826.6248
0.66 | 3060.338 | 2924.9803 | 2695.1715 | 2405.6063 | 2019.8231 | 1930.487 | -1778.8132 | -1587.7002 | 2268.002 | -2197.4371 | 2024.7897 | -1807.2493
0.67 | 3080.2614 | 2935.8394 | 2692.7567 | 2407.5509 | 2063.7752 | 1967.0124 | -1804.147 | -1613.0591 | 2268.002 | -2179.4529 | 1998.9979 | -1787.2721
0.68 | 3100.1848 | 2946.6985 | 2690.3419 | 2409.4955 | 2108.1257 | 2003.755 | -1829.4325 | -1638.4569 | 2268.002 | -2160.555 | 1972.5913 | -1766.6713
0.69 | 3120.1082 | 2957.5576 | 2687.9271 | 2411.44 | 2152.8747 | 2040.7147 | -1854.6697 | -1663.8936 | 2258.3636 | -2140.7079 | 1945.5468 | -1745.4229
0.7 | 3140.0316 | 2968.4167 | 2685.5124 | 2413.3846 | 2198.0222 | 2077.8917 | -1879.8586 | -1689.3692 | 2242.4311 | -2119.8735 | 1917.8394 | -1723.5013
0.71 | 3143.3707 | 2976.5367 | 2682.9088 | 2416.2989 | 2231.7932 | 2113.3411 | -1904.8652 | -1715.5722 | 2213.5669 | -2096.0821 | 1889.3089 | -1701.5617
0.72 | 3146.7098 | 2984.6568 | 2680.3053 | 2419.2131 | 2265.6311 | 2148.9529 | -1929.8198 | -1741.8334 | 2183.735 | -2071.2744 | 1860.0623 | -1678.8712
0.73 | 3150.0489 | 2992.7768 | 2677.7017 | 2422.1274 | 2299.5357 | 2184.7271 | -1954.7222 | -1768.153 | 2152.8919 | -2045.4048 | 1830.0676 | -1655.396
0.74 | 3153.388 | 3000.8969 | 2675.0982 | 2425.0416 | 2333.5071 | 2220.6637 | -1979.5726 | -1794.5308 | 2120.9904 | -2018.4239 | 1799.2894 | -1631.0997
0.75 | 3156.727 | 3009.017 | 2672.4946 | 2427.9559 | 2367.5453 | 2256.7627 | -2004.371 | -1820.9669 | 2087.9787 | -1990.2777 | 1767.689 | -1605.9419
0.76 | 3160.0661 | 3017.137 | 2669.8911 | 2430.8701 | 2401.6502 | 2293.0242 | -2029.1172 | -1847.4613 | 2053.7999 | -1960.907 | 1735.2238 | -1579.8786
0.77 | 3163.4052 | 3025.2571 | 2667.2875 | 2433.7844 | 2435.822 | 2329.448 | -2053.8114 | -1874.014 | 2018.3913 | -1930.2468 | 1701.8465 | -1552.8613
0.78 | 3166.7443 | 3033.3772 | 2664.684 | 2436.6987 | 2470.0605 | 2366.0342 | -2078.4535 | -1900.625 | 1981.6837 | -1898.2253 | 1667.5046 | -1524.8361
0.79 | 3170.0833 | 3041.4972 | 2662.0804 | 2439.6129 | 2504.3658 | 2402.7828 | -2103.0435 | -1927.2942 | 1943.5998 | -1864.7628 | 1632.1397 | -1495.7434
0.8 | 3173.4224 | 3049.6173 | 2659.4769 | 2442.5272 | 2538.7379 | 2439.6938 | -2127.5815 | -1954.0217 | 1904.0535 | -1829.7704 | 1595.6861 | -1465.5163
0.81 | 3177.3802 | 3059.3885 | 2657.0301 | 2447.05 | 2573.6779 | 2478.1047 | -2152.1944 | -1982.1105 | 1863.3107 | -1794.1168 | 1558.1618 | -1435.0232
0.82 | 3181.3379 | 3069.1598 | 2654.5833 | 2451.5729 | 2608.6971 | 2516.711 | -2176.7583 | -2010.2898 | 1820.8818 | -1756.6751 | 1519.3866 | -1403.1909
0.83 | 3185.2957 | 3078.931 | 2652.1365 | 2456.0957 | 2643.7954 | 2555.5127 | -2201.2733 | -2038.5594 | 1776.6413 | -1717.315 | 1479.2646 | -1369.9203
0.84 | 3189.2535 | 3088.7022 | 2649.6897 | 2460.6186 | 2678.9729 | 2594.5099 | -2225.7394 | -2066.9196 | 1730.4455 | -1675.8878 | 1437.6856 | -1335.0982
0.85 | 3193.2112 | 3098.4735 | 2647.2429 | 2465.1414 | 2714.2295 | 2633.7024 | -2250.1565 | -2095.3702 | 1682.1284 | -1632.2222 | 1394.5217 | -1298.5938
0.86 | 3197.169 | 3108.2447 | 2644.7962 | 2469.6643 | 2749.5653 | 2673.0904 | -2274.5247 | -2123.9113 | 1631.4962 | -1586.1187 | 1349.6237 | -1260.2549
0.87 | 3201.1267 | 3118.0159 | 2642.3494 | 2474.1871 | 2784.9803 | 2712.6738 | -2298.844 | -2152.5428 | 1578.321 | -1537.3431 | 1302.8149 | -1219.9022
0.88 | 3205.0845 | 3127.7871 | 2639.9026 | 2478.71 | 2820.4743 | 2752.4527 | -2323.1143 | -2181.2648 | 1522.3308 | -1485.6166 | 1253.8843 | -1177.322
0.89 | 3209.0422 | 3137.5584 | 2637.4558 | 2483.2328 | 2856.0476 | 2792.427 | -2347.3357 | -2210.0772 | 1463.1966 | -1430.6028 | 1202.5757 | -1132.2561
0.9 | 3213 | 3147.3296 | 2635.009 | 2487.7557 | 2891.7 | 2832.5967 | -2371.5081 | -2238.9801 | 1400.5142 | -1371.8892 | 1148.5738 | -1084.3876
0.91 | 3213 | 3157.4543 | 2629.0831 | 2493.769 | 2923.83 | 2873.2834 | -2392.4656 | -2269.3298 | 1332.1363 | -1309.1066 | 1090.0395 | -1033.9372
0.92 | 3213 | 3167.5789 | 2623.1571 | 2499.7824 | 2955.96 | 2914.1726 | -2413.3045 | -2299.7998 | 1259.2337 | -1241.4323 | 1028.0634 | -979.7106
0.93 | 3213 | 3177.7036 | 2617.2311 | 2505.7957 | 2988.09 | 2955.2643 | -2434.0249 | -2330.39 | 1180.9687 | -1167.9952 | 961.9882 | -921.0291
0.94 | 3213 | 3187.8282 | 2611.3051 | 2511.8091 | 3020.22 | 2996.5585 | -2454.6268 | -2361.1005 | 1096.1935 | -1087.6055 | 890.9106 | -856.9651
0.95 | 3213 | 3197.9529 | 2605.3792 | 2517.8224 | 3052.35 | 3038.0552 | -2475.1102 | -2391.9313 | 1003.2589 | -998.5605 | 813.5294 | -786.1898
0.96 | 3213 | 3200.9623 | 2598.3651 | 2528.3197 | 3084.48 | 3072.9238 | -2494.4305 | -2427.1869 | 899.64 | -896.2694 | 727.5422 | -707.9295
0.97 | 3213 | 3203.9717 | 2591.3511 | 2538.817 | 3116.61 | 3107.8526 | -2513.6105 | -2462.6525 | 781.0961 | -778.9013 | 629.9702 | -617.1989
0.98 | 3213 | 3206.9811 | 2584.337 | 2549.3143 | 3148.74 | 3142.8415 | -2532.6503 | -2498.328 | 639.3789 | -638.1812 | 514.2766 | -507.3071
0.99 | 3213 | 3209.9906 | 2577.323 | 2559.8116 | 3180.87 | 3177.8907 | -2551.5497 | -2534.2135 | 453.2494 | -452.8249 | 363.5761 | -361.1059
1 | 3213 | 3213 | 2570.3089 | 2570.3089 | 3213 | 3213 | -2570.3089 | -2570.3089 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_50C_1.0pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 50 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1490 |  | VDC
Nom. Battery Voltage** |  |  |  | 1291.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1159 |  | VDC |  | Please select:
AC Voltage |  |  |  | 1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @50°C, 1159Vdc min. battery voltage and 1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2520.0022 | 2520.0018 | 2520.0019 | 2520.0015 | 0 | 0 | 0 | 0 | 2520.0022 | -2520.0018 | 2520.0019 | -2520.0015
0.01 | 2520.0022 | 2520.0018 | 2520.0019 | 2520.0015 | 0.0252 | 0.0252 | -0.0252 | -0.0252 | 2520.0022 | -2520.0018 | 2520.0019 | -2520.0015
0.05 | 2531.196 | 2528.8595 | 2529.5625 | 2527.5509 | 126.5598 | 126.443 | -126.4781 | -126.3775 | 2520.0022 | -2520.0018 | 2520.0019 | -2520.0018
0.1 | 2542.392 | 2537.7189 | 2539.125 | 2535.1017 | 254.2392 | 253.7719 | -253.9125 | -253.5102 | 2520.0022 | -2520.0018 | 2520.0019 | -2520.0018
0.15 | 2575.8286 | 2564.8879 | 2566.9775 | 2556.61 | 386.3743 | 384.7332 | -385.0466 | -383.4915 | 2520.0022 | -2520.0018 | 2520.0019 | -2520.0018
0.2 | 2609.2652 | 2592.0568 | 2594.83 | 2578.1184 | 521.853 | 518.4114 | -518.966 | -515.6237 | 2520.0022 | -2520.0018 | 2520.0019 | -2520.0018
0.25 | 2663.8702 | 2637.8926 | 2639.0173 | 2612.2248 | 665.9676 | 659.4732 | -659.7543 | -653.0562 | 2520.0022 | -2520.0018 | 2520.0019 | -2520.0018
0.3 | 2718.4753 | 2683.7284 | 2683.2046 | 2646.3313 | 815.5426 | 805.1185 | -804.9614 | -793.8994 | 2520.0022 | -2520.0018 | 2520.0019 | -2520.0018
0.35 | 2794.7168 | 2747.8913 | 2741.7887 | 2658.2978 | 978.1509 | 961.762 | -959.626 | -930.4042 | 2520.0022 | -2520.0018 | 2520.0019 | -2490.1597
0.4 | 2870.9582 | 2812.0542 | 2800.3727 | 2670.2644 | 1148.3833 | 1124.8217 | -1120.1491 | -1068.1058 | 2520.0022 | -2520.0018 | 2520.0019 | -2447.3377
0.45 | 2962.4301 | 2893.7739 | 2871.1617 | 2659.5727 | 1333.0936 | 1302.1983 | -1292.0228 | -1196.8077 | 2520.0022 | -2520.0018 | 2520.0019 | -2375.0744
0.5 | 3053.902 | 2975.4936 | 2941.9507 | 2648.8811 | 1526.951 | 1487.7468 | -1470.9753 | -1324.4405 | 2520.0022 | -2520.0018 | 2520.0019 | -2293.9983
0.51 | 3075.2671 | 2995.7026 | 2948.829 | 2649.9862 | 1568.3862 | 1527.8083 | -1503.9028 | -1351.4929 | 2520.0022 | -2520.0018 | 2520.0019 | -2279.4503
0.52 | 3096.6322 | 3015.9117 | 2955.7073 | 2651.0913 | 1610.2488 | 1568.2741 | -1536.9678 | -1378.5675 | 2520.0022 | -2520.0018 | 2520.0019 | -2264.4727
0.53 | 3117.9973 | 3036.1207 | 2962.5856 | 2652.1964 | 1652.5386 | 1609.144 | -1570.1704 | -1405.6641 | 2520.0022 | -2520.0018 | 2512.2656 | -2249.0563
0.54 | 3139.3624 | 3056.3298 | 2969.4639 | 2653.3015 | 1695.2557 | 1650.4181 | -1603.5105 | -1432.7828 | 2520.0022 | -2520.0018 | 2499.2939 | -2233.191
0.55 | 3160.7275 | 3076.5388 | 2976.3422 | 2654.4066 | 1738.4001 | 1692.0964 | -1636.9882 | -1459.9236 | 2520.0022 | -2520.0018 | 2485.7358 | -2216.8665
0.56 | 3182.0925 | 3096.7479 | 2983.2205 | 2655.5117 | 1781.9718 | 1734.1788 | -1670.6035 | -1487.0865 | 2520.0022 | -2520.0018 | 2471.5761 | -2200.0718
0.57 | 3203.4576 | 3116.9569 | 2990.0988 | 2656.6168 | 1825.9708 | 1776.6655 | -1704.3563 | -1514.2716 | 2520.0022 | -2520.0018 | 2456.7988 | -2182.7951
0.58 | 3224.8227 | 3137.166 | 2996.9771 | 2657.7219 | 1870.3972 | 1819.5563 | -1738.2467 | -1541.4787 | 2520.0022 | -2520.0018 | 2441.3869 | -2165.024
0.59 | 3246.1878 | 3157.375 | 3003.8554 | 2658.827 | 1915.2508 | 1862.8513 | -1772.2747 | -1568.7079 | 2520.0022 | -2520.0018 | 2425.3226 | -2146.7455
0.6 | 3267.5529 | 3177.5841 | 3010.7337 | 2659.9321 | 1960.5317 | 1906.5505 | -1806.4402 | -1595.9592 | 2520.0022 | -2520.0018 | 2408.587 | -2127.9457
0.61 | 3289.69 | 3189.6498 | 3008.0506 | 2662.0927 | 2006.7109 | 1945.6863 | -1834.9109 | -1623.8766 | 2520.0022 | -2520.0018 | 2383.5835 | -2109.446
0.62 | 3311.8271 | 3201.7154 | 3005.3675 | 2664.2533 | 2053.3328 | 1985.0636 | -1863.3278 | -1651.8371 | 2520.0022 | -2512.0717 | 2358.0168 | -2090.378
0.63 | 3333.9642 | 3213.7811 | 3002.6844 | 2666.414 | 2100.3975 | 2024.6821 | -1891.6912 | -1679.8408 | 2520.0022 | -2495.8067 | 2331.8701 | -2070.7241
0.64 | 3356.1013 | 3225.8467 | 3000.0013 | 2668.5746 | 2147.9049 | 2064.5419 | -1920.0008 | -1707.8878 | 2520.0022 | -2478.6597 | 2305.1257 | -2050.4658
0.65 | 3378.2385 | 3237.9124 | 2997.3182 | 2670.7353 | 2195.855 | 2104.6431 | -1948.2568 | -1735.9779 | 2520.0022 | -2460.6004 | 2277.7646 | -2029.5831
0.66 | 3400.3756 | 3249.9781 | 2994.635 | 2672.8959 | 2244.2479 | 2144.9855 | -1976.4591 | -1764.1113 | 2520.0022 | -2441.5967 | 2249.7663 | -2008.0547
0.67 | 3422.5127 | 3262.0437 | 2991.9519 | 2675.0565 | 2293.0835 | 2185.5693 | -2004.6078 | -1792.2879 | 2520.0022 | -2421.6144 | 2221.1087 | -1985.8579
0.68 | 3444.6498 | 3274.1094 | 2989.2688 | 2677.2172 | 2342.3619 | 2226.3944 | -2032.7028 | -1820.5077 | 2520.0022 | -2400.6167 | 2191.7681 | -1962.9681
0.69 | 3466.7869 | 3286.1751 | 2986.5857 | 2679.3778 | 2392.083 | 2267.4608 | -2060.7441 | -1848.7707 | 2509.2929 | -2378.5643 | 2161.7187 | -1939.3588
0.7 | 3488.9241 | 3298.2407 | 2983.9026 | 2681.5385 | 2442.2468 | 2308.7685 | -2088.7318 | -1877.0769 | 2491.5901 | -2355.415 | 2130.9327 | -1915.0015
0.71 | 3492.6341 | 3307.263 | 2981.0098 | 2684.7765 | 2479.7702 | 2348.1567 | -2116.5169 | -1906.1913 | 2459.5188 | -2328.9802 | 2099.2321 | -1890.6241
0.72 | 3496.3442 | 3316.2853 | 2978.1169 | 2688.0146 | 2517.3678 | 2387.7254 | -2144.2442 | -1935.3705 | 2426.3722 | -2301.416 | 2066.7359 | -1865.4124
0.73 | 3500.0543 | 3325.3076 | 2975.2241 | 2691.2526 | 2555.0396 | 2427.4746 | -2171.9136 | -1964.6144 | 2392.1021 | -2272.672 | 2033.4084 | -1839.3289
0.74 | 3503.7644 | 3334.3299 | 2972.3313 | 2694.4907 | 2592.7857 | 2467.4041 | -2199.5251 | -1993.9231 | 2356.656 | -2242.6932 | 1999.2104 | -1812.333
0.75 | 3507.4745 | 3343.3522 | 2969.4384 | 2697.7288 | 2630.6059 | 2507.5141 | -2227.0788 | -2023.2966 | 2319.9763 | -2211.4196 | 1964.0989 | -1784.3799
0.76 | 3511.1846 | 3352.3745 | 2966.5456 | 2700.9668 | 2668.5003 | 2547.8046 | -2254.5747 | -2052.7348 | 2281.9999 | -2178.7855 | 1928.0264 | -1755.4207
0.77 | 3514.8947 | 3361.3968 | 2963.6528 | 2704.2049 | 2706.4689 | 2588.2755 | -2282.0126 | -2082.2378 | 2242.657 | -2144.7187 | 1890.9405 | -1725.4014
0.78 | 3518.6047 | 3370.4191 | 2960.7599 | 2707.443 | 2744.5117 | 2628.9269 | -2309.3928 | -2111.8055 | 2201.8708 | -2109.1392 | 1852.7829 | -1694.2623
0.79 | 3522.3148 | 3379.4414 | 2957.8671 | 2710.681 | 2782.6287 | 2669.7587 | -2336.715 | -2141.438 | 2159.5553 | -2071.9586 | 1813.4886 | -1661.9371
0.8 | 3526.0249 | 3388.4637 | 2954.9743 | 2713.9191 | 2820.8199 | 2710.7709 | -2363.9794 | -2171.1353 | 2115.6149 | -2033.0782 | 1772.9846 | -1628.3514
0.81 | 3530.4224 | 3399.3206 | 2952.2556 | 2718.9445 | 2859.6422 | 2753.4497 | -2391.3271 | -2202.345 | 2070.3452 | -1993.4632 | 1731.2909 | -1594.4703
0.82 | 3534.8199 | 3410.1775 | 2949.537 | 2723.9699 | 2898.5523 | 2796.3456 | -2418.6203 | -2233.6553 | 2023.202 | -1951.8612 | 1688.2074 | -1559.101
0.83 | 3539.2174 | 3421.0344 | 2946.8183 | 2728.9952 | 2937.5505 | 2839.4586 | -2445.8592 | -2265.0661 | 1974.0459 | -1908.1278 | 1643.6274 | -1522.1336
0.84 | 3543.6149 | 3431.8914 | 2944.0997 | 2734.0206 | 2976.6366 | 2882.7887 | -2473.0437 | -2296.5773 | 1922.7173 | -1862.0976 | 1597.4284 | -1483.4424
0.85 | 3548.0125 | 3442.7483 | 2941.381 | 2739.046 | 3015.8106 | 2926.336 | -2500.1739 | -2328.1891 | 1869.0315 | -1813.5802 | 1549.4686 | -1442.882
0.86 | 3552.41 | 3453.6052 | 2938.6624 | 2744.0714 | 3055.0726 | 2970.1005 | -2527.2497 | -2359.9014 | 1812.7736 | -1762.3541 | 1499.5819 | -1400.2833
0.87 | 3556.8075 | 3464.4621 | 2935.9437 | 2749.0968 | 3094.4225 | 3014.0821 | -2554.2711 | -2391.7142 | 1753.69 | -1708.159 | 1447.5721 | -1355.4469
0.88 | 3561.205 | 3475.3191 | 2933.2251 | 2754.1222 | 3133.8604 | 3058.2808 | -2581.2381 | -2423.6275 | 1691.4786 | -1650.6851 | 1393.2047 | -1308.1356
0.89 | 3565.6025 | 3486.176 | 2930.5065 | 2759.1476 | 3173.3862 | 3102.6966 | -2608.1507 | -2455.6413 | 1625.774 | -1589.5586 | 1336.1953 | -1258.0624
0.9 | 3570 | 3497.0329 | 2927.7878 | 2764.173 | 3213 | 3147.3296 | -2635.009 | -2487.7557 | 1556.1269 | -1524.3213 | 1276.1931 | -1204.8751
0.91 | 3570 | 3508.2825 | 2921.2034 | 2770.8545 | 3248.7 | 3192.5371 | -2658.2951 | -2521.4776 | 1480.1514 | -1454.5629 | 1211.155 | -1148.8191
0.92 | 3570 | 3519.5321 | 2914.619 | 2777.536 | 3284.4 | 3237.9696 | -2681.4495 | -2555.3331 | 1399.1485 | -1379.3693 | 1142.2927 | -1088.5673
0.93 | 3570 | 3530.7817 | 2908.0346 | 2784.2175 | 3320.1 | 3283.627 | -2704.4722 | -2589.3222 | 1312.1875 | -1297.7724 | 1068.8758 | -1023.3656
0.94 | 3570 | 3542.0313 | 2901.4502 | 2790.899 | 3355.8 | 3329.5095 | -2727.3632 | -2623.445 | 1217.9928 | -1208.4506 | 989.9006 | -952.1834
0.95 | 3570 | 3553.281 | 2894.8657 | 2797.5805 | 3391.5 | 3375.6169 | -2750.1225 | -2657.7014 | 1114.7321 | -1109.5116 | 903.9215 | -873.5442
0.96 | 3570 | 3556.6248 | 2887.0724 | 2809.2441 | 3427.2 | 3414.3598 | -2771.5895 | -2696.8744 | 999.6 | -995.8549 | 808.3803 | -786.5884
0.97 | 3570 | 3559.9686 | 2879.279 | 2820.9078 | 3462.9 | 3453.1695 | -2792.9006 | -2736.2806 | 867.8845 | -865.4459 | 699.9669 | -685.7766
0.98 | 3570 | 3563.3124 | 2871.4856 | 2832.5715 | 3498.6 | 3492.0461 | -2814.0559 | -2775.92 | 710.421 | -709.0902 | 571.4184 | -563.6746
0.99 | 3570 | 3566.6562 | 2863.6922 | 2844.2351 | 3534.3 | 3530.9896 | -2835.0553 | -2815.7928 | 503.6105 | -503.1388 | 403.9735 | -401.2287
1 | 3570 | 3570 | 2855.8988 | 2855.8988 | 3570 | 3570 | -2855.8988 | -2855.8988 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_50C_1.1pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 50 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1490 |  | VDC
Nom. Battery Voltage** |  |  |  | 1291.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1159 |  | VDC |  | Please select:
AC Voltage |  |  |  | 1.1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @50°C, 1159Vdc min. battery voltage and 1.1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2520.0022 | 2520.0018 | 2520.0019 | 2520.0015 | 0 | 0 | 0 | 0 | 2520.0022 | -2520.0018 | 2520.0019 | -2520.0015
0.01 | 2520.0022 | 2520.0018 | 2520.0019 | 2520.0015 | 0.0252 | 0.0252 | -0.0252 | -0.0252 | 2520.0022 | -2520.0018 | 2520.0019 | -2520.0015
0.05 | 2531.196 | 2528.8595 | 2529.5625 | 2527.5509 | 126.5598 | 126.443 | -126.4781 | -126.3775 | 2520.0022 | -2520.0018 | 2520.0019 | -2520.0018
0.1 | 2542.392 | 2537.7189 | 2539.125 | 2535.1017 | 254.2392 | 253.7719 | -253.9125 | -253.5102 | 2520.0022 | -2520.0018 | 2520.0019 | -2520.0018
0.15 | 2575.8286 | 2564.8879 | 2566.9775 | 2556.61 | 386.3743 | 384.7332 | -385.0466 | -383.4915 | 2520.0022 | -2520.0018 | 2520.0019 | -2520.0018
0.2 | 2609.2652 | 2592.0568 | 2594.83 | 2578.1184 | 521.853 | 518.4114 | -518.966 | -515.6237 | 2520.0022 | -2520.0018 | 2520.0019 | -2520.0018
0.25 | 2663.8702 | 2637.8926 | 2639.0173 | 2612.2248 | 665.9676 | 659.4732 | -659.7543 | -653.0562 | 2520.0022 | -2520.0018 | 2520.0019 | -2520.0018
0.3 | 2718.4753 | 2683.7284 | 2683.2046 | 2646.3313 | 815.5426 | 805.1185 | -804.9614 | -793.8994 | 2520.0022 | -2520.0018 | 2520.0019 | -2520.0018
0.35 | 2794.7168 | 2747.8913 | 2741.7887 | 2658.2978 | 978.1509 | 961.762 | -959.626 | -930.4042 | 2520.0022 | -2520.0018 | 2520.0019 | -2490.1597
0.4 | 2870.9582 | 2812.0542 | 2800.3727 | 2670.2644 | 1148.3833 | 1124.8217 | -1120.1491 | -1068.1058 | 2520.0022 | -2520.0018 | 2520.0019 | -2447.3377
0.45 | 2962.4301 | 2893.7739 | 2871.1617 | 2659.5727 | 1333.0936 | 1302.1983 | -1292.0228 | -1196.8077 | 2520.0022 | -2520.0018 | 2520.0019 | -2375.0744
0.5 | 3053.902 | 2975.4936 | 2941.9507 | 2648.8811 | 1526.951 | 1487.7468 | -1470.9753 | -1324.4405 | 2520.0022 | -2520.0018 | 2520.0019 | -2293.9983
0.51 | 3075.2671 | 2995.7026 | 2948.829 | 2649.9862 | 1568.3862 | 1527.8083 | -1503.9028 | -1351.4929 | 2520.0022 | -2520.0018 | 2520.0019 | -2279.4503
0.52 | 3096.6322 | 3015.9117 | 2955.7073 | 2651.0913 | 1610.2488 | 1568.2741 | -1536.9678 | -1378.5675 | 2520.0022 | -2520.0018 | 2520.0019 | -2264.4727
0.53 | 3117.9973 | 3036.1207 | 2962.5856 | 2652.1964 | 1652.5386 | 1609.144 | -1570.1704 | -1405.6641 | 2520.0022 | -2520.0018 | 2512.2656 | -2249.0563
0.54 | 3139.3624 | 3056.3298 | 2969.4639 | 2653.3015 | 1695.2557 | 1650.4181 | -1603.5105 | -1432.7828 | 2520.0022 | -2520.0018 | 2499.2939 | -2233.191
0.55 | 3160.7275 | 3076.5388 | 2976.3422 | 2654.4066 | 1738.4001 | 1692.0964 | -1636.9882 | -1459.9236 | 2520.0022 | -2520.0018 | 2485.7358 | -2216.8665
0.56 | 3182.0925 | 3096.7479 | 2983.2205 | 2655.5117 | 1781.9718 | 1734.1788 | -1670.6035 | -1487.0865 | 2520.0022 | -2520.0018 | 2471.5761 | -2200.0718
0.57 | 3203.4576 | 3116.9569 | 2990.0988 | 2656.6168 | 1825.9708 | 1776.6655 | -1704.3563 | -1514.2716 | 2520.0022 | -2520.0018 | 2456.7988 | -2182.7951
0.58 | 3224.8227 | 3137.166 | 2996.9771 | 2657.7219 | 1870.3972 | 1819.5563 | -1738.2467 | -1541.4787 | 2520.0022 | -2520.0018 | 2441.3869 | -2165.024
0.59 | 3246.1878 | 3157.375 | 3003.8554 | 2658.827 | 1915.2508 | 1862.8513 | -1772.2747 | -1568.7079 | 2520.0022 | -2520.0018 | 2425.3226 | -2146.7455
0.6 | 3267.5529 | 3177.5841 | 3010.7337 | 2659.9321 | 1960.5317 | 1906.5505 | -1806.4402 | -1595.9592 | 2520.0022 | -2520.0018 | 2408.587 | -2127.9457
0.61 | 3289.69 | 3189.6498 | 3008.0506 | 2662.0927 | 2006.7109 | 1945.6863 | -1834.9109 | -1623.8766 | 2520.0022 | -2520.0018 | 2383.5835 | -2109.446
0.62 | 3311.8271 | 3201.7154 | 3005.3675 | 2664.2533 | 2053.3328 | 1985.0636 | -1863.3278 | -1651.8371 | 2520.0022 | -2512.0717 | 2358.0168 | -2090.378
0.63 | 3333.9642 | 3213.7811 | 3002.6844 | 2666.414 | 2100.3975 | 2024.6821 | -1891.6912 | -1679.8408 | 2520.0022 | -2495.8067 | 2331.8701 | -2070.7241
0.64 | 3356.1013 | 3225.8467 | 3000.0013 | 2668.5746 | 2147.9049 | 2064.5419 | -1920.0008 | -1707.8878 | 2520.0022 | -2478.6597 | 2305.1257 | -2050.4658
0.65 | 3378.2385 | 3237.9124 | 2997.3182 | 2670.7353 | 2195.855 | 2104.6431 | -1948.2568 | -1735.9779 | 2520.0022 | -2460.6004 | 2277.7646 | -2029.5831
0.66 | 3400.3756 | 3249.9781 | 2994.635 | 2672.8959 | 2244.2479 | 2144.9855 | -1976.4591 | -1764.1113 | 2520.0022 | -2441.5967 | 2249.7663 | -2008.0547
0.67 | 3422.5127 | 3262.0437 | 2991.9519 | 2675.0565 | 2293.0835 | 2185.5693 | -2004.6078 | -1792.2879 | 2520.0022 | -2421.6144 | 2221.1087 | -1985.8579
0.68 | 3444.6498 | 3274.1094 | 2989.2688 | 2677.2172 | 2342.3619 | 2226.3944 | -2032.7028 | -1820.5077 | 2520.0022 | -2400.6167 | 2191.7681 | -1962.9681
0.69 | 3466.7869 | 3286.1751 | 2986.5857 | 2679.3778 | 2392.083 | 2267.4608 | -2060.7441 | -1848.7707 | 2509.2929 | -2378.5643 | 2161.7187 | -1939.3588
0.7 | 3488.9241 | 3298.2407 | 2983.9026 | 2681.5385 | 2442.2468 | 2308.7685 | -2088.7318 | -1877.0769 | 2491.5901 | -2355.415 | 2130.9327 | -1915.0015
0.71 | 3492.6341 | 3307.263 | 2981.0098 | 2684.7765 | 2479.7702 | 2348.1567 | -2116.5169 | -1906.1913 | 2459.5188 | -2328.9802 | 2099.2321 | -1890.6241
0.72 | 3496.3442 | 3316.2853 | 2978.1169 | 2688.0146 | 2517.3678 | 2387.7254 | -2144.2442 | -1935.3705 | 2426.3722 | -2301.416 | 2066.7359 | -1865.4124
0.73 | 3500.0543 | 3325.3076 | 2975.2241 | 2691.2526 | 2555.0396 | 2427.4746 | -2171.9136 | -1964.6144 | 2392.1021 | -2272.672 | 2033.4084 | -1839.3289
0.74 | 3503.7644 | 3334.3299 | 2972.3313 | 2694.4907 | 2592.7857 | 2467.4041 | -2199.5251 | -1993.9231 | 2356.656 | -2242.6932 | 1999.2104 | -1812.333
0.75 | 3507.4745 | 3343.3522 | 2969.4384 | 2697.7288 | 2630.6059 | 2507.5141 | -2227.0788 | -2023.2966 | 2319.9763 | -2211.4196 | 1964.0989 | -1784.3799
0.76 | 3511.1846 | 3352.3745 | 2966.5456 | 2700.9668 | 2668.5003 | 2547.8046 | -2254.5747 | -2052.7348 | 2281.9999 | -2178.7855 | 1928.0264 | -1755.4207
0.77 | 3514.8947 | 3361.3968 | 2963.6528 | 2704.2049 | 2706.4689 | 2588.2755 | -2282.0126 | -2082.2378 | 2242.657 | -2144.7187 | 1890.9405 | -1725.4014
0.78 | 3518.6047 | 3370.4191 | 2960.7599 | 2707.443 | 2744.5117 | 2628.9269 | -2309.3928 | -2111.8055 | 2201.8708 | -2109.1392 | 1852.7829 | -1694.2623
0.79 | 3522.3148 | 3379.4414 | 2957.8671 | 2710.681 | 2782.6287 | 2669.7587 | -2336.715 | -2141.438 | 2159.5553 | -2071.9586 | 1813.4886 | -1661.9371
0.8 | 3526.0249 | 3388.4637 | 2954.9743 | 2713.9191 | 2820.8199 | 2710.7709 | -2363.9794 | -2171.1353 | 2115.6149 | -2033.0782 | 1772.9846 | -1628.3514
0.81 | 3530.4224 | 3399.3206 | 2952.2556 | 2718.9445 | 2859.6422 | 2753.4497 | -2391.3271 | -2202.345 | 2070.3452 | -1993.4632 | 1731.2909 | -1594.4703
0.82 | 3534.8199 | 3410.1775 | 2949.537 | 2723.9699 | 2898.5523 | 2796.3456 | -2418.6203 | -2233.6553 | 2023.202 | -1951.8612 | 1688.2074 | -1559.101
0.83 | 3539.2174 | 3421.0344 | 2946.8183 | 2728.9952 | 2937.5505 | 2839.4586 | -2445.8592 | -2265.0661 | 1974.0459 | -1908.1278 | 1643.6274 | -1522.1336
0.84 | 3543.6149 | 3431.8914 | 2944.0997 | 2734.0206 | 2976.6366 | 2882.7887 | -2473.0437 | -2296.5773 | 1922.7173 | -1862.0976 | 1597.4284 | -1483.4424
0.85 | 3548.0125 | 3442.7483 | 2941.381 | 2739.046 | 3015.8106 | 2926.336 | -2500.1739 | -2328.1891 | 1869.0315 | -1813.5802 | 1549.4686 | -1442.882
0.86 | 3552.41 | 3453.6052 | 2938.6624 | 2744.0714 | 3055.0726 | 2970.1005 | -2527.2497 | -2359.9014 | 1812.7736 | -1762.3541 | 1499.5819 | -1400.2833
0.87 | 3556.8075 | 3464.4621 | 2935.9437 | 2749.0968 | 3094.4225 | 3014.0821 | -2554.2711 | -2391.7142 | 1753.69 | -1708.159 | 1447.5721 | -1355.4469
0.88 | 3561.205 | 3475.3191 | 2933.2251 | 2754.1222 | 3133.8604 | 3058.2808 | -2581.2381 | -2423.6275 | 1691.4786 | -1650.6851 | 1393.2047 | -1308.1356
0.89 | 3565.6025 | 3486.176 | 2930.5065 | 2759.1476 | 3173.3862 | 3102.6966 | -2608.1507 | -2455.6413 | 1625.774 | -1589.5586 | 1336.1953 | -1258.0624
0.9 | 3570 | 3497.0329 | 2927.7878 | 2764.173 | 3213 | 3147.3296 | -2635.009 | -2487.7557 | 1556.1269 | -1524.3213 | 1276.1931 | -1204.8751
0.91 | 3570 | 3508.2825 | 2921.2034 | 2770.8545 | 3248.7 | 3192.5371 | -2658.2951 | -2521.4776 | 1480.1514 | -1454.5629 | 1211.155 | -1148.8191
0.92 | 3570 | 3519.5321 | 2914.619 | 2777.536 | 3284.4 | 3237.9696 | -2681.4495 | -2555.3331 | 1399.1485 | -1379.3693 | 1142.2927 | -1088.5673
0.93 | 3570 | 3530.7817 | 2908.0346 | 2784.2175 | 3320.1 | 3283.627 | -2704.4722 | -2589.3222 | 1312.1875 | -1297.7724 | 1068.8758 | -1023.3656
0.94 | 3570 | 3542.0313 | 2901.4502 | 2790.899 | 3355.8 | 3329.5095 | -2727.3632 | -2623.445 | 1217.9928 | -1208.4506 | 989.9006 | -952.1834
0.95 | 3570 | 3553.281 | 2894.8657 | 2797.5805 | 3391.5 | 3375.6169 | -2750.1225 | -2657.7014 | 1114.7321 | -1109.5116 | 903.9215 | -873.5442
0.96 | 3570 | 3556.6248 | 2887.0724 | 2809.2441 | 3427.2 | 3414.3598 | -2771.5895 | -2696.8744 | 999.6 | -995.8549 | 808.3803 | -786.5884
0.97 | 3570 | 3559.9686 | 2879.279 | 2820.9078 | 3462.9 | 3453.1695 | -2792.9006 | -2736.2806 | 867.8845 | -865.4459 | 699.9669 | -685.7766
0.98 | 3570 | 3563.3124 | 2871.4856 | 2832.5715 | 3498.6 | 3492.0461 | -2814.0559 | -2775.92 | 710.421 | -709.0902 | 571.4184 | -563.6746
0.99 | 3570 | 3566.6562 | 2863.6922 | 2844.2351 | 3534.3 | 3530.9896 | -2835.0553 | -2815.7928 | 503.6105 | -503.1388 | 403.9735 | -401.2287
1 | 3570 | 3570 | 2855.8988 | 2855.8988 | 3570 | 3570 | -2855.8988 | -2855.8988 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE