## CATL_25C_0.9pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 25 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V) |  |  |  | 1496 |  | VDC
Min. battery voltage |  |  |  | 1164 |  | VDC |  | Please select:
AC voltage |  |  |  | 0.9 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@min battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @25°C, 1164Vdc min. battery voltage and 0.9pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2268.0025 | 2268.002 | 2268.0025 | 2268.002 | 0 | 0 | 0 | 0 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.01 | 2268.0025 | 2268.002 | 2268.0025 | 2268.002 | 0.02268 | 0.02268 | -0.02268 | -0.02268 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.05 | 2280.6488 | 2278.2421 | 2280.3174 | 2277.7983 | 114.0324 | 113.9121 | -114.0159 | -113.8899 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.1 | 2293.2977 | 2288.4841 | 2292.6349 | 2287.5966 | 229.3298 | 228.8484 | -229.2635 | -228.7597 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.15 | 2330.8286 | 2319.4997 | 2328.1383 | 2315.2348 | 349.6243 | 347.925 | -349.2208 | -347.2852 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.2 | 2368.3595 | 2350.5153 | 2363.6418 | 2342.8729 | 473.6719 | 470.1031 | -472.7284 | -468.5746 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.25 | 2429.2871 | 2402.3843 | 2419.6669 | 2386.6701 | 607.3218 | 600.5961 | -604.9167 | -596.6675 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.3 | 2490.2146 | 2454.2533 | 2475.692 | 2430.4673 | 747.0644 | 736.276 | -742.7076 | -729.1402 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.35 | 2572.7261 | 2526.4941 | 2549.3166 | 2488.3277 | 900.4541 | 884.2729 | -892.2608 | -870.9147 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.4 | 2655.2376 | 2598.7348 | 2622.9413 | 2546.188 | 1062.095 | 1039.4939 | -1049.1765 | -1018.4752 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.45 | 2756.1178 | 2690.4304 | 2710.8697 | 2615.7073 | 1240.253 | 1210.6937 | -1219.8914 | -1177.0683 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.5 | 2856.9981 | 2782.126 | 2798.7981 | 2685.2267 | 1428.499 | 1391.063 | -1399.399 | -1342.6133 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.51 | 2880.5054 | 2804.4175 | 2817.9498 | 2702.0716 | 1469.0578 | 1430.2529 | -1437.1544 | -1378.0565 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.52 | 2904.0128 | 2826.7089 | 2837.1016 | 2718.9166 | 1510.0867 | 1469.8886 | -1475.2928 | -1413.8366 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.53 | 2927.5202 | 2849.0003 | 2856.2533 | 2735.7615 | 1551.5857 | 1509.9702 | -1513.8142 | -1449.9536 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.54 | 2951.0275 | 2871.2918 | 2875.405 | 2752.6065 | 1593.5549 | 1550.4976 | -1552.7187 | -1486.4075 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.55 | 2974.5349 | 2893.5832 | 2894.5567 | 2769.4514 | 1635.9942 | 1591.4708 | -1592.0062 | -1523.1983 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.56 | 2998.0423 | 2915.8746 | 2913.7085 | 2786.2964 | 1678.9037 | 1632.8898 | -1631.6767 | -1560.326 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.57 | 3021.5497 | 2938.1661 | 2932.8602 | 2803.1413 | 1722.2833 | 1674.7547 | -1671.7303 | -1597.7905 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.58 | 3045.057 | 2960.4575 | 2952.0119 | 2819.9863 | 1766.1331 | 1717.0654 | -1712.1669 | -1635.592 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.59 | 3068.5644 | 2982.7489 | 2971.1637 | 2836.8312 | 1810.453 | 1759.8219 | -1752.9866 | -1673.7304 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.6 | 3092.0718 | 3005.0404 | 2990.3154 | 2853.6762 | 1855.2431 | 1803.0242 | -1794.1892 | -1712.2057 | 2268.0025 | -2268.002 | 2268.0025 | -2268.002
0.61 | 3118.2152 | 3031.0495 | 3011.1599 | 2858.7316 | 1902.1113 | 1848.9402 | -1836.8076 | -1743.8263 | 2268.0025 | -2268.002 | 2268.0025 | -2265.263
0.62 | 3144.3587 | 3057.0586 | 3032.0045 | 2863.7871 | 1949.5024 | 1895.3763 | -1879.8428 | -1775.548 | 2268.0025 | -2268.002 | 2268.0025 | -2246.9325
0.63 | 3170.5022 | 3083.0677 | 3052.849 | 2868.8425 | 1997.4164 | 1942.3327 | -1923.2949 | -1807.3708 | 2268.0025 | -2268.002 | 2268.0025 | -2227.9291
0.64 | 3196.6457 | 3109.0768 | 3073.6935 | 2873.898 | 2045.8532 | 1989.8092 | -1967.1638 | -1839.2947 | 2268.0025 | -2268.002 | 2268.0025 | -2208.2311
0.65 | 3222.7891 | 3135.086 | 3094.538 | 2878.9534 | 2094.8129 | 2037.8059 | -2011.4497 | -1871.3197 | 2268.0025 | -2268.002 | 2268.0025 | -2187.8152
0.66 | 3248.9326 | 3161.0951 | 3115.3826 | 2884.0089 | 2144.2955 | 2086.3228 | -2056.1525 | -1903.4459 | 2268.0025 | -2268.002 | 2268.0025 | -2166.6567
0.67 | 3275.0761 | 3187.1042 | 3136.2271 | 2889.0643 | 2194.301 | 2135.3598 | -2101.2722 | -1935.6731 | 2268.0025 | -2268.002 | 2268.0025 | -2144.729
0.68 | 3301.2195 | 3213.1133 | 3157.0716 | 2894.1198 | 2244.8293 | 2184.9171 | -2146.8087 | -1968.0015 | 2268.0025 | -2268.002 | 2268.0025 | -2122.0037
0.69 | 3327.363 | 3239.1224 | 3177.9161 | 2899.1753 | 2295.8805 | 2234.9945 | -2192.7621 | -2000.4309 | 2268.0025 | -2268.002 | 2268.0025 | -2098.4502
0.7 | 3353.5065 | 3265.1316 | 3198.7607 | 2904.2307 | 2347.4545 | 2285.5921 | -2239.1325 | -2032.9615 | 2268.0025 | -2268.002 | 2268.0025 | -2074.0356
0.71 | 3373.5863 | 3284.224 | 3197.718 | 2907.3178 | 2395.2462 | 2331.7991 | -2270.3798 | -2064.1957 | 2268.0025 | -2268.002 | 2251.8384 | -2047.3381
0.72 | 3393.666 | 3303.3165 | 3196.6754 | 2910.405 | 2443.4395 | 2378.3879 | -2301.6063 | -2095.4916 | 2268.0025 | -2268.002 | 2218.4098 | -2019.7456
0.73 | 3413.7458 | 3322.409 | 3195.6327 | 2913.4921 | 2492.0344 | 2425.3585 | -2332.8119 | -2126.8492 | 2268.0025 | -2268.002 | 2184.0461 | -1991.2178
0.74 | 3433.8256 | 3341.5014 | 3194.5901 | 2916.5792 | 2541.0309 | 2472.7111 | -2363.9967 | -2158.2686 | 2268.0025 | -2247.5168 | 2148.7032 | -1961.7112
0.75 | 3453.9054 | 3360.5939 | 3193.5474 | 2919.6663 | 2590.429 | 2520.4454 | -2395.1606 | -2189.7497 | 2268.0025 | -2222.8239 | 2112.3331 | -1931.1778
0.76 | 3473.9851 | 3379.6864 | 3192.5048 | 2922.7535 | 2640.2287 | 2568.5616 | -2426.3036 | -2221.2926 | 2257.8231 | -2196.5362 | 2074.8825 | -1899.5649
0.77 | 3494.0649 | 3398.7788 | 3191.4621 | 2925.8406 | 2690.43 | 2617.0597 | -2457.4258 | -2252.8972 | 2229.3667 | -2168.5701 | 2036.2929 | -1866.8147
0.78 | 3514.1447 | 3417.8713 | 3190.4195 | 2928.9277 | 2741.0328 | 2665.9396 | -2488.5272 | -2284.5636 | 2199.0797 | -2138.8338 | 1996.4991 | -1832.863
0.79 | 3534.2245 | 3436.9638 | 3189.3768 | 2932.0148 | 2792.0373 | 2715.2014 | -2519.6077 | -2316.2917 | 2166.8572 | -2107.226 | 1955.4287 | -1797.6383
0.8 | 3554.3042 | 3456.0562 | 3188.3342 | 2935.1019 | 2843.4434 | 2764.845 | -2550.6673 | -2348.0816 | 2132.5825 | -2073.6337 | 1913.0005 | -1761.0612
0.81 | 3558.1339 | 3464.623 | 3185.1099 | 2940.2654 | 2882.0885 | 2806.3446 | -2579.939 | -2381.6149 | 2086.596 | -2031.7584 | 1867.8436 | -1724.2595
0.82 | 3561.9636 | 3473.1897 | 3181.8857 | 2945.4288 | 2920.8102 | 2848.0156 | -2609.1463 | -2415.2516 | 2038.738 | -1987.9271 | 1821.1953 | -1685.856
0.83 | 3565.7933 | 3481.7565 | 3178.6615 | 2950.5922 | 2959.6084 | 2889.8579 | -2638.289 | -2448.9915 | 1988.869 | -1941.9963 | 1772.941 | -1645.7323
0.84 | 3569.623 | 3490.3232 | 3175.4372 | 2955.7556 | 2998.4833 | 2931.8715 | -2667.3673 | -2482.8347 | 1936.8289 | -1893.8019 | 1722.9491 | -1603.7528
0.85 | 3573.4527 | 3498.89 | 3172.213 | 2960.9191 | 3037.4348 | 2974.0565 | -2696.3811 | -2516.7812 | 1882.433 | -1843.1547 | 1671.0669 | -1559.7609
0.86 | 3577.2824 | 3507.4567 | 3168.9888 | 2966.0825 | 3076.4628 | 3016.4128 | -2725.3303 | -2550.831 | 1825.4659 | -1789.8342 | 1617.1161 | -1513.5742
0.87 | 3581.1121 | 3516.0234 | 3165.7645 | 2971.2459 | 3115.5675 | 3058.9404 | -2754.2152 | -2584.984 | 1765.6735 | -1733.5814 | 1560.8857 | -1464.9779
0.88 | 3584.9418 | 3524.5902 | 3162.5403 | 2976.4094 | 3154.7488 | 3101.6394 | -2783.0355 | -2619.2402 | 1702.753 | -1674.0876 | 1502.1234 | -1413.7161
0.89 | 3588.7715 | 3533.1569 | 3159.3161 | 2981.5728 | 3194.0066 | 3144.5097 | -2811.7913 | -2653.5998 | 1636.3381 | -1610.9801 | 1440.5234 | -1359.4795
0.9 | 3592.6012 | 3541.7237 | 3156.0918 | 2986.7362 | 3233.341 | 3187.5513 | -2840.4827 | -2688.0626 | 1565.9785 | -1543.8016 | 1375.7085 | -1301.8881
0.91 | 3602.3272 | 3551.2028 | 3149.3454 | 2993.0382 | 3278.1178 | 3231.5946 | -2865.9043 | -2723.6648 | 1493.5546 | -1472.358 | 1305.7446 | -1240.9383
0.92 | 3612.0533 | 3560.682 | 3142.5989 | 2999.3402 | 3323.089 | 3275.8274 | -2891.191 | -2759.393 | 1415.63 | -1395.4966 | 1231.6422 | -1175.4965
0.93 | 3621.7794 | 3570.1612 | 3135.8524 | 3005.6422 | 3368.2548 | 3320.2499 | -2916.3427 | -2795.2473 | 1331.2195 | -1312.2467 | 1152.6124 | -1104.7524
0.94 | 3631.5055 | 3579.6403 | 3129.1059 | 3011.9442 | 3413.6151 | 3364.8619 | -2941.3595 | -2831.2276 | 1238.9769 | -1221.2818 | 1067.571 | -1027.5984
0.95 | 3641.2315 | 3589.1195 | 3122.3594 | 3018.2462 | 3459.17 | 3409.6635 | -2966.2414 | -2867.3339 | 1136.9742 | -1120.7022 | 974.9564 | -942.4471
0.96 | 3652.703 | 3611.0134 | 3113.6495 | 3030.359 | 3506.5949 | 3466.5729 | -2989.1036 | -2909.1447 | 1022.7568 | -1011.0838 | 871.8219 | -848.5005
0.97 | 3664.1745 | 3632.9073 | 3104.9397 | 3042.4718 | 3554.2493 | 3523.9201 | -3011.7915 | -2951.1977 | 890.7788 | -883.1776 | 754.8261 | -739.6399
0.98 | 3675.646 | 3654.8012 | 3096.2299 | 3054.5846 | 3602.1331 | 3581.7051 | -3034.3053 | -2993.4929 | 731.4443 | -727.2962 | 616.142 | -607.8547
0.99 | 3687.1174 | 3676.695 | 3087.52 | 3066.6974 | 3650.2463 | 3639.9281 | -3056.6448 | -3036.0304 | 520.1319 | -518.6617 | 435.5483 | -432.6109
1 | 3698.5889 | 3698.5889 | 3078.8102 | 3078.8102 | 3698.5889 | 3698.5889 | -3078.8102 | -3078.8102 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited

## CATL_25C_1.0pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 25 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V) |  |  |  | 1496 |  | VDC
Min. battery voltage |  |  |  | 1164 |  | VDC |  | Please select:
AC voltage |  |  |  | 1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@min battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @25°C, 1164Vdc min. battery voltage and 1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2520.0028 | 2520.0023 | 2520.0027 | 2520.0022 | 0 | 0 | 0 | 0 | 2520.0028 | -2520.0023 | 2520.0027 | -2520.0022
0.01 | 2520.0028 | 2520.0023 | 2520.0027 | 2520.0022 | 0.0252 | 0.0252 | -0.0252 | -0.0252 | 2520.0028 | -2520.0023 | 2520.0027 | -2520.0022
0.05 | 2534.0543 | 2531.3801 | 2533.686 | 2530.887 | 126.7027 | 126.569 | -126.6843 | -126.5444 | 2520.0028 | -2520.0023 | 2520.0028 | -2520.0023
0.1 | 2548.1085 | 2542.7601 | 2547.3721 | 2541.774 | 254.8109 | 254.276 | -254.7372 | -254.1774 | 2520.0028 | -2520.0023 | 2520.0028 | -2520.0023
0.15 | 2589.8096 | 2577.2219 | 2586.8204 | 2572.4831 | 388.4714 | 386.5833 | -388.0231 | -385.8725 | 2520.0028 | -2520.0023 | 2520.0028 | -2520.0023
0.2 | 2631.5106 | 2611.6837 | 2626.2687 | 2603.1921 | 526.3021 | 522.3367 | -525.2537 | -520.6384 | 2520.0028 | -2520.0023 | 2520.0028 | -2520.0023
0.25 | 2699.2078 | 2669.3159 | 2688.5188 | 2651.8557 | 674.802 | 667.329 | -672.1297 | -662.9639 | 2520.0028 | -2520.0023 | 2520.0028 | -2520.0023
0.3 | 2766.9051 | 2726.9482 | 2750.7689 | 2700.5193 | 830.0715 | 818.0844 | -825.2307 | -810.1558 | 2520.0028 | -2520.0023 | 2520.0028 | -2520.0023
0.35 | 2858.5845 | 2807.2156 | 2832.574 | 2764.8085 | 1000.5046 | 982.5255 | -991.4009 | -967.683 | 2520.0028 | -2520.0023 | 2520.0028 | -2520.0023
0.4 | 2950.264 | 2887.4831 | 2914.3792 | 2829.0977 | 1180.1056 | 1154.9932 | -1165.7517 | -1131.6391 | 2520.0028 | -2520.0023 | 2520.0028 | -2520.0023
0.45 | 3062.3531 | 2989.3671 | 3012.0774 | 2906.3415 | 1378.0589 | 1345.2152 | -1355.4348 | -1307.8537 | 2520.0028 | -2520.0023 | 2520.0028 | -2520.0023
0.5 | 3174.4423 | 3091.2512 | 3109.7757 | 2983.5852 | 1587.2211 | 1545.6256 | -1554.8878 | -1491.7926 | 2520.0028 | -2520.0023 | 2520.0028 | -2520.0023
0.51 | 3200.5616 | 3116.0194 | 3131.0554 | 3002.3018 | 1632.2864 | 1589.1699 | -1596.8382 | -1531.1739 | 2520.0028 | -2520.0023 | 2520.0028 | -2520.0023
0.52 | 3226.6809 | 3140.7877 | 3152.3351 | 3021.0184 | 1677.8741 | 1633.2096 | -1639.2142 | -1570.9296 | 2520.0028 | -2520.0023 | 2520.0028 | -2520.0023
0.53 | 3252.8002 | 3165.5559 | 3173.6148 | 3039.735 | 1723.9841 | 1677.7446 | -1682.0158 | -1611.0596 | 2520.0028 | -2520.0023 | 2520.0028 | -2520.0023
0.54 | 3278.9195 | 3190.3242 | 3194.8945 | 3058.4516 | 1770.6165 | 1722.7751 | -1725.243 | -1651.5639 | 2520.0028 | -2520.0023 | 2520.0028 | -2520.0023
0.55 | 3305.0388 | 3215.0925 | 3216.1742 | 3077.1682 | 1817.7713 | 1768.3008 | -1768.8958 | -1692.4425 | 2520.0028 | -2520.0023 | 2520.0028 | -2520.0023
0.56 | 3331.1581 | 3239.8607 | 3237.4539 | 3095.8848 | 1865.4485 | 1814.322 | -1812.9742 | -1733.6955 | 2520.0028 | -2520.0023 | 2520.0028 | -2520.0023
0.57 | 3357.2774 | 3264.629 | 3258.7336 | 3114.6015 | 1913.6481 | 1860.8385 | -1857.4781 | -1775.3228 | 2520.0028 | -2520.0023 | 2520.0028 | -2520.0023
0.58 | 3383.3967 | 3289.3972 | 3280.0133 | 3133.3181 | 1962.3701 | 1907.8504 | -1902.4077 | -1817.3245 | 2520.0028 | -2520.0023 | 2520.0028 | -2520.0023
0.59 | 3409.516 | 3314.1655 | 3301.293 | 3152.0347 | 2011.6144 | 1955.3576 | -1947.7628 | -1859.7005 | 2520.0028 | -2520.0023 | 2520.0028 | -2520.0023
0.6 | 3435.6353 | 3338.9337 | 3322.5727 | 3170.7513 | 2061.3812 | 2003.3602 | -1993.5436 | -1902.4508 | 2520.0028 | -2520.0023 | 2520.0028 | -2520.0023
0.61 | 3464.6836 | 3367.8328 | 3345.7332 | 3176.3685 | 2113.457 | 2054.378 | -2040.8973 | -1937.5848 | 2520.0028 | -2520.0023 | 2520.0028 | -2516.9589
0.62 | 3493.7319 | 3396.7318 | 3368.8938 | 3181.9856 | 2166.1138 | 2105.9737 | -2088.7142 | -1972.8311 | 2520.0028 | -2520.0023 | 2520.0028 | -2496.5917
0.63 | 3522.7802 | 3425.6308 | 3392.0544 | 3187.6028 | 2219.3515 | 2158.1474 | -2136.9943 | -2008.1898 | 2520.0028 | -2520.0023 | 2520.0028 | -2475.4768
0.64 | 3551.8285 | 3454.5298 | 3415.215 | 3193.22 | 2273.1702 | 2210.8991 | -2185.7376 | -2043.6608 | 2520.0028 | -2520.0023 | 2520.0028 | -2453.5901
0.65 | 3580.8768 | 3483.4288 | 3438.3756 | 3198.8372 | 2327.5699 | 2264.2288 | -2234.9441 | -2079.2442 | 2520.0028 | -2520.0023 | 2520.0028 | -2430.9058
0.66 | 3609.9251 | 3512.3279 | 3461.5362 | 3204.4543 | 2382.5506 | 2318.1364 | -2284.6139 | -2114.9399 | 2520.0028 | -2520.0023 | 2520.0028 | -2407.3963
0.67 | 3638.9734 | 3541.2269 | 3484.6968 | 3210.0715 | 2438.1122 | 2372.622 | -2334.7468 | -2150.7479 | 2520.0028 | -2520.0023 | 2520.0028 | -2383.0322
0.68 | 3668.0217 | 3570.1259 | 3507.8574 | 3215.6887 | 2494.2548 | 2427.6856 | -2385.343 | -2186.6683 | 2520.0028 | -2520.0023 | 2520.0028 | -2357.7819
0.69 | 3697.07 | 3599.0249 | 3531.0179 | 3221.3058 | 2550.9783 | 2483.3272 | -2436.4024 | -2222.701 | 2520.0028 | -2520.0023 | 2520.0028 | -2331.6113
0.7 | 3726.1183 | 3627.924 | 3554.1785 | 3226.923 | 2608.2828 | 2539.5468 | -2487.925 | -2258.8461 | 2520.0028 | -2520.0023 | 2520.0028 | -2304.484
0.71 | 3748.4292 | 3649.1378 | 3553.02 | 3230.3531 | 2661.3847 | 2590.8878 | -2522.6442 | -2293.5507 | 2520.0028 | -2520.0023 | 2502.0427 | -2274.8201
0.72 | 3770.74 | 3670.3517 | 3551.8615 | 3233.7833 | 2714.9328 | 2642.6532 | -2557.3403 | -2328.324 | 2520.0028 | -2520.0023 | 2464.8998 | -2244.1617
0.73 | 3793.0509 | 3691.5655 | 3550.703 | 3237.2134 | 2768.9272 | 2694.8428 | -2592.0132 | -2363.1658 | 2520.0028 | -2520.0023 | 2426.7178 | -2212.4643
0.74 | 3815.3618 | 3712.7794 | 3549.5445 | 3240.6436 | 2823.3677 | 2747.4567 | -2626.6629 | -2398.0762 | 2520.0028 | -2497.2409 | 2387.448 | -2179.6791
0.75 | 3837.6726 | 3733.9932 | 3548.386 | 3244.0737 | 2878.2545 | 2800.4949 | -2661.2895 | -2433.0553 | 2520.0028 | -2469.8044 | 2347.0367 | -2145.7531
0.76 | 3859.9835 | 3755.2071 | 3547.2275 | 3247.5038 | 2933.5874 | 2853.9574 | -2695.8929 | -2468.1029 | 2508.6923 | -2440.5957 | 2305.425 | -2110.6277
0.77 | 3882.2943 | 3776.4209 | 3546.069 | 3250.934 | 2989.3666 | 2907.8441 | -2730.4731 | -2503.2192 | 2477.0742 | -2409.5223 | 2262.5477 | -2074.2385
0.78 | 3904.6052 | 3797.6348 | 3544.9105 | 3254.3641 | 3045.5921 | 2962.1551 | -2765.0302 | -2538.404 | 2443.4219 | -2376.4821 | 2218.3324 | -2036.5144
0.79 | 3926.9161 | 3818.8486 | 3543.752 | 3257.7942 | 3102.2637 | 3016.8904 | -2799.5641 | -2573.6575 | 2407.6191 | -2341.3622 | 2172.6986 | -1997.3759
0.8 | 3949.2269 | 3840.0625 | 3542.5935 | 3261.2244 | 3159.3815 | 3072.05 | -2834.0748 | -2608.9795 | 2369.5361 | -2304.0375 | 2125.5561 | -1956.7346
0.81 | 3953.4821 | 3849.5811 | 3539.011 | 3266.9615 | 3202.3205 | 3118.1607 | -2866.5989 | -2646.2388 | 2318.44 | -2257.5094 | 2075.3818 | -1915.8438
0.82 | 3957.7373 | 3859.0997 | 3535.4286 | 3272.6987 | 3245.3446 | 3164.4618 | -2899.0514 | -2683.6129 | 2265.2645 | -2208.8079 | 2023.5503 | -1873.1733
0.83 | 3961.9926 | 3868.6183 | 3531.8461 | 3278.4358 | 3288.4538 | 3210.9532 | -2931.4322 | -2721.1017 | 2209.8544 | -2157.7737 | 1969.9344 | -1828.5915
0.84 | 3966.2478 | 3878.1369 | 3528.2636 | 3284.1729 | 3331.6481 | 3257.635 | -2963.7414 | -2758.7053 | 2152.0321 | -2104.2243 | 1914.3878 | -1781.9476
0.85 | 3970.503 | 3887.6555 | 3524.6811 | 3289.9101 | 3374.9275 | 3304.5072 | -2995.979 | -2796.4236 | 2091.5922 | -2047.9496 | 1856.741 | -1733.0677
0.86 | 3974.7582 | 3897.1741 | 3521.0986 | 3295.6472 | 3418.2921 | 3351.5697 | -3028.1448 | -2834.2566 | 2028.2954 | -1988.7047 | 1796.7956 | -1681.7491
0.87 | 3979.0134 | 3906.6927 | 3517.5162 | 3301.3844 | 3461.7417 | 3398.8227 | -3060.2391 | -2872.2044 | 1961.8594 | -1926.2016 | 1734.3174 | -1627.7532
0.88 | 3983.2686 | 3916.2113 | 3513.9337 | 3307.1215 | 3505.2764 | 3446.266 | -3092.2616 | -2910.2669 | 1891.9478 | -1860.0973 | 1669.026 | -1570.7957
0.89 | 3987.5238 | 3925.7299 | 3510.3512 | 3312.8586 | 3548.8962 | 3493.8996 | -3124.2126 | -2948.4442 | 1818.1535 | -1789.9779 | 1600.5816 | -1510.5328
0.9 | 3991.7791 | 3935.2485 | 3506.7687 | 3318.5958 | 3592.6012 | 3541.7237 | -3156.0918 | -2986.7362 | 1739.9762 | -1715.3351 | 1528.565 | -1446.5424
0.91 | 4002.5858 | 3945.7809 | 3499.2726 | 3325.598 | 3642.3531 | 3590.6606 | -3184.3381 | -3026.2942 | 1659.5051 | -1635.9533 | 1450.8273 | -1378.8204
0.92 | 4013.3926 | 3956.3133 | 3491.7765 | 3332.6002 | 3692.3212 | 3639.8083 | -3212.4344 | -3065.9922 | 1572.9222 | -1550.5518 | 1368.4913 | -1306.1072
0.93 | 4024.1993 | 3966.8458 | 3484.2804 | 3339.6025 | 3742.5054 | 3689.1665 | -3240.3808 | -3105.8303 | 1479.1328 | -1458.0519 | 1280.6804 | -1227.5027
0.94 | 4035.0061 | 3977.3782 | 3476.7843 | 3346.6047 | 3792.9057 | 3738.7355 | -3268.1772 | -3145.8084 | 1376.6409 | -1356.9798 | 1186.1899 | -1141.776
0.95 | 4045.8128 | 3987.9106 | 3469.2882 | 3353.6069 | 3843.5222 | 3788.515 | -3295.8238 | -3185.9266 | 1263.3047 | -1245.2247 | 1083.2849 | -1047.1634
0.96 | 4058.5589 | 4012.2371 | 3459.6106 | 3367.0656 | 3896.2166 | 3851.7476 | -3321.2262 | -3232.383 | 1136.3965 | -1123.4264 | 968.691 | -942.7784
0.97 | 4071.305 | 4036.5636 | 3449.933 | 3380.5242 | 3949.1658 | 3915.4667 | -3346.435 | -3279.1085 | 989.7543 | -981.3085 | 838.6957 | -821.8221
0.98 | 4084.0511 | 4060.8902 | 3440.2554 | 3393.9829 | 4002.3701 | 3979.6724 | -3371.4503 | -3326.1032 | 812.7159 | -808.1069 | 684.6022 | -675.3941
0.99 | 4096.7972 | 4085.2167 | 3430.5778 | 3407.4416 | 4055.8292 | 4044.3645 | -3396.272 | -3373.3671 | 577.9244 | -576.2907 | 483.9426 | -480.6788
1 | 4109.5432 | 4109.5432 | 3420.9002 | 3420.9002 | 4109.5432 | 4109.5432 | -3420.9002 | -3420.9002 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited

## CATL_25C_1.1pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 25 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V) |  |  |  | 1496 |  | VDC
Min. battery voltage |  |  |  | 1164 |  | VDC |  | Please select:
AC voltage |  |  |  | 1.1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@min battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @25°C, 1164Vdc min. battery voltage and 1.1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2520.0034 | 2520.0026 | 2520.0033 | 2520.0025 | 0 | 0 | 0 | 0 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0025
0.01 | 2520.0034 | 2520.0026 | 2520.0033 | 2520.0025 | 0.0252 | 0.0252 | -0.0252 | -0.0252 | 2520.0034 | -2520.0026 | 2520.0033 | -2520.0025
0.05 | 2537.1288 | 2533.1213 | 2536.6993 | 2532.6105 | 126.8564 | 126.6561 | -126.835 | -126.6305 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.1 | 2554.2577 | 2546.2425 | 2553.3987 | 2545.221 | 255.4258 | 254.6243 | -255.3399 | -254.5221 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.15 | 2605.2855 | 2585.931 | 2601.739 | 2581.7046 | 390.7928 | 387.8896 | -390.2609 | -387.2557 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.2 | 2656.3132 | 2625.6194 | 2650.0793 | 2618.1881 | 531.2626 | 525.1239 | -530.0159 | -523.6376 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.25 | 2736.8794 | 2693.4311 | 2725.9743 | 2675.8298 | 684.2199 | 673.3578 | -681.4936 | -668.9574 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.3 | 2817.4457 | 2761.2429 | 2801.8693 | 2733.4714 | 845.2337 | 828.3729 | -840.5608 | -820.0414 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.35 | 2923.0544 | 2854.2582 | 2900.368 | 2808.1679 | 1023.069 | 998.9904 | -1015.1288 | -982.8588 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.4 | 3028.6631 | 2947.2735 | 2998.8667 | 2882.8644 | 1211.4652 | 1178.9094 | -1199.5467 | -1153.1458 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.45 | 3154.484 | 3062.8784 | 3113.3006 | 2973.3807 | 1419.5178 | 1378.2953 | -1400.9853 | -1338.0213 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.5 | 3280.3049 | 3178.4834 | 3227.7344 | 3063.897 | 1640.1524 | 1589.2417 | -1613.8672 | -1531.9485 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.51 | 3308.6562 | 3206.5096 | 3252.0651 | 3085.6164 | 1687.4147 | 1635.3199 | -1658.5532 | -1573.6643 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.52 | 3337.0075 | 3234.5357 | 3276.3957 | 3107.3357 | 1735.2439 | 1681.9586 | -1703.7258 | -1615.8146 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.53 | 3365.3589 | 3262.5618 | 3300.7263 | 3129.0551 | 1783.6402 | 1729.1578 | -1749.3849 | -1658.3992 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.54 | 3393.7102 | 3290.588 | 3325.0569 | 3150.7745 | 1832.6035 | 1776.9175 | -1795.5307 | -1701.4182 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.55 | 3422.0615 | 3318.6141 | 3349.3876 | 3172.4939 | 1882.1338 | 1825.2378 | -1842.1632 | -1744.8716 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.56 | 3450.4129 | 3346.6402 | 3373.7182 | 3194.2133 | 1932.2312 | 1874.1185 | -1889.2822 | -1788.7594 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.57 | 3478.7642 | 3374.6664 | 3398.0488 | 3215.9327 | 1982.8956 | 1923.5598 | -1936.8878 | -1833.0816 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.58 | 3507.1155 | 3402.6925 | 3422.3794 | 3237.6521 | 2034.127 | 1973.5617 | -1984.9801 | -1877.8382 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.59 | 3535.4668 | 3430.7187 | 3446.7101 | 3259.3714 | 2085.9254 | 2024.124 | -2033.5589 | -1923.0291 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.6 | 3563.8182 | 3458.7448 | 3471.0407 | 3281.0908 | 2138.2909 | 2075.2469 | -2082.6244 | -1968.6545 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.61 | 3594.6572 | 3492.1485 | 3498.2025 | 3305.5673 | 2192.7409 | 2130.2106 | -2133.9035 | -2016.3961 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.62 | 3625.4963 | 3525.5522 | 3525.3642 | 3330.0439 | 2247.8077 | 2185.8423 | -2185.7258 | -2064.6272 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.63 | 3656.3353 | 3558.9558 | 3552.526 | 3354.5204 | 2303.4913 | 2242.1422 | -2238.0914 | -2113.3478 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.64 | 3687.1744 | 3592.3595 | 3579.6878 | 3378.9969 | 2359.7916 | 2299.1101 | -2291.0002 | -2162.558 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.65 | 3718.0134 | 3625.7632 | 3606.8495 | 3403.4734 | 2416.7087 | 2356.7461 | -2344.4522 | -2212.2577 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.66 | 3748.8525 | 3659.1669 | 3634.0113 | 3427.9499 | 2474.2426 | 2415.0502 | -2398.4475 | -2262.4469 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.67 | 3779.6915 | 3692.5706 | 3661.1731 | 3452.4264 | 2532.3933 | 2474.0223 | -2452.986 | -2313.1257 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.68 | 3810.5306 | 3725.9743 | 3688.3348 | 3476.9029 | 2591.1608 | 2533.6625 | -2508.0677 | -2364.294 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.69 | 3841.3696 | 3759.378 | 3715.4966 | 3501.3795 | 2650.545 | 2593.9708 | -2563.6927 | -2415.9518 | 2520.0034 | -2520.0026 | 2520.0034 | -2520.0026
0.7 | 3872.2087 | 3792.7816 | 3742.6584 | 3525.856 | 2710.5461 | 2654.9471 | -2619.8609 | -2468.0992 | 2520.0034 | -2520.0026 | 2520.0034 | -2517.9648
0.71 | 3904.9878 | 3829.5345 | 3759.6485 | 3530.8053 | 2772.5413 | 2718.9695 | -2669.3504 | -2506.8718 | 2520.0034 | -2520.0026 | 2520.0034 | -2486.399
0.72 | 3937.7669 | 3866.2874 | 3776.6386 | 3535.7546 | 2835.1922 | 2783.727 | -2719.1798 | -2545.7433 | 2520.0034 | -2520.0026 | 2520.0034 | -2453.722
0.73 | 3970.5461 | 3903.0404 | 3793.6287 | 3540.704 | 2898.4986 | 2849.2195 | -2769.349 | -2584.7139 | 2520.0034 | -2520.0026 | 2520.0034 | -2419.884
0.74 | 4003.3252 | 3939.7933 | 3810.6189 | 3545.6533 | 2962.4607 | 2915.447 | -2819.858 | -2623.7835 | 2520.0034 | -2520.0026 | 2520.0034 | -2384.8308
0.75 | 4036.1043 | 3976.5462 | 3827.609 | 3550.6026 | 3027.0783 | 2982.4096 | -2870.7067 | -2662.952 | 2520.0034 | -2520.0026 | 2520.0034 | -2348.5029
0.76 | 4068.8835 | 4013.2991 | 3844.5991 | 3555.552 | 3092.3514 | 3050.1073 | -2921.8953 | -2702.2195 | 2520.0034 | -2520.0026 | 2498.6937 | -2310.8353
0.77 | 4101.6626 | 4050.052 | 3861.5892 | 3560.5013 | 3158.2802 | 3118.54 | -2973.4237 | -2741.586 | 2520.0034 | -2520.0026 | 2463.8634 | -2271.7561
0.78 | 4134.4417 | 4086.8049 | 3878.5794 | 3565.4506 | 3224.8646 | 3187.7078 | -3025.2919 | -2781.0515 | 2520.0034 | -2520.0026 | 2427.1355 | -2231.186
0.79 | 4167.2209 | 4123.5578 | 3895.5695 | 3570.4 | 3292.1045 | 3257.6107 | -3077.4999 | -2820.616 | 2520.0034 | -2520.0026 | 2388.4003 | -2189.0367
0.8 | 4200 | 4160.3107 | 3896.8529 | 3575.3493 | 3360 | 3328.2486 | -3117.4823 | -2860.2795 | 2520 | -2496.1864 | 2338.1117 | -2145.2096
0.81 | 4200 | 4164.2796 | 3892.9121 | 3580.7193 | 3402 | 3373.0665 | -3153.2588 | -2900.3827 | 2463.0055 | -2442.058 | 2282.92 | -2099.8408
0.82 | 4200 | 4168.2486 | 3888.9714 | 3586.0893 | 3444 | 3417.9638 | -3188.9566 | -2940.5933 | 2403.9268 | -2385.7534 | 2225.9054 | -2052.5467
0.83 | 4200 | 4172.2175 | 3885.0307 | 3591.4593 | 3486 | 3462.9405 | -3224.5755 | -2980.9113 | 2342.6062 | -2327.1102 | 2166.9279 | -2003.1845
0.84 | 4200 | 4176.1864 | 3881.09 | 3596.8293 | 3528 | 3507.9966 | -3260.1156 | -3021.3366 | 2278.8629 | -2265.9419 | 2105.8266 | -1951.5907
0.85 | 4200 | 4180.1553 | 3877.1492 | 3602.1994 | 3570 | 3553.132 | -3295.5768 | -3061.8694 | 2212.4873 | -2202.0335 | 2042.4151 | -1897.5763
0.86 | 4200 | 4184.1243 | 3873.2085 | 3607.5694 | 3612 | 3598.3469 | -3330.9593 | -3102.5096 | 2143.2349 | -2135.1337 | 1976.4752 | -1840.9211
0.87 | 4200 | 4188.0932 | 3869.2678 | 3612.9394 | 3654 | 3643.6411 | -3366.263 | -3143.2572 | 2070.8172 | -2064.9466 | 1907.7491 | -1781.366
0.88 | 4200 | 4192.0621 | 3865.327 | 3618.3094 | 3696 | 3689.0147 | -3401.4878 | -3184.1122 | 1994.8895 | -1991.1192 | 1835.9286 | -1718.6017
0.89 | 4200 | 4196.0311 | 3861.3863 | 3623.6794 | 3738 | 3734.4677 | -3436.6338 | -3225.0746 | 1915.0342 | -1913.2245 | 1760.6397 | -1652.2548
0.9 | 4200 | 4200 | 3857.4456 | 3629.0494 | 3780 | 3780 | -3471.701 | -3266.1444 | 1830.7376 | -1830.7376 | 1681.4216 | -1581.866
0.91 | 4200 | 4200 | 3849.1999 | 3638.5913 | 3822 | 3822 | -3502.7719 | -3311.118 | 1741.3546 | -1741.3546 | 1595.91 | -1508.59
0.92 | 4200 | 4200 | 3840.9542 | 3648.1331 | 3864 | 3864 | -3533.6778 | -3356.2825 | 1646.0571 | -1646.0571 | 1505.3405 | -1429.7704
0.93 | 4200 | 4200 | 3832.7084 | 3657.675 | 3906 | 3906 | -3564.4189 | -3401.6378 | 1543.75 | -1543.75 | 1408.7485 | -1344.4133
0.94 | 4200 | 4200 | 3824.4627 | 3667.2169 | 3948 | 3948 | -3594.995 | -3447.1839 | 1432.9327 | -1432.9327 | 1304.8089 | -1251.1607
0.95 | 4200 | 4200 | 3816.217 | 3676.7588 | 3990 | 3990 | -3625.4062 | -3492.9208 | 1311.4496 | -1311.4496 | 1191.6134 | -1148.0676
0.96 | 4200 | 4200 | 3805.5717 | 3695.207 | 4032 | 4032 | -3653.3488 | -3547.3987 | 1176 | -1176 | 1065.5601 | -1034.658
0.97 | 4200 | 4200 | 3794.9263 | 3713.6553 | 4074 | 4074 | -3681.0785 | -3602.2456 | 1021.0406 | -1021.0406 | 922.5652 | -902.8078
0.98 | 4200 | 4200 | 3784.2809 | 3732.1035 | 4116 | 4116 | -3708.5953 | -3657.4614 | 835.7894 | -835.7894 | 753.0624 | -742.6792
0.99 | 4200 | 4200 | 3773.6356 | 3748.1857 | 4158 | 4158 | -3735.8992 | -3710.7039 | 592.4829 | -592.4829 | 532.3368 | -528.7467
1 | 4200 | 4200 | 3762.9902 | 3762.9902 | 4200 | 4200 | -3762.9902 | -3762.9902 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited

## CATL_35C_0.9pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 35 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1495 |  | VDC
Nom. Battery Voltage** |  |  |  | 1296.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1164 |  | VDC |  | Please select:
AC Voltage |  |  |  | 0.9 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @35°C, 1164Vdc min. battery voltage and 0.9pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2268.0025 | 2268.002 | 2268.0021 | 2268.0017 | 0 | 0 | 0 | 0 | 2268.0025 | -2268.002 | 2268.0021 | -2268.0017
0.01 | 2268.0025 | 2268.002 | 2268.0021 | 2268.0017 | 0.02268 | 0.02268 | -0.02268 | -0.02268 | 2268.0025 | -2268.002 | 2268.0021 | -2268.0017
0.05 | 2280.3404 | 2277.8881 | 2278.727 | 2276.4845 | 114.017 | 113.8944 | -113.9364 | -113.8242 | 2268.0025 | -2268.002 | 2268.0021 | -2268.002
0.1 | 2292.6808 | 2287.7763 | 2289.4541 | 2284.9691 | 229.2681 | 228.7776 | -228.9454 | -228.4969 | 2268.0025 | -2268.002 | 2268.0021 | -2268.002
0.15 | 2329.3208 | 2317.8205 | 2320.5194 | 2309.074 | 349.3981 | 347.6731 | -348.0779 | -346.3611 | 2268.0025 | -2268.002 | 2268.0021 | -2268.002
0.2 | 2365.9608 | 2347.8648 | 2351.5847 | 2333.179 | 473.1922 | 469.573 | -470.3169 | -466.6358 | 2268.0025 | -2268.002 | 2268.0021 | -2268.002
0.25 | 2425.7703 | 2398.1178 | 2400.9615 | 2371.3307 | 606.4426 | 599.5295 | -600.2404 | -592.8327 | 2268.0025 | -2268.002 | 2268.0021 | -2268.002
0.3 | 2485.5798 | 2448.3708 | 2450.3382 | 2409.4824 | 745.6739 | 734.5112 | -735.1015 | -722.8447 | 2268.0025 | -2268.002 | 2268.0021 | -2268.002
0.35 | 2567.298 | 2518.4051 | 2514.9602 | 2460.1479 | 898.5543 | 881.4418 | -880.2361 | -861.0517 | 2268.0025 | -2268.002 | 2268.0021 | -2268.002
0.4 | 2649.0163 | 2588.4394 | 2579.5823 | 2510.8133 | 1059.6065 | 1035.3758 | -1031.8329 | -1004.3253 | 2268.0025 | -2268.002 | 2268.0021 | -2268.002
0.45 | 2746.4961 | 2677.6155 | 2656.6673 | 2558.897 | 1235.9233 | 1204.927 | -1195.5003 | -1151.5036 | 2268.0025 | -2268.002 | 2268.0021 | -2268.002
0.5 | 2843.9759 | 2766.7915 | 2733.7524 | 2606.9807 | 1421.988 | 1383.3958 | -1366.8762 | -1303.4903 | 2268.0025 | -2268.002 | 2268.0021 | -2257.7115
0.51 | 2866.6013 | 2788.1333 | 2750.8871 | 2613.3898 | 1461.9667 | 1421.948 | -1402.9524 | -1332.8288 | 2268.0025 | -2268.002 | 2268.0021 | -2247.971
0.52 | 2889.2267 | 2809.475 | 2768.0219 | 2619.7989 | 1502.3979 | 1460.927 | -1439.3714 | -1362.2954 | 2268.0025 | -2268.002 | 2268.0021 | -2237.7438
0.53 | 2911.852 | 2830.8168 | 2785.1567 | 2626.208 | 1543.2816 | 1500.3329 | -1476.133 | -1391.8902 | 2268.0025 | -2268.002 | 2268.0021 | -2227.0182
0.54 | 2934.4774 | 2852.1585 | 2802.2915 | 2632.6171 | 1584.6178 | 1540.1656 | -1513.2374 | -1421.6132 | 2268.0025 | -2268.002 | 2268.0021 | -2215.7817
0.55 | 2957.1028 | 2873.5003 | 2819.4262 | 2639.0262 | 1626.4065 | 1580.4252 | -1550.6844 | -1451.4644 | 2268.0025 | -2268.002 | 2268.0021 | -2204.0214
0.56 | 2979.7281 | 2894.842 | 2836.561 | 2645.4353 | 1668.6477 | 1621.1115 | -1588.4742 | -1481.4437 | 2268.0025 | -2268.002 | 2268.0021 | -2191.7236
0.57 | 3002.3535 | 2916.1838 | 2853.6958 | 2651.8443 | 1711.3415 | 1662.2248 | -1626.6066 | -1511.5513 | 2268.0025 | -2268.002 | 2268.0021 | -2178.8738
0.58 | 3024.9789 | 2937.5255 | 2870.8306 | 2658.2534 | 1754.4877 | 1703.7648 | -1665.0817 | -1541.787 | 2268.0025 | -2268.002 | 2268.0021 | -2165.457
0.59 | 3047.6042 | 2958.8673 | 2887.9654 | 2664.6625 | 1798.0865 | 1745.7317 | -1703.8996 | -1572.1509 | 2268.0025 | -2268.002 | 2268.0021 | -2151.4572
0.6 | 3070.2296 | 2980.209 | 2905.1001 | 2671.0716 | 1842.1378 | 1788.1254 | -1743.0601 | -1602.643 | 2268.0025 | -2268.002 | 2268.0021 | -2136.8573
0.61 | 3095.4295 | 3005.6854 | 2913.62 | 2674.2072 | 1888.212 | 1833.4681 | -1777.3082 | -1631.2664 | 2268.0025 | -2268.002 | 2268.0021 | -2119.0455
0.62 | 3120.6295 | 3031.1618 | 2922.1399 | 2677.3427 | 1934.7903 | 1879.3203 | -1811.7267 | -1659.9525 | 2268.0025 | -2268.002 | 2268.0021 | -2100.6479
0.63 | 3145.8295 | 3056.6381 | 2930.6598 | 2680.4782 | 1981.8726 | 1925.682 | -1846.3157 | -1688.7013 | 2268.0025 | -2268.002 | 2268.0021 | -2081.6463
0.64 | 3171.0294 | 3082.1145 | 2939.1797 | 2683.6137 | 2029.4588 | 1972.5533 | -1881.075 | -1717.5128 | 2268.0025 | -2268.002 | 2258.3919 | -2062.0215
0.65 | 3196.2294 | 3107.5909 | 2947.6995 | 2686.7493 | 2077.5491 | 2019.9341 | -1916.0047 | -1746.387 | 2268.0025 | -2268.002 | 2240.0577 | -2041.7527
0.66 | 3221.4294 | 3133.0672 | 2956.2194 | 2689.8848 | 2126.1434 | 2067.8244 | -1951.1048 | -1775.324 | 2268.0025 | -2268.002 | 2220.906 | -2020.8179
0.67 | 3246.6293 | 3158.5436 | 2964.7393 | 2693.0203 | 2175.2416 | 2116.2242 | -1986.3753 | -1804.3236 | 2268.0025 | -2268.002 | 2200.9071 | -1999.1935
0.68 | 3271.8293 | 3184.02 | 2973.2592 | 2696.1559 | 2224.8439 | 2165.1336 | -2021.8162 | -1833.386 | 2268.0025 | -2268.002 | 2180.0296 | -1976.8541
0.69 | 3297.0292 | 3209.4964 | 2981.7791 | 2699.2914 | 2274.9502 | 2214.5525 | -2057.4276 | -1862.5111 | 2268.0025 | -2268.002 | 2158.2396 | -1953.7724
0.7 | 3322.2292 | 3234.9727 | 2990.2989 | 2702.4269 | 2325.5604 | 2264.4809 | -2093.2093 | -1891.6988 | 2268.0025 | -2268.002 | 2135.5006 | -1929.9188
0.71 | 3338.9733 | 3249.4445 | 2987.8233 | 2705.3646 | 2370.6711 | 2307.1056 | -2121.3545 | -1920.8089 | 2268.0025 | -2268.002 | 2104.0302 | -1905.1223
0.72 | 3355.7175 | 3263.9163 | 2985.3477 | 2708.3023 | 2416.1166 | 2350.0197 | -2149.4503 | -1949.9776 | 2268.0025 | -2265.0733 | 2071.7538 | -1879.4915
0.73 | 3372.4617 | 3278.3881 | 2982.872 | 2711.2399 | 2461.897 | 2393.2233 | -2177.4966 | -1979.2052 | 2268.0025 | -2240.605 | 2038.6354 | -1852.9892
0.74 | 3389.2058 | 3292.8599 | 2980.3964 | 2714.1776 | 2508.0123 | 2436.7163 | -2205.4933 | -2008.4914 | 2268.0025 | -2214.8002 | 2004.6351 | -1825.5745
0.75 | 3405.95 | 3307.3317 | 2977.9207 | 2717.1153 | 2554.4625 | 2480.4988 | -2233.4405 | -2037.8365 | 2252.8241 | -2187.5943 | 1969.7094 | -1797.2028
0.76 | 3422.6941 | 3321.8035 | 2975.4451 | 2720.053 | 2601.2475 | 2524.5706 | -2261.3383 | -2067.2402 | 2224.4879 | -2158.9167 | 1933.8104 | -1767.8252
0.77 | 3439.4383 | 3336.2752 | 2972.9694 | 2722.9906 | 2648.3675 | 2568.9319 | -2289.1865 | -2096.7028 | 2194.5126 | -2128.69 | 1896.885 | -1737.3875
0.78 | 3456.1824 | 3350.747 | 2970.4938 | 2725.9283 | 2695.8223 | 2613.5827 | -2316.9851 | -2126.2241 | 2162.8082 | -2096.8289 | 1858.8742 | -1705.8301
0.79 | 3472.9266 | 3365.2188 | 2968.0181 | 2728.866 | 2743.612 | 2658.5229 | -2344.7343 | -2155.8041 | 2129.275 | -2063.2387 | 1819.7122 | -1673.0864
0.8 | 3489.6707 | 3379.6906 | 2965.5425 | 2731.8036 | 2791.7366 | 2703.7525 | -2372.434 | -2185.4429 | 2093.8024 | -2027.8144 | 1779.3255 | -1639.0822
0.81 | 3493.3991 | 3388.7417 | 2962.6532 | 2736.4843 | 2829.6533 | 2744.8808 | -2399.7491 | -2216.5523 | 2048.6336 | -1987.2594 | 1737.3883 | -1604.7561
0.82 | 3497.1274 | 3397.7928 | 2959.7639 | 2741.1649 | 2867.6445 | 2786.1901 | -2427.0064 | -2247.7553 | 2001.6282 | -1944.7727 | 1694.0609 | -1568.9428
0.83 | 3500.8558 | 3406.8439 | 2956.8745 | 2745.8456 | 2905.7103 | 2827.6805 | -2454.2059 | -2279.0518 | 1952.6492 | -1900.2128 | 1649.2364 | -1531.5322
0.84 | 3504.5842 | 3415.895 | 2953.9852 | 2750.5263 | 2943.8507 | 2869.3518 | -2481.3476 | -2310.4421 | 1901.5397 | -1853.4182 | 1602.7922 | -1492.3981
0.85 | 3508.3125 | 3424.9461 | 2951.0959 | 2755.2069 | 2982.0656 | 2911.2042 | -2508.4315 | -2341.9259 | 1848.1183 | -1804.2023 | 1554.5862 | -1451.3953
0.86 | 3512.0409 | 3433.9972 | 2948.2066 | 2759.8876 | 3020.3552 | 2953.2376 | -2535.4577 | -2373.5033 | 1792.1735 | -1752.3483 | 1504.4522 | -1408.3542
0.87 | 3515.7692 | 3443.0483 | 2945.3173 | 2764.5682 | 3058.7192 | 2995.452 | -2562.426 | -2405.1743 | 1733.4561 | -1697.6009 | 1452.1938 | -1363.0751
0.88 | 3519.4976 | 3452.0994 | 2942.428 | 2769.2489 | 3097.1579 | 3037.8475 | -2589.3366 | -2436.939 | 1671.6687 | -1639.6564 | 1397.5758 | -1315.3203
0.89 | 3523.226 | 3461.1505 | 2939.5386 | 2773.9295 | 3135.6711 | 3080.424 | -2616.1894 | -2468.7973 | 1606.452 | -1578.148 | 1340.3136 | -1264.8024
0.9 | 3526.9543 | 3470.2016 | 2936.6493 | 2778.6102 | 3174.2589 | 3123.1815 | -2642.9844 | -2500.7492 | 1537.3637 | -1512.6258 | 1280.0558 | -1211.1681
0.91 | 3530.4679 | 3480.2006 | 2930.4956 | 2784.9082 | 3212.7258 | 3166.9825 | -2666.751 | -2534.2664 | 1463.7611 | -1442.9199 | 1215.0076 | -1154.6459
0.92 | 3533.9816 | 3490.1995 | 2924.3418 | 2791.2062 | 3251.263 | 3210.9835 | -2690.3945 | -2567.9097 | 1385.0323 | -1367.8733 | 1146.1032 | -1093.9249
0.93 | 3537.4952 | 3500.1984 | 2918.188 | 2797.5042 | 3289.8705 | 3255.1845 | -2713.9149 | -2601.6789 | 1300.24 | -1286.5312 | 1072.6078 | -1028.2493
0.94 | 3541.0088 | 3510.1973 | 2912.0343 | 2803.8021 | 3328.5483 | 3299.5855 | -2737.3122 | -2635.574 | 1208.1017 | -1197.5896 | 993.5117 | -956.5856
0.95 | 3544.5225 | 3520.1963 | 2905.8805 | 2810.1001 | 3367.2963 | 3344.1865 | -2760.5865 | -2669.5951 | 1106.7768 | -1099.1809 | 907.3609 | -877.4535
0.96 | 3546.258 | 3526.797 | 2897.8668 | 2821.2425 | 3404.4077 | 3385.7251 | -2781.9522 | -2708.3928 | 992.9522 | -987.5032 | 811.4027 | -789.9479
0.97 | 3547.9935 | 3533.3978 | 2889.8532 | 2832.3849 | 3441.5537 | 3427.3958 | -2803.1576 | -2747.4134 | 862.5347 | -858.9864 | 702.5375 | -688.5667
0.98 | 3549.729 | 3539.9985 | 2881.8395 | 2843.5273 | 3478.7344 | 3469.1985 | -2824.2027 | -2786.6568 | 706.3871 | -704.4508 | 573.4788 | -565.8548
0.99 | 3551.4645 | 3546.5993 | 2873.8258 | 2854.6697 | 3515.9498 | 3511.1333 | -2845.0876 | -2826.123 | 500.9957 | -500.3094 | 405.403 | -402.7007
1 | 3553.2 | 3553.2 | 2865.8121 | 2865.8121 | 3553.2 | 3553.2 | -2865.8121 | -2865.8121 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_35C_1.0pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 35 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1495 |  | VDC
Nom. Battery Voltage** |  |  |  | 1296.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1164 |  | VDC |  | Please select:
AC Voltage |  |  |  | 1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @35°C, 1164Vdc min. battery voltage and 1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2520.0027 | 2520.0022 | 2520.0024 | 2520.0019 | 0 | 0 | 0 | 0 | 2520.0027 | -2520.0022 | 2520.0024 | -2520.0019
0.01 | 2520.0027 | 2520.0022 | 2520.0024 | 2520.0019 | 0.0252 | 0.0252 | -0.0252 | -0.0252 | 2520.0027 | -2520.0022 | 2520.0024 | -2520.0019
0.05 | 2533.7116 | 2530.9868 | 2531.9189 | 2529.4273 | 126.6856 | 126.5493 | -126.5959 | -126.4714 | 2520.0027 | -2520.0022 | 2520.0024 | -2520.0022
0.1 | 2547.4232 | 2541.9736 | 2543.8379 | 2538.8545 | 254.7423 | 254.1974 | -254.3838 | -253.8855 | 2520.0027 | -2520.0022 | 2520.0024 | -2520.0022
0.15 | 2588.1342 | 2575.3561 | 2578.3549 | 2565.6378 | 388.2201 | 386.3034 | -386.7532 | -384.8457 | 2520.0027 | -2520.0022 | 2520.0024 | -2520.0022
0.2 | 2628.8453 | 2608.7387 | 2612.8719 | 2592.4211 | 525.7691 | 521.7477 | -522.5744 | -518.4842 | 2520.0027 | -2520.0022 | 2520.0024 | -2520.0022
0.25 | 2695.3003 | 2664.5753 | 2667.7349 | 2634.8119 | 673.8251 | 666.1438 | -666.9337 | -658.703 | 2520.0027 | -2520.0022 | 2520.0024 | -2520.0022
0.3 | 2761.7553 | 2720.412 | 2722.598 | 2677.2027 | 828.5266 | 816.1236 | -816.7794 | -803.1608 | 2520.0027 | -2520.0022 | 2520.0024 | -2520.0022
0.35 | 2852.5534 | 2798.2279 | 2794.4003 | 2733.4976 | 998.3937 | 979.3798 | -978.0401 | -956.7242 | 2520.0027 | -2520.0022 | 2520.0024 | -2520.0022
0.4 | 2943.3515 | 2876.0438 | 2866.2025 | 2789.7925 | 1177.3406 | 1150.4175 | -1146.481 | -1115.917 | 2520.0027 | -2520.0022 | 2520.0024 | -2520.0022
0.45 | 3051.6624 | 2975.1283 | 2951.8526 | 2843.2189 | 1373.2481 | 1338.8077 | -1328.3337 | -1279.4485 | 2520.0027 | -2520.0022 | 2520.0024 | -2520.0022
0.5 | 3159.9733 | 3074.2128 | 3037.5026 | 2896.6452 | 1579.9866 | 1537.1064 | -1518.7513 | -1448.3226 | 2520.0027 | -2520.0022 | 2520.0024 | -2508.5683
0.51 | 3185.1125 | 3097.9259 | 3056.5413 | 2903.7664 | 1624.4074 | 1579.9422 | -1558.836 | -1480.9209 | 2520.0027 | -2520.0022 | 2520.0024 | -2497.7455
0.52 | 3210.2518 | 3121.6389 | 3075.5799 | 2910.8876 | 1669.331 | 1623.2522 | -1599.3016 | -1513.6616 | 2520.0027 | -2520.0022 | 2520.0024 | -2486.382
0.53 | 3235.3911 | 3145.352 | 3094.6185 | 2918.0089 | 1714.7573 | 1667.0365 | -1640.1478 | -1546.5447 | 2520.0027 | -2520.0022 | 2520.0024 | -2474.4646
0.54 | 3260.5304 | 3169.065 | 3113.6572 | 2925.1301 | 1760.6864 | 1711.2951 | -1681.3749 | -1579.5702 | 2520.0027 | -2520.0022 | 2520.0024 | -2461.9797
0.55 | 3285.6697 | 3192.7781 | 3132.6958 | 2932.2513 | 1807.1184 | 1756.0279 | -1722.9827 | -1612.7382 | 2520.0027 | -2520.0022 | 2520.0024 | -2448.9126
0.56 | 3310.809 | 3216.4911 | 3151.7345 | 2939.3725 | 1854.0531 | 1801.235 | -1764.9713 | -1646.0486 | 2520.0027 | -2520.0022 | 2520.0024 | -2435.2484
0.57 | 3335.9483 | 3240.2042 | 3170.7731 | 2946.4937 | 1901.4905 | 1846.9164 | -1807.3407 | -1679.5014 | 2520.0027 | -2520.0022 | 2520.0024 | -2420.9709
0.58 | 3361.0876 | 3263.9172 | 3189.8118 | 2953.6149 | 1949.4308 | 1893.072 | -1850.0908 | -1713.0967 | 2520.0027 | -2520.0022 | 2520.0024 | -2406.0634
0.59 | 3386.2269 | 3287.6303 | 3208.8504 | 2960.7362 | 1997.8739 | 1939.7019 | -1893.2217 | -1746.8343 | 2520.0027 | -2520.0022 | 2520.0024 | -2390.508
0.6 | 3411.3662 | 3311.3434 | 3227.889 | 2967.8574 | 2046.8197 | 1986.806 | -1936.7334 | -1780.7144 | 2520.0027 | -2520.0022 | 2520.0024 | -2374.2859
0.61 | 3439.3662 | 3339.6504 | 3237.3556 | 2971.3413 | 2098.0134 | 2037.1868 | -1974.7869 | -1812.5182 | 2520.0027 | -2520.0022 | 2520.0024 | -2354.495
0.62 | 3467.3661 | 3367.9575 | 3246.8221 | 2974.8252 | 2149.767 | 2088.1337 | -2013.0297 | -1844.3916 | 2520.0027 | -2520.0022 | 2520.0024 | -2334.0532
0.63 | 3495.3661 | 3396.2646 | 3256.2886 | 2978.3091 | 2202.0806 | 2139.6467 | -2051.4618 | -1876.3348 | 2520.0027 | -2520.0022 | 2520.0024 | -2312.9404
0.64 | 3523.366 | 3424.5717 | 3265.7552 | 2981.7931 | 2254.9543 | 2191.7259 | -2090.0833 | -1908.3476 | 2520.0027 | -2520.0022 | 2509.3243 | -2291.135
0.65 | 3551.366 | 3452.8787 | 3275.2217 | 2985.277 | 2308.3879 | 2244.3712 | -2128.8941 | -1940.43 | 2520.0027 | -2520.0022 | 2488.953 | -2268.6141
0.66 | 3579.3659 | 3481.1858 | 3284.6882 | 2988.7609 | 2362.3815 | 2297.5826 | -2167.8942 | -1972.5822 | 2520.0027 | -2520.0022 | 2467.6733 | -2245.3532
0.67 | 3607.3659 | 3509.4929 | 3294.1548 | 2992.2448 | 2416.9352 | 2351.3602 | -2207.0837 | -2004.804 | 2520.0027 | -2520.0022 | 2445.4524 | -2221.3261
0.68 | 3635.3659 | 3537.8 | 3303.6213 | 2995.7287 | 2472.0488 | 2405.704 | -2246.4625 | -2037.0955 | 2520.0027 | -2520.0022 | 2422.2552 | -2196.5046
0.69 | 3663.3658 | 3566.1071 | 3313.0879 | 2999.2127 | 2527.7224 | 2460.6139 | -2286.0306 | -2069.4567 | 2520.0027 | -2520.0022 | 2398.044 | -2170.8582
0.7 | 3691.3658 | 3594.4141 | 3322.5544 | 3002.6966 | 2583.956 | 2516.0899 | -2325.7881 | -2101.8876 | 2520.0027 | -2520.0022 | 2372.7784 | -2144.3543
0.71 | 3709.9704 | 3610.4939 | 3319.8037 | 3005.9607 | 2634.079 | 2563.4507 | -2357.0606 | -2134.2321 | 2520.0027 | -2520.0022 | 2337.8113 | -2116.8025
0.72 | 3728.575 | 3626.5737 | 3317.053 | 3009.2247 | 2684.574 | 2611.133 | -2388.2781 | -2166.6418 | 2520.0027 | -2516.7481 | 2301.9487 | -2088.3239
0.73 | 3747.1796 | 3642.6534 | 3314.3022 | 3012.4888 | 2735.4411 | 2659.137 | -2419.4406 | -2199.1168 | 2520.0027 | -2489.5611 | 2265.1504 | -2058.8769
0.74 | 3765.7842 | 3658.7332 | 3311.5515 | 3015.7529 | 2786.6803 | 2707.4626 | -2450.5481 | -2231.6571 | 2520.0027 | -2460.8891 | 2227.3723 | -2028.4161
0.75 | 3784.3888 | 3674.813 | 3308.8008 | 3019.017 | 2838.2916 | 2756.1097 | -2481.6006 | -2264.2627 | 2503.1379 | -2430.6603 | 2188.566 | -1996.892
0.76 | 3802.9935 | 3690.8927 | 3306.0501 | 3022.2811 | 2890.275 | 2805.0785 | -2512.5981 | -2296.9336 | 2471.6532 | -2398.7963 | 2148.6782 | -1964.2502
0.77 | 3821.5981 | 3706.9725 | 3303.2994 | 3025.5451 | 2942.6305 | 2854.3688 | -2543.5405 | -2329.6698 | 2438.3473 | -2365.2111 | 2107.65 | -1930.4306
0.78 | 3840.2027 | 3723.0523 | 3300.5486 | 3028.8092 | 2995.3581 | 2903.9808 | -2574.4279 | -2362.4712 | 2403.1202 | -2329.8098 | 2065.4157 | -1895.3668
0.79 | 3858.8073 | 3739.132 | 3297.7979 | 3032.0733 | 3048.4578 | 2953.9143 | -2605.2604 | -2395.3379 | 2365.8612 | -2292.4874 | 2021.9025 | -1858.9849
0.8 | 3877.4119 | 3755.2118 | 3295.0472 | 3035.3374 | 3101.9295 | 3004.1694 | -2636.0378 | -2428.2699 | 2326.4472 | -2253.1271 | 1977.0283 | -1821.2024
0.81 | 3881.5545 | 3765.2686 | 3291.8369 | 3040.5381 | 3144.0592 | 3049.8675 | -2666.3879 | -2462.8359 | 2276.2595 | -2208.066 | 1930.4315 | -1783.0624
0.82 | 3885.6972 | 3775.3254 | 3288.6265 | 3045.7388 | 3186.2717 | 3095.7668 | -2696.6737 | -2497.5058 | 2224.0313 | -2160.8585 | 1882.2898 | -1743.2698
0.83 | 3889.8398 | 3785.3821 | 3285.4162 | 3050.9396 | 3228.567 | 3141.8672 | -2726.8954 | -2532.2798 | 2169.6102 | -2111.3476 | 1832.4849 | -1701.7024
0.84 | 3893.9824 | 3795.4389 | 3282.2058 | 3056.1403 | 3270.9452 | 3188.1687 | -2757.0529 | -2567.1578 | 2112.8219 | -2059.3535 | 1780.8802 | -1658.2202
0.85 | 3898.125 | 3805.4957 | 3278.9955 | 3061.341 | 3313.4063 | 3234.6713 | -2787.1461 | -2602.1399 | 2053.4648 | -2004.6692 | 1727.318 | -1612.6614
0.86 | 3902.2676 | 3815.5525 | 3275.7851 | 3066.5417 | 3355.9502 | 3281.3751 | -2817.1752 | -2637.2259 | 1991.3039 | -1947.0537 | 1671.6136 | -1564.8379
0.87 | 3906.4103 | 3825.6093 | 3272.5748 | 3071.7425 | 3398.5769 | 3328.28 | -2847.14 | -2672.4159 | 1926.0623 | -1886.2232 | 1613.5486 | -1514.5279
0.88 | 3910.5529 | 3835.666 | 3269.3644 | 3076.9432 | 3441.2865 | 3375.3861 | -2877.0407 | -2707.71 | 1857.4097 | -1821.8404 | 1552.8621 | -1461.467
0.89 | 3914.6955 | 3845.7228 | 3266.154 | 3082.1439 | 3484.079 | 3422.6933 | -2906.8771 | -2743.1081 | 1784.9466 | -1753.4978 | 1489.2373 | -1405.336
0.9 | 3918.8381 | 3855.7796 | 3262.9437 | 3087.3446 | 3526.9543 | 3470.2016 | -2936.6493 | -2778.6102 | 1708.1819 | -1680.6954 | 1422.2842 | -1345.7423
0.91 | 3922.7422 | 3866.8895 | 3256.1062 | 3094.3424 | 3569.6954 | 3518.8695 | -2963.0566 | -2815.8516 | 1626.4013 | -1603.2443 | 1350.0085 | -1282.9399
0.92 | 3926.6462 | 3877.9994 | 3249.2687 | 3101.3402 | 3612.5145 | 3567.7595 | -2989.3272 | -2853.233 | 1538.9247 | -1519.8592 | 1273.448 | -1215.4722
0.93 | 3930.5502 | 3889.1093 | 3242.4312 | 3108.3379 | 3655.4117 | 3616.8717 | -3015.461 | -2890.7543 | 1444.7111 | -1429.4792 | 1191.7864 | -1142.4992
0.94 | 3934.4543 | 3900.2193 | 3235.5936 | 3115.3357 | 3698.387 | 3666.2061 | -3041.458 | -2928.4156 | 1342.3352 | -1330.6551 | 1103.9019 | -1062.8729
0.95 | 3938.3583 | 3911.3292 | 3228.7561 | 3122.3335 | 3741.4404 | 3715.7627 | -3067.3183 | -2966.2168 | 1229.752 | -1221.3121 | 1008.1788 | -974.9483
0.96 | 3940.2866 | 3918.6633 | 3219.852 | 3134.7139 | 3782.6752 | 3761.9168 | -3091.058 | -3009.3254 | 1103.2803 | -1097.2257 | 901.5586 | -877.7199
0.97 | 3942.215 | 3925.9975 | 3210.948 | 3147.0944 | 3823.9485 | 3808.2176 | -3114.6195 | -3052.6815 | 958.3718 | -954.4293 | 780.5972 | -765.0741
0.98 | 3944.1433 | 3933.3317 | 3202.0439 | 3159.4748 | 3865.2605 | 3854.665 | -3138.003 | -3096.2853 | 784.8746 | -782.7231 | 637.1987 | -628.7276
0.99 | 3946.0717 | 3940.6658 | 3193.1398 | 3171.8553 | 3906.6109 | 3901.2592 | -3161.2084 | -3140.1367 | 556.6619 | -555.8993 | 450.4478 | -447.4452
1 | 3948 | 3948 | 3184.2357 | 3184.2357 | 3948 | 3948 | -3184.2357 | -3184.2357 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_35C_1.1pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 35 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1495 |  | VDC
Nom. Battery Voltage** |  |  |  | 1296.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1164 |  | VDC |  | Please select:
AC Voltage |  |  |  | 1.1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @35°C, 1164Vdc min. battery voltage and 1.1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2520.003 | 2520.0023 | 2520.0029 | 2520.0022 | 0 | 0 | 0 | 0 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0022
0.01 | 2520.003 | 2520.0023 | 2520.0029 | 2520.0022 | 0.0252 | 0.0252 | -0.0252 | -0.0252 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0022
0.05 | 2534.8892 | 2531.6417 | 2534.6203 | 2531.1504 | 126.7445 | 126.5821 | -126.731 | -126.5575 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.1 | 2549.7784 | 2543.2833 | 2549.2407 | 2542.3009 | 254.9778 | 254.3283 | -254.9241 | -254.2301 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.15 | 2594.2669 | 2578.573 | 2591.7118 | 2574.2977 | 389.14 | 386.7859 | -388.7568 | -386.1447 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.2 | 2638.7555 | 2613.8626 | 2634.1829 | 2606.2945 | 527.7511 | 522.7725 | -526.8366 | -521.2589 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.25 | 2709.7023 | 2673.4337 | 2700.8214 | 2657.0648 | 677.4256 | 668.3584 | -675.2054 | -664.2662 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.3 | 2780.6492 | 2733.0049 | 2767.46 | 2707.8352 | 834.1948 | 819.9015 | -830.238 | -812.3506 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.35 | 2875.1122 | 2815.3261 | 2853.3735 | 2773.9995 | 1006.2893 | 985.3641 | -998.6807 | -970.8998 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.4 | 2969.5752 | 2897.6473 | 2939.287 | 2840.1637 | 1187.8301 | 1159.0589 | -1175.7148 | -1136.0655 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.45 | 3082.6192 | 3001.8228 | 3040.9395 | 2920.0913 | 1387.1786 | 1350.8203 | -1368.4228 | -1314.0411 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.5 | 3195.6631 | 3105.9984 | 3142.592 | 3000.0189 | 1597.8315 | 1552.9992 | -1571.296 | -1500.0094 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.51 | 3221.5112 | 3130.9812 | 3164.942 | 3019.5431 | 1642.9707 | 1596.8004 | -1614.1204 | -1539.967 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.52 | 3247.3594 | 3155.9641 | 3187.2921 | 3039.0673 | 1688.6269 | 1641.1013 | -1657.3919 | -1580.315 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.53 | 3273.2076 | 3180.9469 | 3209.6421 | 3058.5916 | 1734.8 | 1685.9019 | -1701.1103 | -1621.0535 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.54 | 3299.0558 | 3205.9297 | 3231.9922 | 3078.1158 | 1781.4901 | 1731.2021 | -1745.2758 | -1662.1825 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.55 | 3324.9039 | 3230.9126 | 3254.3423 | 3097.6401 | 1828.6972 | 1777.0019 | -1789.8882 | -1703.702 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.56 | 3350.7521 | 3255.8954 | 3276.6923 | 3117.1643 | 1876.4212 | 1823.3014 | -1834.9477 | -1745.612 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.57 | 3376.6003 | 3280.8783 | 3299.0424 | 3136.6885 | 1924.6621 | 1870.1006 | -1880.4542 | -1787.9125 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.58 | 3402.4484 | 3305.8611 | 3321.3925 | 3156.2128 | 1973.4201 | 1917.3994 | -1926.4076 | -1830.6034 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.59 | 3428.2966 | 3330.8439 | 3343.7425 | 3175.737 | 2022.695 | 1965.1979 | -1972.8081 | -1873.6848 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.6 | 3454.1448 | 3355.8268 | 3366.0926 | 3195.2613 | 2072.4869 | 2013.4961 | -2019.6555 | -1917.1568 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.61 | 3482.827 | 3385.4275 | 3390.488 | 3205.4109 | 2124.5244 | 2065.1108 | -2068.1977 | -1955.3006 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.62 | 3511.5091 | 3415.0282 | 3414.8834 | 3215.5605 | 2177.1357 | 2117.3175 | -2117.2277 | -1993.6475 | 2520.003 | -2520.0023 | 2520.0029 | -2520.0023
0.63 | 3540.1913 | 3444.6289 | 3439.2788 | 3225.7101 | 2230.3205 | 2170.1162 | -2166.7456 | -2032.1974 | 2520.003 | -2520.0023 | 2520.0029 | -2505.0708
0.64 | 3568.8735 | 3474.2296 | 3463.6741 | 3235.8598 | 2284.079 | 2223.5069 | -2216.7515 | -2070.9503 | 2520.003 | -2520.0023 | 2520.0029 | -2486.3535
0.65 | 3597.5557 | 3503.8303 | 3488.0695 | 3246.0094 | 2338.4112 | 2277.4897 | -2267.2452 | -2109.9061 | 2520.003 | -2520.0023 | 2520.0029 | -2466.7536
0.66 | 3626.2379 | 3533.431 | 3512.4649 | 3256.159 | 2393.317 | 2332.0644 | -2318.2269 | -2149.065 | 2520.003 | -2520.0023 | 2520.0029 | -2446.2403
0.67 | 3654.9201 | 3563.0317 | 3536.8603 | 3266.3087 | 2448.7964 | 2387.2312 | -2369.6964 | -2188.4268 | 2520.003 | -2520.0023 | 2520.0029 | -2424.7805
0.68 | 3683.6022 | 3592.6324 | 3561.2557 | 3276.4583 | 2504.8495 | 2442.99 | -2421.6539 | -2227.9916 | 2520.003 | -2520.0023 | 2520.0029 | -2402.3389
0.69 | 3712.2844 | 3622.2331 | 3585.6511 | 3286.6079 | 2561.4763 | 2499.3408 | -2474.0993 | -2267.7595 | 2520.003 | -2520.0023 | 2520.0029 | -2378.8776
0.7 | 3740.9666 | 3651.8338 | 3610.0465 | 3296.7576 | 2618.6766 | 2556.2836 | -2527.0325 | -2307.7303 | 2520.003 | -2520.0023 | 2520.0029 | -2354.3558
0.71 | 3761.67 | 3674.4868 | 3614.4749 | 3300.6396 | 2670.7857 | 2608.8857 | -2566.2772 | -2343.4541 | 2520.003 | -2520.0023 | 2520.0029 | -2324.316
0.72 | 3782.3733 | 3697.1399 | 3618.9033 | 3304.5217 | 2723.3088 | 2661.9407 | -2605.6104 | -2379.2556 | 2520.003 | -2520.0023 | 2511.425 | -2293.2524
0.73 | 3803.0766 | 3719.793 | 3623.3317 | 3308.4038 | 2776.2459 | 2715.4489 | -2645.0321 | -2415.1348 | 2520.003 | -2520.0023 | 2476.3557 | -2261.1191
0.74 | 3823.78 | 3742.446 | 3627.7601 | 3312.2859 | 2829.5972 | 2769.4101 | -2684.5425 | -2451.0916 | 2520.003 | -2517.1949 | 2440.0564 | -2227.8662
0.75 | 3844.4833 | 3765.0991 | 3632.1885 | 3316.168 | 2883.3625 | 2823.8243 | -2724.1414 | -2487.126 | 2520.003 | -2490.379 | 2402.4669 | -2193.4389
0.76 | 3865.1866 | 3787.7522 | 3636.6169 | 3320.0501 | 2937.5419 | 2878.6916 | -2763.8288 | -2523.238 | 2512.074 | -2461.7475 | 2363.5212 | -2157.7771
0.77 | 3885.89 | 3810.4052 | 3633.6293 | 3323.9321 | 2992.1353 | 2934.012 | -2797.8946 | -2559.4278 | 2479.3683 | -2431.2058 | 2318.415 | -2120.8146
0.78 | 3906.5933 | 3833.0583 | 3630.6035 | 3327.8142 | 3047.1428 | 2989.7855 | -2831.8707 | -2595.6951 | 2444.6661 | -2398.6494 | 2271.9573 | -2082.478
0.79 | 3927.2967 | 3855.7114 | 3627.5777 | 3331.6963 | 3102.5644 | 3046.012 | -2865.7864 | -2632.0401 | 2407.8525 | -2363.963 | 2224.0927 | -2042.6858
0.8 | 3948 | 3878.3644 | 3624.5519 | 3335.5784 | 3158.4 | 3102.6915 | -2899.6415 | -2668.4627 | 2368.8 | -2327.0187 | 2174.7312 | -2001.347
0.81 | 3948 | 3885.328 | 3621.0205 | 3341.2267 | 3197.88 | 3147.1157 | -2933.0266 | -2706.3936 | 2315.2252 | -2278.4724 | 2123.4746 | -1959.3951
0.82 | 3948 | 3892.2915 | 3617.4892 | 3346.8749 | 3237.36 | 3191.6791 | -2966.3411 | -2744.4374 | 2259.6912 | -2227.8057 | 2070.5188 | -1915.6291
0.83 | 3948 | 3899.2551 | 3613.9578 | 3352.5232 | 3276.84 | 3236.3817 | -2999.5849 | -2782.5942 | 2202.0499 | -2174.8617 | 2015.7333 | -1869.9147
0.84 | 3948 | 3906.2187 | 3610.4264 | 3358.1714 | 3316.32 | 3281.2237 | -3032.7582 | -2820.864 | 2142.1311 | -2119.4611 | 1958.9682 | -1822.0981
0.85 | 3948 | 3913.1822 | 3606.895 | 3363.8197 | 3355.8 | 3326.2049 | -3065.8607 | -2859.2467 | 2079.7381 | -2061.3966 | 1900.0498 | -1772.002
0.86 | 3948 | 3920.1458 | 3603.3636 | 3369.4679 | 3395.28 | 3371.3254 | -3098.8927 | -2897.7424 | 2014.6408 | -2000.427 | 1838.7749 | -1719.4194
0.87 | 3948 | 3927.1093 | 3599.8322 | 3375.1162 | 3434.76 | 3416.5851 | -3131.854 | -2936.3511 | 1946.5682 | -1936.268 | 1774.9035 | -1664.1068
0.88 | 3948 | 3934.0729 | 3596.3008 | 3380.7644 | 3474.24 | 3461.9841 | -3164.7447 | -2975.0727 | 1875.1961 | -1868.5811 | 1708.1483 | -1605.7741
0.89 | 3948 | 3941.0364 | 3592.7695 | 3386.4127 | 3513.72 | 3507.5224 | -3197.5648 | -3013.9073 | 1800.1322 | -1796.957 | 1638.161 | -1544.0705
0.9 | 3948 | 3948 | 3589.2381 | 3392.0609 | 3553.2 | 3553.2 | -3230.3143 | -3052.8548 | 1720.8933 | -1720.8933 | 1564.5126 | -1478.5651
0.91 | 3948 | 3948 | 3581.7168 | 3401.425 | 3592.68 | 3592.68 | -3259.3623 | -3095.2967 | 1636.8734 | -1636.8734 | 1485.0093 | -1410.2589
0.92 | 3948 | 3948 | 3574.1955 | 3410.789 | 3632.16 | 3632.16 | -3288.2599 | -3137.9259 | 1547.2937 | -1547.2937 | 1400.7928 | -1336.7508
0.93 | 3948 | 3948 | 3566.6743 | 3419.1717 | 3671.64 | 3671.64 | -3317.0071 | -3179.8297 | 1451.125 | -1451.125 | 1310.9651 | -1256.7491
0.94 | 3948 | 3948 | 3559.153 | 3426.8693 | 3711.12 | 3711.12 | -3345.6038 | -3221.2571 | 1346.9567 | -1346.9567 | 1214.292 | -1169.1602
0.95 | 3948 | 3948 | 3551.6317 | 3434.5668 | 3750.6 | 3750.6 | -3374.0502 | -3262.8385 | 1232.7626 | -1232.7626 | 1108.9967 | -1072.4431
0.96 | 3948 | 3948 | 3541.8372 | 3448.1853 | 3790.08 | 3790.08 | -3400.1638 | -3310.2579 | 1105.44 | -1105.44 | 991.7144 | -965.4919
0.97 | 3948 | 3948 | 3532.0428 | 3461.8038 | 3829.56 | 3829.56 | -3426.0815 | -3357.9497 | 959.7782 | -959.7782 | 858.657 | -841.5815
0.98 | 3948 | 3948 | 3522.2483 | 3475.4223 | 3869.04 | 3869.04 | -3451.8033 | -3405.9139 | 785.6421 | -785.6421 | 700.9186 | -691.6003
0.99 | 3948 | 3948 | 3512.4538 | 3489.0408 | 3908.52 | 3908.52 | -3477.3292 | -3454.1504 | 556.9339 | -556.9339 | 495.4926 | -492.1898
1 | 3948 | 3948 | 3502.6593 | 3502.6593 | 3948 | 3948 | -3502.6593 | -3502.6593 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_40C_0.9pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 40 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V) |  |  |  | 1496 |  | VDC
Min. battery voltage |  |  |  | 1164 |  | VDC |  | Please select:
AC voltage |  |  |  | 0.9 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@min battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @40°C, 1164Vdc min. battery voltage and 0.9pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2268.002 | 2268.0017 | 2268.002 | 2268.0016 | 0 | 0 | 0 | 0 | 2268.002 | -2268.0017 | 2268.002 | -2268.0016
0.01 | 2268.002 | 2268.0017 | 2268.002 | 2268.0016 | 0.02268 | 0.02268 | -0.02268 | -0.02268 | 2268.002 | -2268.0017 | 2268.002 | -2268.0016
0.05 | 2278.152 | 2276.3546 | 2277.9219 | 2275.8204 | 113.9076 | 113.8177 | -113.8961 | -113.791 | 2268.002 | -2268.0017 | 2268.002 | -2268.0017
0.1 | 2288.304 | 2284.7093 | 2287.8437 | 2283.6407 | 228.8304 | 228.4709 | -228.7844 | -228.3641 | 2268.002 | -2268.0017 | 2268.002 | -2268.0017
0.15 | 2318.8466 | 2310.5499 | 2316.6609 | 2305.9586 | 347.827 | 346.5825 | -347.4991 | -345.8938 | 2268.002 | -2268.0017 | 2268.002 | -2268.0017
0.2 | 2349.3891 | 2336.3904 | 2345.478 | 2328.2765 | 469.8778 | 467.2781 | -469.0956 | -465.6553 | 2268.002 | -2268.0017 | 2268.002 | -2268.0017
0.25 | 2399.3173 | 2379.5333 | 2391.4898 | 2363.5712 | 599.8293 | 594.8833 | -597.8725 | -590.8928 | 2268.002 | -2268.0017 | 2268.002 | -2268.0017
0.3 | 2449.2454 | 2422.6762 | 2437.5017 | 2398.866 | 734.7736 | 726.8029 | -731.2505 | -719.6598 | 2268.002 | -2268.0017 | 2268.002 | -2268.0017
0.35 | 2517.4045 | 2484.1816 | 2497.5644 | 2445.8943 | 881.0916 | 869.4636 | -874.1475 | -856.063 | 2268.002 | -2268.0017 | 2268.002 | -2268.0017
0.4 | 2585.5636 | 2545.687 | 2557.6271 | 2492.9226 | 1034.2254 | 1018.2748 | -1023.0508 | -997.169 | 2268.002 | -2268.0017 | 2268.002 | -2268.0017
0.45 | 2670.0943 | 2622.9923 | 2629.2257 | 2530.0375 | 1201.5424 | 1180.3465 | -1183.1516 | -1138.5169 | 2268.002 | -2268.0017 | 2268.002 | -2259.3958
0.5 | 2754.625 | 2700.2976 | 2700.8243 | 2567.1525 | 1377.3125 | 1350.1488 | -1350.4121 | -1283.5762 | 2268.002 | -2268.0017 | 2268.002 | -2223.2193
0.51 | 2774.4185 | 2719.3077 | 2716.9354 | 2568.3198 | 1414.9534 | 1386.8469 | -1385.637 | -1309.8431 | 2268.002 | -2268.0017 | 2268.002 | -2209.2029
0.52 | 2794.212 | 2738.3178 | 2733.0465 | 2569.487 | 1452.9902 | 1423.9252 | -1421.1842 | -1336.1333 | 2268.002 | -2268.0017 | 2268.002 | -2194.7691
0.53 | 2814.0054 | 2757.3278 | 2749.1576 | 2570.6543 | 1491.4229 | 1461.3838 | -1457.0535 | -1362.4468 | 2268.002 | -2268.0017 | 2268.002 | -2179.9088
0.54 | 2833.7989 | 2776.3379 | 2765.2687 | 2571.8216 | 1530.2514 | 1499.2225 | -1493.2451 | -1388.7837 | 2268.002 | -2268.0017 | 2268.002 | -2164.6123
0.55 | 2853.5924 | 2795.348 | 2781.3797 | 2572.9889 | 1569.4758 | 1537.4414 | -1529.7589 | -1415.1439 | 2268.002 | -2268.0017 | 2268.002 | -2148.8694
0.56 | 2873.3858 | 2814.358 | 2797.4908 | 2574.1562 | 1609.0961 | 1576.0405 | -1566.5949 | -1441.5275 | 2268.002 | -2268.0017 | 2268.002 | -2132.6694
0.57 | 2893.1793 | 2833.3681 | 2813.6019 | 2575.3235 | 1649.1122 | 1615.0198 | -1603.7531 | -1467.9344 | 2268.002 | -2268.0017 | 2268.002 | -2116.0009
0.58 | 2912.9728 | 2852.3782 | 2829.713 | 2576.4908 | 1689.5242 | 1654.3793 | -1641.2335 | -1494.3646 | 2268.002 | -2268.0017 | 2268.002 | -2098.8518
0.59 | 2932.7663 | 2871.3883 | 2845.8241 | 2577.658 | 1730.3321 | 1694.1191 | -1679.0362 | -1520.8182 | 2268.002 | -2268.0017 | 2268.002 | -2081.2095
0.6 | 2952.5597 | 2890.3983 | 2861.9352 | 2578.8253 | 1771.5358 | 1734.239 | -1717.1611 | -1547.2952 | 2268.002 | -2268.0017 | 2268.002 | -2063.0603
0.61 | 2974.9054 | 2906.2156 | 2864.2253 | 2580.9731 | 1814.6923 | 1772.7915 | -1747.1774 | -1574.3936 | 2268.002 | -2268.0017 | 2268.002 | -2045.1667
0.62 | 2997.2512 | 2922.0328 | 2866.5155 | 2583.1209 | 1858.2957 | 1811.6604 | -1777.2396 | -1601.5349 | 2268.002 | -2268.0017 | 2249.0732 | -2026.7213
0.63 | 3019.5969 | 2937.8501 | 2868.8056 | 2585.2686 | 1902.346 | 1850.8456 | -1807.3475 | -1628.7192 | 2268.002 | -2268.0017 | 2227.9004 | -2007.707
0.64 | 3041.9426 | 2953.6674 | 2871.0957 | 2587.4164 | 1946.8433 | 1890.3471 | -1837.5013 | -1655.9465 | 2268.002 | -2268.0017 | 2206.0779 | -1988.1058
0.65 | 3064.2883 | 2969.4846 | 2873.3858 | 2589.5642 | 1991.7874 | 1930.165 | -1867.7008 | -1683.2167 | 2268.002 | -2256.6129 | 2183.5842 | -1967.8984
0.66 | 3086.634 | 2985.3019 | 2875.676 | 2591.7119 | 2037.1784 | 1970.2992 | -1897.9461 | -1710.5299 | 2268.002 | -2242.7546 | 2160.3964 | -1947.064
0.67 | 3108.9797 | 3001.1191 | 2877.9661 | 2593.8597 | 2083.0164 | 2010.7498 | -1928.2373 | -1737.886 | 2268.002 | -2227.9141 | 2136.4901 | -1925.5805
0.68 | 3131.3254 | 3016.9364 | 2880.2562 | 2596.0074 | 2129.3013 | 2051.5167 | -1958.5742 | -1765.2851 | 2268.002 | -2212.0543 | 2111.8387 | -1903.4241
0.69 | 3153.6712 | 3032.7536 | 2882.5463 | 2598.1552 | 2176.0331 | 2092.6 | -1988.957 | -1792.7271 | 2268.002 | -2195.1355 | 2086.414 | -1880.5691
0.7 | 3176.0169 | 3048.5709 | 2884.8365 | 2600.303 | 2223.2118 | 2133.9996 | -2019.3855 | -1820.2121 | 2268.002 | -2177.1151 | 2060.1853 | -1856.9878
0.71 | 3179.1777 | 3057.4004 | 2881.6172 | 2603.1655 | 2257.2161 | 2170.7543 | -2045.9482 | -1848.2475 | 2238.7822 | -2153.0265 | 2029.2396 | -1833.1535
0.72 | 3182.3385 | 3066.23 | 2878.3979 | 2606.028 | 2291.2837 | 2207.6856 | -2072.4465 | -1876.3402 | 2208.4603 | -2127.8841 | 1997.5335 | -1808.5158
0.73 | 3185.4992 | 3075.0595 | 2875.1786 | 2608.8905 | 2325.4144 | 2244.7935 | -2098.8804 | -1904.4901 | 2177.1204 | -2101.6407 | 1965.0326 | -1783.0388
0.74 | 3188.66 | 3083.8891 | 2871.9593 | 2611.753 | 2359.6084 | 2282.0779 | -2125.2499 | -1932.6972 | 2144.7146 | -2074.245 | 1931.6995 | -1756.683
0.75 | 3191.8208 | 3092.7187 | 2868.74 | 2614.6156 | 2393.8656 | 2319.539 | -2151.555 | -1960.9617 | 2111.191 | -2045.6411 | 1897.4931 | -1729.4056
0.76 | 3194.9816 | 3101.5482 | 2865.5207 | 2617.4781 | 2428.186 | 2357.1766 | -2177.7957 | -1989.2833 | 2076.4923 | -2015.7677 | 1862.368 | -1701.1594
0.77 | 3198.1424 | 3110.3778 | 2862.3014 | 2620.3406 | 2462.5697 | 2394.9909 | -2203.9721 | -2017.6622 | 2040.5552 | -1984.5575 | 1826.2739 | -1671.8923
0.78 | 3201.3032 | 3119.2073 | 2859.0821 | 2623.2031 | 2497.0165 | 2432.9817 | -2230.084 | -2046.0984 | 2003.31 | -1951.936 | 1789.155 | -1641.5468
0.79 | 3204.464 | 3128.0369 | 2855.8628 | 2626.0656 | 2531.5266 | 2471.1491 | -2256.1316 | -2074.5918 | 1964.6788 | -1917.8208 | 1750.949 | -1610.0588
0.8 | 3207.6248 | 3136.8664 | 2852.6435 | 2628.9281 | 2566.0998 | 2509.4931 | -2282.1148 | -2103.1425 | 1924.5749 | -1882.1198 | 1711.5861 | -1577.3569
0.81 | 3212.5516 | 3144.1601 | 2849.9269 | 2633.365 | 2602.1668 | 2546.7697 | -2308.4408 | -2133.0256 | 1883.9363 | -1843.8294 | 1671.2823 | -1544.2839
0.82 | 3217.4785 | 3151.4538 | 2847.2103 | 2637.8018 | 2638.3324 | 2584.1921 | -2334.7124 | -2162.9975 | 1841.5673 | -1803.7772 | 1629.6393 | -1509.7815
0.83 | 3222.4054 | 3158.7475 | 2844.4937 | 2642.2387 | 2674.5964 | 2621.7604 | -2360.9298 | -2193.0581 | 1797.3397 | -1761.8337 | 1586.5544 | -1473.744
0.84 | 3227.3322 | 3166.0412 | 2841.7771 | 2646.6755 | 2710.9591 | 2659.4746 | -2387.0927 | -2223.2075 | 1751.1066 | -1717.8509 | 1541.9096 | -1436.0501
0.85 | 3232.2591 | 3173.3349 | 2839.0605 | 2651.1124 | 2747.4202 | 2697.3347 | -2413.2014 | -2253.4455 | 1702.6981 | -1671.6579 | 1495.5679 | -1396.5601
0.86 | 3237.1859 | 3180.6286 | 2836.3439 | 2655.5492 | 2783.9799 | 2735.3406 | -2439.2557 | -2283.7723 | 1651.9167 | -1623.0558 | 1447.3694 | -1355.1109
0.87 | 3242.1128 | 3187.9223 | 2833.6273 | 2659.9861 | 2820.6381 | 2773.4924 | -2465.2557 | -2314.1879 | 1598.5293 | -1571.8106 | 1397.1248 | -1311.5107
0.88 | 3247.0396 | 3195.216 | 2830.9107 | 2664.4229 | 2857.3949 | 2811.7901 | -2491.2014 | -2344.6922 | 1542.2584 | -1517.6435 | 1344.6081 | -1265.5308
0.89 | 3251.9665 | 3202.5097 | 2828.1941 | 2668.8598 | 2894.2502 | 2850.2337 | -2517.0927 | -2375.2852 | 1482.7683 | -1460.218 | 1289.5449 | -1216.8947
0.9 | 3256.8934 | 3209.8034 | 2825.4775 | 2673.2966 | 2931.204 | 2888.8231 | -2542.9297 | -2405.967 | 1419.6469 | -1399.1209 | 1231.5971 | -1165.263
0.91 | 3266.8396 | 3218.496 | 2819.6216 | 2679.5751 | 2972.824 | 2928.8314 | -2565.8557 | -2438.4133 | 1354.4586 | -1334.415 | 1169.0384 | -1110.9739
0.92 | 3276.7858 | 3227.1886 | 2813.7658 | 2685.8535 | 3014.6429 | 2969.0135 | -2588.6645 | -2470.9852 | 1284.2325 | -1264.7944 | 1102.7665 | -1052.6353
0.93 | 3286.732 | 3235.8811 | 2807.91 | 2692.1319 | 3056.6607 | 3009.3695 | -2611.3563 | -2503.6826 | 1208.0696 | -1189.3789 | 1032.074 | -989.5187
0.94 | 3296.6782 | 3244.5737 | 2802.0541 | 2698.4103 | 3098.8775 | 3049.8993 | -2633.9309 | -2536.5057 | 1124.7423 | -1106.9656 | 955.9893 | -920.6286
0.95 | 3306.6244 | 3253.2663 | 2796.1983 | 2704.6887 | 3141.2932 | 3090.603 | -2656.3884 | -2569.4542 | 1032.4931 | -1015.8321 | 873.1126 | -844.5388
0.96 | 3317.3662 | 3274.6797 | 2788.5545 | 2715.3468 | 3184.6716 | 3143.6925 | -2677.0123 | -2606.7329 | 928.8625 | -916.9103 | 780.7953 | -760.2971
0.97 | 3328.108 | 3296.0931 | 2780.9107 | 2726.0049 | 3228.2648 | 3197.2103 | -2697.4834 | -2644.2248 | 809.0794 | -801.2964 | 676.0531 | -662.7052
0.98 | 3338.8498 | 3317.5065 | 2773.2669 | 2736.6631 | 3272.0728 | 3251.1564 | -2717.8016 | -2681.9298 | 664.4227 | -660.1755 | 551.8731 | -544.5891
0.99 | 3349.5916 | 3338.92 | 2765.6231 | 2747.3212 | 3316.0957 | 3305.5308 | -2737.9669 | -2719.848 | 472.518 | -471.0126 | 390.1392 | -387.5573
1 | 3360.3334 | 3360.3334 | 2757.9793 | 2757.9793 | 3360.3334 | 3360.3334 | -2757.9793 | -2757.9793 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited

## CATL_40C_1.0pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 40 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V) |  |  |  | 1496 |  | VDC
Min. battery voltage |  |  |  | 1164 |  | VDC |  | Please select:
AC voltage |  |  |  | 1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@min battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @40°C, 1164Vdc min. battery voltage and 1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2520.0023 | 2520.0019 | 2520.0022 | 2520.0017 | 0 | 0 | 0 | 0 | 2520.0023 | -2520.0019 | 2520.0022 | -2520.0017
0.01 | 2520.0023 | 2520.0019 | 2520.0022 | 2520.0017 | 0.0252 | 0.0252 | -0.0252 | -0.0252 | 2520.0023 | -2520.0019 | 2520.0022 | -2520.0017
0.05 | 2531.28 | 2529.2829 | 2531.0243 | 2528.6893 | 126.564 | 126.4641 | -126.5512 | -126.4345 | 2520.0023 | -2520.0019 | 2520.0023 | -2520.0019
0.1 | 2542.56 | 2538.5659 | 2542.0486 | 2537.3786 | 254.256 | 253.8566 | -254.2049 | -253.7379 | 2520.0023 | -2520.0019 | 2520.0023 | -2520.0019
0.15 | 2576.4962 | 2567.2776 | 2574.0676 | 2562.1762 | 386.4744 | 385.0916 | -386.1101 | -384.3264 | 2520.0023 | -2520.0019 | 2520.0023 | -2520.0019
0.2 | 2610.4324 | 2595.9894 | 2606.0867 | 2586.9739 | 522.0865 | 519.1979 | -521.2173 | -517.3948 | 2520.0023 | -2520.0019 | 2520.0023 | -2520.0019
0.25 | 2665.9081 | 2643.9259 | 2657.2109 | 2626.1903 | 666.477 | 660.9815 | -664.3027 | -656.5476 | 2520.0023 | -2520.0019 | 2520.0023 | -2520.0019
0.3 | 2721.3838 | 2691.8625 | 2708.3352 | 2665.4066 | 816.4151 | 807.5587 | -812.5006 | -799.622 | 2520.0023 | -2520.0019 | 2520.0023 | -2520.0019
0.35 | 2797.1161 | 2760.2018 | 2775.0715 | 2717.6603 | 978.9906 | 966.0706 | -971.275 | -951.1811 | 2520.0023 | -2520.0019 | 2520.0023 | -2520.0019
0.4 | 2872.8484 | 2828.5411 | 2841.8078 | 2769.914 | 1149.1394 | 1131.4164 | -1136.7231 | -1107.9656 | 2520.0023 | -2520.0019 | 2520.0023 | -2520.0019
0.45 | 2966.7714 | 2914.4359 | 2921.3619 | 2811.1528 | 1335.0472 | 1311.4962 | -1314.6128 | -1265.0188 | 2520.0023 | -2520.0019 | 2520.0023 | -2510.4397
0.5 | 3060.6945 | 3000.3307 | 3000.9159 | 2852.3916 | 1530.3472 | 1500.1654 | -1500.4579 | -1426.1958 | 2520.0023 | -2520.0019 | 2520.0023 | -2470.2436
0.51 | 3082.6872 | 3021.453 | 3018.8171 | 2853.6886 | 1572.1705 | 1540.941 | -1539.5967 | -1455.3812 | 2520.0023 | -2520.0019 | 2520.0023 | -2454.6699
0.52 | 3104.68 | 3042.5753 | 3036.7183 | 2854.9856 | 1614.4336 | 1582.1392 | -1579.0935 | -1484.5925 | 2520.0023 | -2520.0019 | 2520.0023 | -2438.6324
0.53 | 3126.6727 | 3063.6976 | 3054.6195 | 2856.2826 | 1657.1365 | 1623.7597 | -1618.9483 | -1513.8298 | 2520.0023 | -2520.0019 | 2520.0023 | -2422.1209
0.54 | 3148.6654 | 3084.8199 | 3072.5207 | 2857.5796 | 1700.2793 | 1665.8027 | -1659.1612 | -1543.093 | 2520.0023 | -2520.0019 | 2520.0023 | -2405.1248
0.55 | 3170.6582 | 3105.9422 | 3090.4219 | 2858.8766 | 1743.862 | 1708.2682 | -1699.7321 | -1572.3821 | 2520.0023 | -2520.0019 | 2520.0023 | -2387.6327
0.56 | 3192.6509 | 3127.0645 | 3108.3231 | 2860.1735 | 1787.8845 | 1751.1561 | -1740.661 | -1601.6972 | 2520.0023 | -2520.0019 | 2520.0023 | -2369.6326
0.57 | 3214.6437 | 3148.1868 | 3126.2244 | 2861.4705 | 1832.3469 | 1794.4665 | -1781.9479 | -1631.0382 | 2520.0023 | -2520.0019 | 2520.0023 | -2351.1121
0.58 | 3236.6364 | 3169.3091 | 3144.1256 | 2862.7675 | 1877.2491 | 1838.1993 | -1823.5928 | -1660.4052 | 2520.0023 | -2520.0019 | 2520.0023 | -2332.0576
0.59 | 3258.6292 | 3190.4314 | 3162.0268 | 2864.0645 | 1922.5912 | 1882.3545 | -1865.5958 | -1689.7981 | 2520.0023 | -2520.0019 | 2520.0023 | -2312.455
0.6 | 3280.6219 | 3211.5537 | 3179.928 | 2865.3615 | 1968.3731 | 1926.9322 | -1907.9568 | -1719.2169 | 2520.0023 | -2520.0019 | 2520.0023 | -2292.2892
0.61 | 3305.4505 | 3229.1284 | 3182.4726 | 2867.7479 | 2016.3248 | 1969.7683 | -1941.3083 | -1749.3262 | 2520.0023 | -2520.0019 | 2520.0023 | -2272.4075
0.62 | 3330.2791 | 3246.7032 | 3185.0172 | 2870.1343 | 2064.773 | 2012.956 | -1974.7106 | -1779.4833 | 2520.0023 | -2520.0019 | 2498.9702 | -2251.9126
0.63 | 3355.1076 | 3264.2779 | 3187.5618 | 2872.5207 | 2113.7178 | 2056.4951 | -2008.1639 | -1809.688 | 2520.0023 | -2520.0019 | 2475.4449 | -2230.7856
0.64 | 3379.9362 | 3281.8526 | 3190.1063 | 2874.9071 | 2163.1592 | 2100.3857 | -2041.6681 | -1839.9405 | 2520.0023 | -2520.0019 | 2451.1977 | -2209.0065
0.65 | 3404.7648 | 3299.4273 | 3192.6509 | 2877.2935 | 2213.0971 | 2144.6278 | -2075.2231 | -1870.2408 | 2520.0023 | -2507.3477 | 2426.2047 | -2186.5538
0.66 | 3429.5933 | 3317.0021 | 3195.1955 | 2879.6799 | 2263.5316 | 2189.2214 | -2108.829 | -1900.5887 | 2520.0023 | -2491.9495 | 2400.4405 | -2163.4044
0.67 | 3454.4219 | 3334.5768 | 3197.7401 | 2882.0663 | 2314.4627 | 2234.1665 | -2142.4859 | -1930.9844 | 2520.0023 | -2475.4601 | 2373.8779 | -2139.5339
0.68 | 3479.2505 | 3352.1515 | 3200.2847 | 2884.4527 | 2365.8903 | 2279.463 | -2176.1936 | -1961.4278 | 2520.0023 | -2457.8381 | 2346.4875 | -2114.9157
0.69 | 3504.0791 | 3369.7263 | 3202.8293 | 2886.8391 | 2417.8146 | 2325.1111 | -2209.9522 | -1991.919 | 2520.0023 | -2439.0394 | 2318.2378 | -2089.5212
0.7 | 3528.9076 | 3387.301 | 3205.3739 | 2889.2255 | 2470.2353 | 2371.1107 | -2243.7617 | -2022.4579 | 2520.0023 | -2419.0168 | 2289.0948 | -2063.3197
0.71 | 3532.4196 | 3397.1116 | 3201.7969 | 2892.4061 | 2508.0179 | 2411.9492 | -2273.2758 | -2053.6083 | 2487.5358 | -2392.2517 | 2254.7107 | -2036.8372
0.72 | 3535.9316 | 3406.9222 | 3198.2199 | 2895.5867 | 2545.8708 | 2452.984 | -2302.7183 | -2084.8224 | 2453.8448 | -2364.3156 | 2219.4816 | -2009.462
0.73 | 3539.4436 | 3416.7328 | 3194.6429 | 2898.7672 | 2583.7938 | 2494.215 | -2332.0893 | -2116.1001 | 2419.0226 | -2335.1563 | 2183.3695 | -1981.1542
0.74 | 3542.9556 | 3426.5434 | 3191.0659 | 2901.9478 | 2621.7871 | 2535.6421 | -2361.3887 | -2147.4414 | 2383.0163 | -2304.7167 | 2146.3328 | -1951.87
0.75 | 3546.4676 | 3436.3541 | 3187.4889 | 2905.1284 | 2659.8507 | 2577.2655 | -2390.6167 | -2178.8463 | 2345.7678 | -2272.9346 | 2108.3257 | -1921.5618
0.76 | 3549.9796 | 3446.1647 | 3183.9119 | 2908.309 | 2697.9845 | 2619.0851 | -2419.773 | -2210.3148 | 2307.2136 | -2239.7419 | 2069.2978 | -1890.1771
0.77 | 3553.4916 | 3455.9753 | 3180.3349 | 2911.4895 | 2736.1885 | 2661.101 | -2448.8579 | -2241.8469 | 2267.2836 | -2205.0639 | 2029.1932 | -1857.6581
0.78 | 3557.0036 | 3465.7859 | 3176.7579 | 2914.6701 | 2774.4628 | 2703.313 | -2477.8711 | -2273.4427 | 2225.9 | -2168.8178 | 1987.95 | -1823.9408
0.79 | 3560.5155 | 3475.5965 | 3173.1809 | 2917.8507 | 2812.8073 | 2745.7212 | -2506.8129 | -2305.102 | 2182.9764 | -2130.912 | 1945.4989 | -1788.9542
0.8 | 3564.0275 | 3485.4071 | 3169.6039 | 2921.0313 | 2851.222 | 2788.3257 | -2535.6831 | -2336.825 | 2138.4165 | -2091.2443 | 1901.7623 | -1752.6188
0.81 | 3569.5018 | 3493.5112 | 3166.5854 | 2925.9611 | 2891.2965 | 2829.7441 | -2564.9342 | -2370.0285 | 2093.2625 | -2048.6994 | 1856.9803 | -1715.871
0.82 | 3574.9761 | 3501.6154 | 3163.567 | 2930.8909 | 2931.4804 | 2871.3246 | -2594.1249 | -2403.3306 | 2046.1859 | -2004.1969 | 1810.7103 | -1677.5351
0.83 | 3580.4504 | 3509.7195 | 3160.5485 | 2935.8208 | 2971.7738 | 2913.0672 | -2623.2553 | -2436.7312 | 1997.0442 | -1957.593 | 1762.8383 | -1637.4933
0.84 | 3585.9247 | 3517.8236 | 3157.5301 | 2940.7506 | 3012.1767 | 2954.9718 | -2652.3253 | -2470.2305 | 1945.674 | -1908.7232 | 1713.2329 | -1595.6113
0.85 | 3591.399 | 3525.9277 | 3154.5116 | 2945.6804 | 3052.6891 | 2997.0385 | -2681.3349 | -2503.8284 | 1891.8868 | -1857.3977 | 1661.7421 | -1551.7335
0.86 | 3596.8732 | 3534.0318 | 3151.4932 | 2950.6103 | 3093.311 | 3039.2673 | -2710.2841 | -2537.5248 | 1835.463 | -1803.3953 | 1608.1882 | -1505.6788
0.87 | 3602.3475 | 3542.1359 | 3148.4747 | 2955.5401 | 3134.0424 | 3081.6582 | -2739.173 | -2571.3199 | 1776.1437 | -1746.4562 | 1552.3609 | -1457.2341
0.88 | 3607.8218 | 3550.24 | 3145.4563 | 2960.4699 | 3174.8832 | 3124.2112 | -2768.0015 | -2605.2135 | 1713.6204 | -1686.2706 | 1494.009 | -1406.1453
0.89 | 3613.2961 | 3558.3441 | 3142.4379 | 2965.3998 | 3215.8335 | 3166.9263 | -2796.7697 | -2639.2058 | 1647.5204 | -1622.4645 | 1432.8276 | -1352.1052
0.9 | 3618.7704 | 3566.4483 | 3139.4194 | 2970.3296 | 3256.8934 | 3209.8034 | -2825.4775 | -2673.2966 | 1577.3854 | -1554.5788 | 1368.4412 | -1294.7367
0.91 | 3629.8217 | 3576.1067 | 3132.9129 | 2977.3056 | 3303.1378 | 3254.2571 | -2850.9508 | -2709.3481 | 1504.954 | -1482.6833 | 1298.9315 | -1234.4155
0.92 | 3640.8731 | 3585.7651 | 3126.4064 | 2984.2816 | 3349.6032 | 3298.9039 | -2876.2939 | -2745.5391 | 1426.925 | -1405.3272 | 1225.2961 | -1169.5948
0.93 | 3651.9244 | 3595.4235 | 3119.9 | 2991.2576 | 3396.2897 | 3343.7438 | -2901.507 | -2781.8696 | 1342.2996 | -1321.5321 | 1146.7489 | -1099.4652
0.94 | 3662.9758 | 3605.0819 | 3113.3935 | 2998.2336 | 3443.1972 | 3388.777 | -2926.5899 | -2818.3396 | 1249.7137 | -1229.9618 | 1062.2103 | -1022.9207
0.95 | 3674.0271 | 3614.7403 | 3106.887 | 3005.2096 | 3490.3258 | 3434.0033 | -2951.5427 | -2854.9492 | 1147.2146 | -1128.7023 | 970.1252 | -938.3764
0.96 | 3685.9624 | 3638.533 | 3098.3939 | 3017.052 | 3538.5239 | 3492.9917 | -2974.4581 | -2896.3699 | 1032.0695 | -1018.7892 | 867.5503 | -844.7746
0.97 | 3697.8978 | 3662.3257 | 3089.9008 | 3028.8944 | 3586.9608 | 3552.4559 | -2997.2038 | -2938.0275 | 898.9771 | -890.3294 | 751.1701 | -736.3391
0.98 | 3709.8331 | 3686.1184 | 3081.4077 | 3040.7367 | 3635.6364 | 3612.396 | -3019.7795 | -2979.922 | 738.2475 | -733.5283 | 613.1924 | -605.099
0.99 | 3721.7684 | 3709.9111 | 3072.9146 | 3052.5791 | 3684.5507 | 3672.812 | -3042.1854 | -3022.0533 | 525.02 | -523.3474 | 433.4879 | -430.6193
1 | 3733.7038 | 3733.7038 | 3064.4215 | 3064.4215 | 3733.7038 | 3733.7038 | -3064.4215 | -3064.4215 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited

## CATL_40C_1.1pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 40 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V) |  |  |  | 1496 |  | VDC
Min. battery voltage |  |  |  | 1164 |  | VDC |  | Please select:
AC voltage |  |  |  | 1.1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@min battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @40°C, 1164Vdc min. battery voltage and 1.1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2520.0028 | 2520.0022 | 2520.0027 | 2520.0021 | 0 | 0 | 0 | 0 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0021
0.01 | 2520.0028 | 2520.0022 | 2520.0027 | 2520.0021 | 0.0252 | 0.0252 | -0.0252 | -0.0252 | 2520.0028 | -2520.0022 | 2520.0027 | -2520.0021
0.05 | 2533.7694 | 2530.9019 | 2533.5809 | 2530.4204 | 126.6885 | 126.5451 | -126.679 | -126.521 | 2520.0028 | -2520.0022 | 2520.0028 | -2520.0022
0.1 | 2547.5388 | 2541.8037 | 2547.1617 | 2540.8408 | 254.7539 | 254.1804 | -254.7162 | -254.0841 | 2520.0028 | -2520.0022 | 2520.0028 | -2520.0022
0.15 | 2588.7577 | 2574.894 | 2586.6982 | 2570.5942 | 388.3137 | 386.2341 | -388.0047 | -385.5891 | 2520.0028 | -2520.0022 | 2520.0028 | -2520.0022
0.2 | 2629.9766 | 2607.9842 | 2626.2347 | 2600.3476 | 525.9953 | 521.5968 | -525.2469 | -520.0695 | 2520.0028 | -2520.0022 | 2520.0028 | -2520.0022
0.25 | 2696.1138 | 2663.435 | 2688.245 | 2647.6824 | 674.0284 | 665.8588 | -672.0613 | -661.9206 | 2520.0028 | -2520.0022 | 2520.0028 | -2520.0022
0.3 | 2762.2509 | 2718.8858 | 2750.2553 | 2695.0171 | 828.6753 | 815.6658 | -825.0766 | -808.5051 | 2520.0028 | -2520.0022 | 2520.0028 | -2520.0022
0.35 | 2851.1411 | 2795.86 | 2829.8763 | 2756.9152 | 997.8994 | 978.551 | -990.4567 | -964.9203 | 2520.0028 | -2520.0022 | 2520.0028 | -2520.0022
0.4 | 2940.0313 | 2872.8342 | 2909.4972 | 2818.8134 | 1176.0125 | 1149.1337 | -1163.7989 | -1127.5254 | 2520.0028 | -2520.0022 | 2520.0028 | -2520.0022
0.45 | 3046.6868 | 2971.295 | 3004.759 | 2893.4466 | 1371.009 | 1337.0828 | -1352.1415 | -1302.051 | 2520.0028 | -2520.0022 | 2520.0028 | -2520.0022
0.5 | 3153.3422 | 3069.7559 | 3100.0207 | 2968.0798 | 1576.6711 | 1534.8779 | -1550.0104 | -1484.0399 | 2520.0028 | -2520.0022 | 2520.0028 | -2520.0022
0.51 | 3177.9388 | 3093.2171 | 3121.3805 | 2986.5065 | 1620.7488 | 1577.5407 | -1591.9041 | -1523.1183 | 2520.0028 | -2520.0022 | 2520.0028 | -2520.0022
0.52 | 3202.5354 | 3116.6783 | 3142.7403 | 3004.9331 | 1665.3184 | 1620.6727 | -1634.2249 | -1562.5652 | 2520.0028 | -2520.0022 | 2520.0028 | -2520.0022
0.53 | 3227.1319 | 3140.1394 | 3164.1001 | 3023.3598 | 1710.3799 | 1664.2739 | -1676.973 | -1602.3807 | 2520.0028 | -2520.0022 | 2520.0028 | -2520.0022
0.54 | 3251.7285 | 3163.6006 | 3185.4598 | 3041.7865 | 1755.9334 | 1708.3443 | -1720.1483 | -1642.5647 | 2520.0028 | -2520.0022 | 2520.0028 | -2520.0022
0.55 | 3276.3251 | 3187.0618 | 3206.8196 | 3060.2131 | 1801.9788 | 1752.884 | -1763.7508 | -1683.1172 | 2520.0028 | -2520.0022 | 2520.0028 | -2520.0022
0.56 | 3300.9217 | 3210.523 | 3228.1794 | 3078.6398 | 1848.5162 | 1797.8929 | -1807.7805 | -1724.0383 | 2520.0028 | -2520.0022 | 2520.0028 | -2520.0022
0.57 | 3325.5183 | 3233.9842 | 3249.5392 | 3097.0665 | 1895.5454 | 1843.371 | -1852.2373 | -1765.3279 | 2520.0028 | -2520.0022 | 2520.0028 | -2520.0022
0.58 | 3350.1149 | 3257.4454 | 3270.899 | 3115.4931 | 1943.0666 | 1889.3183 | -1897.1214 | -1806.986 | 2520.0028 | -2520.0022 | 2520.0028 | -2520.0022
0.59 | 3374.7115 | 3280.9066 | 3292.2587 | 3133.9198 | 1991.0798 | 1935.7349 | -1942.4327 | -1849.0127 | 2520.0028 | -2520.0022 | 2520.0028 | -2520.0022
0.6 | 3399.3081 | 3304.3678 | 3313.6185 | 3151.8976 | 2039.5848 | 1982.6207 | -1988.1711 | -1891.1386 | 2520.0028 | -2520.0022 | 2520.0028 | -2520.0022
0.61 | 3426.9118 | 3332.067 | 3336.6307 | 3154.5227 | 2090.4162 | 2032.5608 | -2035.3447 | -1924.2588 | 2520.0028 | -2520.0022 | 2520.0028 | -2499.6482
0.62 | 3454.5156 | 3359.7662 | 3359.6429 | 3157.1477 | 2141.7997 | 2083.055 | -2082.9786 | -1957.4316 | 2520.0028 | -2520.0022 | 2520.0028 | -2477.1038
0.63 | 3482.1193 | 3387.4654 | 3382.6551 | 3159.7728 | 2193.7352 | 2134.1032 | -2131.0727 | -1990.6568 | 2520.0028 | -2520.0022 | 2520.0028 | -2453.8641
0.64 | 3509.7231 | 3415.1646 | 3405.6673 | 3162.3978 | 2246.2228 | 2185.7053 | -2179.6271 | -2023.9346 | 2520.0028 | -2520.0022 | 2520.0028 | -2429.9071
0.65 | 3537.3268 | 3442.8638 | 3428.6795 | 3165.0229 | 2299.2624 | 2237.8615 | -2228.6417 | -2057.2649 | 2520.0028 | -2520.0022 | 2520.0028 | -2405.2091
0.66 | 3564.9306 | 3470.563 | 3451.6917 | 3167.6479 | 2352.8542 | 2290.5716 | -2278.1165 | -2090.6476 | 2520.0028 | -2520.0022 | 2520.0028 | -2379.7449
0.67 | 3592.5343 | 3498.2622 | 3474.7039 | 3170.2729 | 2406.998 | 2343.8357 | -2328.0516 | -2124.0829 | 2520.0028 | -2520.0022 | 2520.0028 | -2353.4873
0.68 | 3620.1381 | 3525.9614 | 3497.7161 | 3172.898 | 2461.6939 | 2397.6538 | -2378.447 | -2157.5706 | 2520.0028 | -2520.0022 | 2520.0028 | -2326.4072
0.69 | 3647.7418 | 3553.6606 | 3520.7283 | 3175.523 | 2516.9419 | 2452.0258 | -2429.3026 | -2191.1109 | 2520.0028 | -2520.0022 | 2520.0028 | -2298.4733
0.7 | 3675.3456 | 3581.3598 | 3525.9112 | 3178.1481 | 2572.7419 | 2506.9519 | -2468.1379 | -2224.7037 | 2520.0028 | -2520.0022 | 2518.0043 | -2269.6517
0.71 | 3690.011 | 3596.963 | 3521.9766 | 3181.6467 | 2619.9078 | 2553.8437 | -2500.6034 | -2258.9692 | 2520.0028 | -2520.0022 | 2480.1818 | -2240.5209
0.72 | 3704.6765 | 3612.5661 | 3518.0419 | 3185.1453 | 2667.3671 | 2601.0476 | -2532.9901 | -2293.3046 | 2520.0028 | -2507.0272 | 2441.4298 | -2210.4083
0.73 | 3719.3419 | 3628.1693 | 3514.1072 | 3188.644 | 2715.1196 | 2648.5636 | -2565.2982 | -2327.7101 | 2520.0028 | -2479.6619 | 2401.7065 | -2179.2696
0.74 | 3734.0074 | 3643.7724 | 3510.1725 | 3192.1426 | 2763.1654 | 2696.3916 | -2597.5276 | -2362.1855 | 2511.519 | -2450.8264 | 2360.9661 | -2147.057
0.75 | 3748.6728 | 3659.3756 | 3506.2378 | 3195.6412 | 2811.5046 | 2744.5317 | -2629.6783 | -2396.7309 | 2479.514 | -2420.4494 | 2319.1583 | -2113.718
0.76 | 3763.3382 | 3674.9787 | 3502.3031 | 3199.1399 | 2860.1371 | 2792.9838 | -2661.7503 | -2431.3463 | 2445.8803 | -2388.4535 | 2276.2276 | -2079.1948
0.77 | 3778.0037 | 3690.5819 | 3498.3684 | 3202.6385 | 2909.0628 | 2841.748 | -2693.7436 | -2466.0316 | 2410.5321 | -2354.7532 | 2232.1125 | -2043.4239
0.78 | 3792.6691 | 3706.185 | 3494.4337 | 3206.1371 | 2958.2819 | 2890.8243 | -2725.6583 | -2500.787 | 2373.3746 | -2319.2546 | 2186.745 | -2006.3349
0.79 | 3807.3346 | 3721.7881 | 3490.499 | 3209.6358 | 3007.7943 | 2940.2126 | -2757.4942 | -2535.6122 | 2334.3029 | -2281.8538 | 2140.0488 | -1967.8496
0.8 | 3822 | 3737.3913 | 3486.5643 | 3213.1344 | 3057.6 | 2989.913 | -2789.2514 | -2570.5075 | 2293.2 | -2242.4348 | 2091.9386 | -1927.8806
0.81 | 3822 | 3745.8522 | 3483.244 | 3218.5572 | 3095.82 | 3034.1402 | -2821.4276 | -2607.0313 | 2241.335 | -2196.6796 | 2042.6783 | -1887.4581
0.82 | 3822 | 3754.313 | 3479.9237 | 3223.98 | 3134.04 | 3078.5367 | -2853.5374 | -2643.6636 | 2187.5734 | -2148.8318 | 1991.7814 | -1845.2886
0.83 | 3822 | 3762.7739 | 3476.6034 | 3229.4028 | 3172.26 | 3123.1023 | -2885.5808 | -2680.4044 | 2131.7717 | -2098.7375 | 1939.1221 | -1801.2427
0.84 | 3822 | 3771.2348 | 3473.2831 | 3234.8257 | 3210.48 | 3167.8372 | -2917.5578 | -2717.2536 | 2073.7652 | -2046.2207 | 1884.5562 | -1755.1724
0.85 | 3822 | 3779.6956 | 3469.9628 | 3240.2485 | 3248.7 | 3212.7413 | -2949.4684 | -2754.2112 | 2013.3634 | -1991.0782 | 1827.9163 | -1706.9068
0.86 | 3822 | 3788.1565 | 3466.6425 | 3245.6713 | 3286.92 | 3257.8146 | -2981.3126 | -2791.2773 | 1950.3438 | -1933.0737 | 1769.007 | -1656.2467
0.87 | 3822 | 3796.6174 | 3463.3222 | 3251.0941 | 3325.14 | 3303.0571 | -3013.0903 | -2828.4519 | 1884.4437 | -1871.9287 | 1707.597 | -1602.9575
0.88 | 3822 | 3805.0783 | 3460.0019 | 3256.5169 | 3363.36 | 3348.4689 | -3044.8017 | -2865.7349 | 1815.3494 | -1807.312 | 1643.4099 | -1546.7598
0.89 | 3822 | 3813.5391 | 3456.6816 | 3261.9398 | 3401.58 | 3394.0498 | -3076.4467 | -2903.1264 | 1742.6811 | -1738.8233 | 1576.1104 | -1487.3158
0.9 | 3822 | 3822 | 3453.3613 | 3267.3626 | 3439.8 | 3439.8 | -3108.0252 | -2940.6263 | 1665.9712 | -1665.9712 | 1505.2853 | -1424.2103
0.91 | 3822 | 3822 | 3446.2042 | 3275.0362 | 3478.02 | 3478.02 | -3136.0458 | -2980.2829 | 1584.6327 | -1584.6327 | 1428.8247 | -1357.857
0.92 | 3822 | 3822 | 3439.0471 | 3282.7098 | 3516.24 | 3516.24 | -3163.9233 | -3020.093 | 1497.912 | -1497.912 | 1347.8257 | -1286.5542
0.93 | 3822 | 3822 | 3431.89 | 3290.3834 | 3554.46 | 3554.46 | -3191.6577 | -3060.0566 | 1404.8125 | -1404.8125 | 1261.4238 | -1209.4117
0.94 | 3822 | 3822 | 3424.7328 | 3298.057 | 3592.68 | 3592.68 | -3219.2489 | -3100.1736 | 1303.9687 | -1303.9687 | 1168.4313 | -1125.2128
0.95 | 3822 | 3822 | 3417.5757 | 3305.7306 | 3630.9 | 3630.9 | -3246.6969 | -3140.4441 | 1193.4191 | -1193.4191 | 1067.1377 | -1032.214
0.96 | 3822 | 3822 | 3408.2333 | 3318.7572 | 3669.12 | 3669.12 | -3271.904 | -3186.0069 | 1070.16 | -1070.16 | 954.3053 | -929.252
0.97 | 3822 | 3822 | 3398.8909 | 3331.7838 | 3707.34 | 3707.34 | -3296.9241 | -3231.8303 | 929.147 | -929.147 | 826.2871 | -809.973
0.98 | 3822 | 3822 | 3389.5484 | 3344.8104 | 3745.56 | 3745.56 | -3321.7575 | -3277.9142 | 760.5684 | -760.5684 | 674.5116 | -665.6089
0.99 | 3822 | 3822 | 3380.206 | 3357.837 | 3783.78 | 3783.78 | -3346.404 | -3324.2586 | 539.1594 | -539.1594 | 476.8367 | -473.6812
1 | 3822 | 3822 | 3370.8636 | 3370.8636 | 3822 | 3822 | -3370.8636 | -3370.8636 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited

## CATL_50C_0.9pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 50 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V) |  |  |  | 1496 |  | VDC
Min. battery voltage |  |  |  | 1164 |  | VDC |  | Please select:
AC voltage |  |  |  | 0.9 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@min battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @50°C, 1164Vdc min. battery voltage and 0.9pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2268.0018 | 2268.0014 | 2268.0017 | 2268.0014 | 0 | 0 | 0 | 0 | 2268.0018 | -2268.0014 | 2268.0017 | -2268.0014
0.01 | 2268.0018 | 2268.0014 | 2268.0017 | 2268.0014 | 0.02268 | 0.02268 | -0.02268 | -0.02268 | 2268.0018 | -2268.0014 | 2268.0017 | -2268.0014
0.05 | 2276.7604 | 2275.0879 | 2276.5703 | 2274.7713 | 113.838 | 113.7544 | -113.8285 | -113.7386 | 2268.0018 | -2268.0014 | 2268.0018 | -2268.0014
0.1 | 2285.5208 | 2282.1757 | 2285.1406 | 2281.5427 | 228.5521 | 228.2176 | -228.5141 | -228.1543 | 2268.0018 | -2268.0014 | 2268.0018 | -2268.0014
0.15 | 2311.9069 | 2303.7809 | 2310.1053 | 2300.8304 | 346.786 | 345.5671 | -346.5158 | -345.1246 | 2268.0018 | -2268.0014 | 2268.0018 | -2268.0014
0.2 | 2338.293 | 2325.3861 | 2335.0699 | 2320.1182 | 467.6586 | 465.0772 | -467.014 | -464.0236 | 2268.0018 | -2268.0014 | 2268.0018 | -2268.0014
0.25 | 2381.7733 | 2362.1921 | 2374.6771 | 2350.6985 | 595.4433 | 590.548 | -593.6693 | -587.6746 | 2268.0018 | -2268.0014 | 2268.0018 | -2268.0014
0.3 | 2425.2535 | 2398.9982 | 2414.2844 | 2381.2787 | 727.576 | 719.6995 | -724.2853 | -714.3836 | 2268.0018 | -2268.0014 | 2268.0018 | -2268.0014
0.35 | 2484.9946 | 2450.588 | 2466.8081 | 2389.9892 | 869.7481 | 857.7058 | -863.3828 | -836.4962 | 2268.0018 | -2268.0014 | 2268.0018 | -2238.8217
0.4 | 2544.7357 | 2502.1778 | 2519.3318 | 2398.6997 | 1017.8943 | 1000.8711 | -1007.7327 | -959.4799 | 2268.0018 | -2268.0014 | 2268.0018 | -2198.4446
0.45 | 2618.9906 | 2568.6769 | 2582.8072 | 2389.1111 | 1178.5458 | 1155.9046 | -1162.2632 | -1075.1 | 2268.0018 | -2268.0014 | 2268.0018 | -2133.5445
0.5 | 2693.2455 | 2635.1761 | 2646.2826 | 2379.5226 | 1346.6228 | 1317.588 | -1323.1413 | -1189.7613 | 2268.0018 | -2268.0014 | 2268.0018 | -2060.727
0.51 | 2710.8287 | 2644.8351 | 2652.0597 | 2380.4982 | 1382.5226 | 1348.8659 | -1352.5504 | -1214.0541 | 2268.0018 | -2268.0014 | 2268.0018 | -2047.6436
0.52 | 2728.4119 | 2654.4942 | 2657.8368 | 2381.4737 | 1418.7742 | 1380.337 | -1382.0751 | -1238.3663 | 2268.0018 | -2267.3794 | 2268.0018 | -2034.1745
0.53 | 2745.995 | 2664.1533 | 2663.6138 | 2382.4493 | 1455.3774 | 1412.0013 | -1411.7153 | -1262.6981 | 2268.0018 | -2259.1957 | 2258.7383 | -2020.3114
0.54 | 2763.5782 | 2673.8124 | 2669.3909 | 2383.4249 | 1492.3322 | 1443.8587 | -1441.4711 | -1287.0494 | 2268.0018 | -2250.4544 | 2246.733 | -2006.0453
0.55 | 2781.1614 | 2683.4715 | 2675.168 | 2384.4004 | 1529.6388 | 1475.9093 | -1471.3424 | -1311.4202 | 2268.0018 | -2241.1406 | 2234.2058 | -1991.367
0.56 | 2798.7446 | 2693.1306 | 2680.9451 | 2385.376 | 1567.297 | 1508.1531 | -1501.3293 | -1335.8106 | 2268.0018 | -2231.2388 | 2221.1432 | -1976.2664
0.57 | 2816.3277 | 2702.7897 | 2686.7222 | 2386.3516 | 1605.3068 | 1540.5901 | -1531.4316 | -1360.2204 | 2268.0018 | -2220.7328 | 2207.531 | -1960.7331
0.58 | 2833.9109 | 2712.4488 | 2692.4993 | 2387.3272 | 1643.6683 | 1573.2203 | -1561.6496 | -1384.6498 | 2268.0018 | -2209.6055 | 2193.3543 | -1944.756
0.59 | 2851.4941 | 2722.1079 | 2698.2764 | 2388.3027 | 1682.3815 | 1606.0437 | -1591.9831 | -1409.0986 | 2268.0018 | -2197.8387 | 2178.5971 | -1928.3234
0.6 | 2869.0772 | 2731.767 | 2704.0535 | 2389.2783 | 1721.4463 | 1639.0602 | -1622.4321 | -1433.567 | 2268.0018 | -2185.4136 | 2163.2428 | -1911.4226
0.61 | 2877.9727 | 2738.8576 | 2701.6447 | 2391.2222 | 1755.5633 | 1670.7032 | -1648.0033 | -1458.6455 | 2268.0018 | -2170.2747 | 2140.7871 | -1894.8078
0.62 | 2886.8681 | 2745.9483 | 2699.236 | 2393.1661 | 1789.8582 | 1702.4879 | -1673.5263 | -1483.763 | 2265.0419 | -2154.476 | 2117.8254 | -1877.6824
0.63 | 2895.7635 | 2753.039 | 2696.8272 | 2395.1099 | 1824.331 | 1734.4145 | -1699.0011 | -1508.9193 | 2248.8358 | -2137.9967 | 2094.3429 | -1860.0307
0.64 | 2904.6589 | 2760.1296 | 2694.4185 | 2397.0538 | 1858.9817 | 1766.483 | -1724.4278 | -1534.1144 | 2231.867 | -2120.8143 | 2070.3236 | -1841.836
0.65 | 2913.5543 | 2767.2203 | 2692.0097 | 2398.9977 | 1893.8103 | 1798.6932 | -1749.8063 | -1559.3485 | 2214.1096 | -2102.9054 | 2045.7503 | -1823.0804
0.66 | 2922.4498 | 2774.3109 | 2689.601 | 2400.9416 | 1928.8168 | 1831.0452 | -1775.1367 | -1584.6214 | 2195.536 | -2084.2444 | 2020.6047 | -1803.7448
0.67 | 2931.3452 | 2781.4016 | 2687.1922 | 2402.8855 | 1964.0013 | 1863.5391 | -1800.4188 | -1609.9333 | 2176.1166 | -2064.8043 | 1994.867 | -1783.8087
0.68 | 2940.2406 | 2788.4923 | 2684.7835 | 2404.8293 | 1999.3636 | 1896.1747 | -1825.6528 | -1635.284 | 2155.82 | -2044.5563 | 1968.5158 | -1763.25
0.69 | 2949.136 | 2795.5829 | 2682.3748 | 2406.7732 | 2034.9039 | 1928.9522 | -1850.8386 | -1660.6735 | 2134.6123 | -2023.4691 | 1941.528 | -1742.045
0.7 | 2958.0314 | 2802.6736 | 2679.966 | 2408.7171 | 2070.622 | 1961.8715 | -1875.9762 | -1686.102 | 2112.457 | -2001.5093 | 1913.8786 | -1720.1681
0.71 | 2961.1743 | 2810.544 | 2677.3636 | 2411.6282 | 2102.4338 | 1995.4863 | -1900.9281 | -1712.2561 | 2085.2639 | -1979.1898 | 1885.4039 | -1698.2727
0.72 | 2964.3172 | 2818.4145 | 2674.7612 | 2414.5394 | 2134.3084 | 2029.2584 | -1925.828 | -1738.4684 | 2057.1592 | -1955.9065 | 1856.2149 | -1675.6277
0.73 | 2967.46 | 2826.2849 | 2672.1587 | 2417.4505 | 2166.2458 | 2063.188 | -1950.6759 | -1764.7389 | 2028.1021 | -1931.6163 | 1826.2793 | -1652.1997
0.74 | 2970.6029 | 2834.1553 | 2669.5563 | 2420.3617 | 2198.2462 | 2097.2749 | -1975.4717 | -1791.0676 | 1998.0479 | -1906.2723 | 1795.5619 | -1627.9519
0.75 | 2973.7458 | 2842.0258 | 2666.9539 | 2423.2728 | 2230.3093 | 2131.5193 | -2000.2154 | -1817.4546 | 1966.948 | -1879.8233 | 1764.0242 | -1602.8443
0.76 | 2976.8887 | 2849.8962 | 2664.3514 | 2426.1839 | 2262.4354 | 2165.9211 | -2024.9071 | -1843.8998 | 1934.7486 | -1852.2133 | 1731.6235 | -1576.8329
0.77 | 2980.0315 | 2857.7666 | 2661.749 | 2429.0951 | 2294.6243 | 2200.4803 | -2049.5467 | -1870.4032 | 1901.3909 | -1823.3805 | 1698.3127 | -1549.8693
0.78 | 2983.1744 | 2865.6371 | 2659.1466 | 2432.0062 | 2326.876 | 2235.1969 | -2074.1343 | -1896.9648 | 1866.8094 | -1793.257 | 1664.0395 | -1521.8997
0.79 | 2986.3173 | 2873.5075 | 2656.5441 | 2434.9173 | 2359.1906 | 2270.0709 | -2098.6699 | -1923.5847 | 1830.9315 | -1761.7671 | 1628.7454 | -1492.8645
0.8 | 2989.4601 | 2881.3779 | 2653.9417 | 2437.8285 | 2391.5681 | 2305.1024 | -2123.1534 | -1950.2628 | 1793.6761 | -1728.8268 | 1592.365 | -1462.6971
0.81 | 2993.7255 | 2890.3425 | 2651.5118 | 2442.3575 | 2424.9176 | 2341.1774 | -2147.7246 | -1978.3096 | 1755.61 | -1694.9832 | 1554.9257 | -1432.2714
0.82 | 2997.9908 | 2899.307 | 2649.0819 | 2446.8866 | 2458.3524 | 2377.4318 | -2172.2471 | -2006.447 | 1715.9406 | -1659.4576 | 1516.2378 | -1400.5086
0.83 | 3002.2561 | 2908.2715 | 2646.652 | 2451.4156 | 2491.8726 | 2413.8654 | -2196.7211 | -2034.675 | 1674.5485 | -1622.1274 | 1476.2056 | -1367.3099
0.84 | 3006.5214 | 2917.2361 | 2644.222 | 2455.9447 | 2525.478 | 2450.4783 | -2221.1465 | -2062.9935 | 1631.2976 | -1582.8526 | 1434.7189 | -1332.5622
0.85 | 3010.7867 | 2926.2006 | 2641.7921 | 2460.4737 | 2559.1687 | 2487.2705 | -2245.5233 | -2091.4027 | 1586.0303 | -1541.4718 | 1391.6504 | -1296.135
0.86 | 3015.052 | 2935.1651 | 2639.3622 | 2465.0028 | 2592.9448 | 2524.242 | -2269.8515 | -2119.9024 | 1538.5631 | -1497.7973 | 1346.8508 | -1257.8762
0.87 | 3019.3174 | 2944.1297 | 2636.9323 | 2469.5319 | 2626.8061 | 2561.3928 | -2294.1311 | -2148.4927 | 1488.6796 | -1451.6082 | 1300.144 | -1217.6069
0.88 | 3023.5827 | 2953.0942 | 2634.5024 | 2474.0609 | 2660.7528 | 2598.7229 | -2318.3621 | -2177.1736 | 1436.1222 | -1402.642 | 1251.3193 | -1175.1138
0.89 | 3027.848 | 2962.0587 | 2632.0724 | 2478.59 | 2694.7847 | 2636.2323 | -2342.5445 | -2205.9451 | 1380.5792 | -1350.5819 | 1200.1211 | -1130.1392
0.9 | 3032.1133 | 2971.0233 | 2629.6425 | 2483.119 | 2728.902 | 2673.9209 | -2366.6783 | -2234.8071 | 1321.6676 | -1295.039 | 1146.2346 | -1082.3665
0.91 | 3044.2651 | 2982.876 | 2623.7846 | 2489.1257 | 2770.2812 | 2714.4171 | -2387.6439 | -2265.1044 | 1262.1774 | -1236.725 | 1087.8427 | -1032.0121
0.92 | 3056.4168 | 2994.7287 | 2617.9266 | 2495.1324 | 2811.9035 | 2755.1504 | -2408.4925 | -2295.5218 | 1197.8659 | -1173.6892 | 1026.0135 | -977.8882
0.93 | 3068.5686 | 3006.5814 | 2612.0686 | 2501.1391 | 2853.7688 | 2796.1207 | -2429.2238 | -2326.0594 | 1127.8816 | -1105.0976 | 960.0907 | -919.3175
0.94 | 3080.7203 | 3018.4341 | 2606.2107 | 2507.1458 | 2895.8771 | 2837.3281 | -2449.838 | -2356.7171 | 1051.063 | -1029.8126 | 889.1725 | -855.3741
0.95 | 3092.8721 | 3030.2868 | 2600.3527 | 2513.1525 | 2938.2285 | 2878.7725 | -2470.3351 | -2387.4949 | 965.749 | -946.2068 | 811.9599 | -784.7316
0.96 | 3100.8082 | 3050.74 | 2593.3595 | 2523.5993 | 2976.7759 | 2928.7104 | -2489.6251 | -2422.6553 | 868.2263 | -854.2072 | 726.1407 | -706.6078
0.97 | 3108.7443 | 3071.1932 | 2586.3662 | 2534.0461 | 3015.482 | 2979.0574 | -2508.7753 | -2458.0247 | 755.751 | -746.6222 | 628.7583 | -616.0391
0.98 | 3116.6804 | 3091.6463 | 2579.373 | 2544.4929 | 3054.3468 | 3029.8134 | -2527.7856 | -2493.6031 | 620.2116 | -615.2298 | 513.2887 | -506.3477
0.99 | 3124.6165 | 3112.0995 | 2572.3798 | 2554.9397 | 3093.3704 | 3080.9785 | -2546.656 | -2529.3903 | 440.7814 | -439.0157 | 362.8788 | -360.4186
1 | 3132.5526 | 3132.5526 | 2565.3865 | 2565.3865 | 3132.5526 | 3132.5526 | -2565.3865 | -2565.3865 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited

## CATL_50C_1.0pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 50 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V) |  |  |  | 1496 |  | VDC
Min. battery voltage |  |  |  | 1164 |  | VDC |  | Please select:
AC voltage |  |  |  | 1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@min battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @50°C, 1164Vdc min. battery voltage and 1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2520.0019 | 2520.0016 | 2520.0019 | 2520.0015 | 0 | 0 | 0 | 0 | 2520.0019 | -2520.0016 | 2520.0019 | -2520.0015
0.01 | 2520.0019 | 2520.0016 | 2520.0019 | 2520.0015 | 0.0252 | 0.0252 | -0.0252 | -0.0252 | 2520.0019 | -2520.0016 | 2520.0019 | -2520.0015
0.05 | 2529.7338 | 2527.8754 | 2529.5226 | 2527.5237 | 126.4867 | 126.3938 | -126.4761 | -126.3762 | 2520.0019 | -2520.0016 | 2520.0019 | -2520.0016
0.1 | 2539.4675 | 2535.7508 | 2539.0451 | 2535.0474 | 253.9468 | 253.5751 | -253.9045 | -253.5047 | 2520.0019 | -2520.0016 | 2520.0019 | -2520.0016
0.15 | 2568.7854 | 2559.7566 | 2566.7836 | 2556.4783 | 385.3178 | 383.9635 | -385.0175 | -383.4717 | 2520.0019 | -2520.0016 | 2520.0019 | -2520.0016
0.2 | 2598.1034 | 2583.7623 | 2594.5221 | 2577.9092 | 519.6207 | 516.7525 | -518.9044 | -515.5818 | 2520.0019 | -2520.0016 | 2520.0019 | -2520.0016
0.25 | 2646.4147 | 2624.6579 | 2638.5302 | 2611.8872 | 661.6037 | 656.1645 | -659.6325 | -652.9718 | 2520.0019 | -2520.0016 | 2520.0019 | -2520.0016
0.3 | 2694.7261 | 2665.5535 | 2682.5382 | 2645.8653 | 808.4178 | 799.6661 | -804.7615 | -793.7596 | 2520.0019 | -2520.0016 | 2520.0019 | -2520.0016
0.35 | 2761.1051 | 2722.8756 | 2740.8979 | 2655.5436 | 966.3868 | 953.0064 | -959.3143 | -929.4403 | 2520.0019 | -2520.0016 | 2520.0019 | -2487.5796
0.4 | 2827.4841 | 2780.1976 | 2799.2576 | 2665.2219 | 1130.9936 | 1112.079 | -1119.703 | -1066.0888 | 2520.0019 | -2520.0016 | 2520.0019 | -2442.7162
0.45 | 2909.9896 | 2854.0855 | 2869.7858 | 2654.5679 | 1309.4953 | 1284.3385 | -1291.4036 | -1194.5556 | 2520.0019 | -2520.0016 | 2520.0019 | -2370.605
0.5 | 2992.495 | 2927.9734 | 2940.314 | 2643.914 | 1496.2475 | 1463.9867 | -1470.157 | -1321.957 | 2520.0019 | -2520.0016 | 2520.0019 | -2289.6967
0.51 | 3012.0319 | 2938.7057 | 2946.733 | 2644.998 | 1536.1363 | 1498.7399 | -1502.8338 | -1348.949 | 2520.0019 | -2520.0016 | 2520.0019 | -2275.1595
0.52 | 3031.5687 | 2949.438 | 2953.152 | 2646.0819 | 1576.4157 | 1533.7078 | -1535.639 | -1375.9626 | 2520.0019 | -2519.3105 | 2520.0019 | -2260.1939
0.53 | 3051.1056 | 2960.1704 | 2959.5709 | 2647.1659 | 1617.086 | 1568.8903 | -1568.5726 | -1402.9979 | 2520.0019 | -2510.2175 | 2509.7092 | -2244.7904
0.54 | 3070.6425 | 2970.9027 | 2965.9899 | 2648.2499 | 1658.1469 | 1604.2875 | -1601.6346 | -1430.0549 | 2520.0019 | -2500.5049 | 2496.37 | -2228.9393
0.55 | 3090.1793 | 2981.635 | 2972.4089 | 2649.3338 | 1699.5986 | 1639.8993 | -1634.8249 | -1457.1336 | 2520.0019 | -2490.1562 | 2482.4509 | -2212.63
0.56 | 3109.7162 | 2992.3673 | 2978.8279 | 2650.4178 | 1741.4411 | 1675.7257 | -1668.1436 | -1484.234 | 2520.0019 | -2479.1542 | 2467.9369 | -2195.8516
0.57 | 3129.253 | 3003.0997 | 2985.2469 | 2651.5018 | 1783.6742 | 1711.7668 | -1701.5907 | -1511.356 | 2520.0019 | -2467.4809 | 2452.8123 | -2178.5924
0.58 | 3148.7899 | 3013.832 | 2991.6659 | 2652.5857 | 1826.2981 | 1748.0226 | -1735.1662 | -1538.4997 | 2520.0019 | -2455.1172 | 2437.0603 | -2160.84
0.59 | 3168.3268 | 3024.5643 | 2998.0848 | 2653.6697 | 1869.3128 | 1784.4929 | -1768.8701 | -1565.6651 | 2520.0019 | -2442.043 | 2420.6634 | -2142.5815
0.6 | 3187.8636 | 3035.2966 | 3004.5038 | 2654.7537 | 1912.7182 | 1821.178 | -1802.7023 | -1592.8522 | 2520.0019 | -2428.2373 | 2403.6031 | -2123.8029
0.61 | 3197.7474 | 3043.1752 | 3001.8275 | 2656.9135 | 1950.6259 | 1856.3368 | -1831.1147 | -1620.7173 | 2520.0019 | -2411.4163 | 2378.6523 | -2105.342
0.62 | 3207.6312 | 3051.0537 | 2999.1511 | 2659.0734 | 1988.7313 | 1891.6533 | -1859.4737 | -1648.6255 | 2516.7133 | -2393.8622 | 2353.1394 | -2086.3138
0.63 | 3217.515 | 3058.9322 | 2996.4747 | 2661.2333 | 2027.0345 | 1927.1273 | -1887.7791 | -1676.577 | 2498.7065 | -2375.5518 | 2327.0477 | -2066.7008
0.64 | 3227.3988 | 3066.8107 | 2993.7983 | 2663.3931 | 2065.5352 | 1962.7588 | -1916.0309 | -1704.5716 | 2479.8523 | -2356.4604 | 2300.3595 | -2046.4845
0.65 | 3237.2826 | 3074.6892 | 2991.1219 | 2665.553 | 2104.2337 | 1998.548 | -1944.2293 | -1732.6095 | 2460.1218 | -2336.5615 | 2273.0559 | -2025.6449
0.66 | 3247.1664 | 3082.5677 | 2988.4455 | 2667.7129 | 2143.1298 | 2034.4947 | -1972.3741 | -1760.6905 | 2439.4844 | -2315.8271 | 2245.1163 | -2004.1609
0.67 | 3257.0502 | 3090.4462 | 2985.7692 | 2669.8727 | 2182.2236 | 2070.599 | -2000.4653 | -1788.8147 | 2417.9074 | -2294.2271 | 2216.5189 | -1982.0097
0.68 | 3266.934 | 3098.3247 | 2983.0928 | 2672.0326 | 2221.5151 | 2106.8608 | -2028.5031 | -1816.9822 | 2395.3556 | -2271.7292 | 2187.2398 | -1959.1667
0.69 | 3276.8178 | 3106.2032 | 2980.4164 | 2674.1925 | 2261.0043 | 2143.2802 | -2056.4873 | -1845.1928 | 2371.7914 | -2248.299 | 2157.2533 | -1935.6056
0.7 | 3286.7016 | 3114.0818 | 2977.74 | 2676.3523 | 2300.6911 | 2179.8572 | -2084.418 | -1873.4466 | 2347.1744 | -2223.8992 | 2126.5317 | -1911.2979
0.71 | 3290.1937 | 3122.8267 | 2974.8484 | 2679.5869 | 2336.0375 | 2217.2069 | -2112.1424 | -1902.5067 | 2316.9599 | -2199.0998 | 2094.8932 | -1886.9696
0.72 | 3293.6857 | 3131.5716 | 2971.9568 | 2682.8215 | 2371.4537 | 2254.7316 | -2139.8089 | -1931.6315 | 2285.7325 | -2173.2295 | 2062.461 | -1861.8086
0.73 | 3297.1778 | 3140.3165 | 2969.0653 | 2686.0561 | 2406.9398 | 2292.4311 | -2167.4176 | -1960.821 | 2253.4468 | -2146.2404 | 2029.1992 | -1835.7774
0.74 | 3300.6699 | 3149.0615 | 2966.1737 | 2689.2907 | 2442.4957 | 2330.3055 | -2194.9685 | -1990.0751 | 2220.0532 | -2118.0804 | 1995.0688 | -1808.8354
0.75 | 3304.162 | 3157.8064 | 2963.2821 | 2692.5253 | 2478.1215 | 2368.3548 | -2222.4616 | -2019.394 | 2185.4977 | -2088.6926 | 1960.0269 | -1780.9381
0.76 | 3307.6541 | 3166.5513 | 2960.3905 | 2695.7599 | 2513.8171 | 2406.579 | -2249.8968 | -2048.7775 | 2149.7207 | -2058.0148 | 1924.0261 | -1752.0366
0.77 | 3311.1461 | 3175.2963 | 2957.4989 | 2698.9945 | 2549.5825 | 2444.9781 | -2277.2742 | -2078.2258 | 2112.6565 | -2025.9784 | 1887.0141 | -1722.0769
0.78 | 3314.6382 | 3184.0412 | 2954.6073 | 2702.2291 | 2585.4178 | 2483.5521 | -2304.5937 | -2107.7387 | 2074.2327 | -1992.5078 | 1848.9327 | -1690.9996
0.79 | 3318.1303 | 3192.7861 | 2951.7157 | 2705.4637 | 2621.3229 | 2522.301 | -2331.8554 | -2137.3163 | 2034.3684 | -1957.519 | 1809.7171 | -1658.7383
0.8 | 3321.6224 | 3201.5311 | 2948.8241 | 2708.6983 | 2657.2979 | 2561.2248 | -2359.0593 | -2166.9586 | 1992.9734 | -1920.9186 | 1769.2945 | -1625.219
0.81 | 3326.3616 | 3211.4916 | 2946.1242 | 2713.7306 | 2694.3529 | 2601.3082 | -2386.3606 | -2198.1218 | 1950.6778 | -1883.3146 | 1727.6953 | -1591.4127
0.82 | 3331.1009 | 3221.4522 | 2943.4243 | 2718.7629 | 2731.5027 | 2641.5908 | -2413.6079 | -2229.3856 | 1906.6006 | -1843.8417 | 1684.7087 | -1556.1207
0.83 | 3335.8401 | 3231.4128 | 2940.7244 | 2723.7952 | 2768.7473 | 2682.0726 | -2440.8012 | -2260.75 | 1860.6095 | -1802.3638 | 1640.2284 | -1519.2332
0.84 | 3340.5793 | 3241.3734 | 2938.0245 | 2728.8274 | 2806.0866 | 2722.7537 | -2467.9406 | -2292.215 | 1812.5529 | -1758.7251 | 1594.1321 | -1480.6247
0.85 | 3345.3186 | 3251.334 | 2935.3246 | 2733.8597 | 2843.5208 | 2763.6339 | -2495.0259 | -2323.7808 | 1762.2559 | -1712.7465 | 1546.2782 | -1440.15
0.86 | 3350.0578 | 3261.2946 | 2932.6247 | 2738.892 | 2881.0497 | 2804.7134 | -2522.0572 | -2355.4471 | 1709.5145 | -1664.2192 | 1496.5009 | -1397.6402
0.87 | 3354.7971 | 3271.2552 | 2929.9247 | 2743.9243 | 2918.6734 | 2845.992 | -2549.0345 | -2387.2141 | 1654.0885 | -1612.898 | 1444.6044 | -1352.8966
0.88 | 3359.5363 | 3281.2158 | 2927.2248 | 2748.9566 | 2956.3919 | 2887.4699 | -2575.9579 | -2419.0818 | 1595.6913 | -1558.4911 | 1390.3548 | -1305.682
0.89 | 3364.2755 | 3291.1764 | 2924.5249 | 2753.9889 | 2994.2052 | 2929.147 | -2602.8272 | -2451.0501 | 1533.9768 | -1500.6465 | 1333.4679 | -1255.7102
0.9 | 3369.0148 | 3301.137 | 2921.825 | 2759.0211 | 3032.1133 | 2971.0233 | -2629.6425 | -2483.119 | 1468.5195 | -1438.9322 | 1273.594 | -1202.6294
0.91 | 3382.5167 | 3314.3066 | 2915.3162 | 2765.6952 | 3078.0902 | 3016.019 | -2652.9377 | -2516.7827 | 1402.4193 | -1374.1389 | 1208.7141 | -1146.6801
0.92 | 3396.0187 | 3327.4763 | 2908.8073 | 2772.3694 | 3124.3372 | 3061.2782 | -2676.1027 | -2550.5798 | 1330.9621 | -1304.0991 | 1140.015 | -1086.5424
0.93 | 3409.5206 | 3340.646 | 2902.2985 | 2779.0435 | 3170.8542 | 3106.8008 | -2699.1376 | -2584.5104 | 1253.2018 | -1227.8862 | 1066.7674 | -1021.4639
0.94 | 3423.0226 | 3353.8157 | 2895.7896 | 2785.7176 | 3217.6412 | 3152.5868 | -2722.0423 | -2618.5745 | 1167.8478 | -1144.2362 | 987.9694 | -950.4156
0.95 | 3436.5245 | 3366.9854 | 2889.2808 | 2792.3917 | 3264.6983 | 3198.6361 | -2744.8168 | -2652.7721 | 1073.0544 | -1051.3408 | 902.1776 | -871.924
0.96 | 3445.3424 | 3389.7111 | 2881.5105 | 2803.9992 | 3307.5287 | 3254.1227 | -2766.2501 | -2691.8393 | 964.6959 | -949.1191 | 806.823 | -785.1198
0.97 | 3454.1603 | 3412.4368 | 2873.7403 | 2815.6068 | 3350.5355 | 3310.0637 | -2787.5281 | -2731.1386 | 839.7234 | -829.5802 | 698.6204 | -684.4879
0.98 | 3462.9782 | 3435.1626 | 2865.97 | 2827.2144 | 3393.7187 | 3366.4593 | -2808.6506 | -2770.6701 | 689.124 | -683.5887 | 570.3208 | -562.6086
0.99 | 3471.7961 | 3457.8883 | 2858.1998 | 2838.8219 | 3437.0782 | 3423.3094 | -2829.6178 | -2810.4337 | 489.7571 | -487.7952 | 403.1987 | -400.4651
1 | 3480.614 | 3480.614 | 2850.4295 | 2850.4295 | 3480.614 | 3480.614 | -2850.4295 | -2850.4295 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited

## CATL_50C_1.1pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP-XT |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 50 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V) |  |  |  | 1496 |  | VDC
Min. battery voltage |  |  |  | 1164 |  | VDC |  | Please select:
AC voltage |  |  |  | 1.1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2520 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@min battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP-XT @50°C, 1164Vdc min. battery voltage and 1.1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2520.0024 | 2520.0019 | 2520.0024 | 2520.0018 | 0 | 0 | 0 | 0 | 2520.0024 | -2520.0019 | 2520.0024 | -2520.0018
0.01 | 2520.0024 | 2520.0019 | 2520.0024 | 2520.0018 | 0.0252 | 0.0252 | -0.0252 | -0.0252 | 2520.0024 | -2520.0019 | 2520.0024 | -2520.0018
0.05 | 2532.2202 | 2529.4882 | 2531.8879 | 2529.0675 | 126.611 | 126.4744 | -126.5944 | -126.4534 | 2520.0024 | -2520.0019 | 2520.0024 | -2520.0019
0.1 | 2544.4403 | 2538.9763 | 2543.7759 | 2538.135 | 254.444 | 253.8976 | -254.3776 | -253.8135 | 2520.0024 | -2520.0019 | 2520.0024 | -2520.0019
0.15 | 2580.7835 | 2567.9225 | 2578.3842 | 2564.0717 | 387.1175 | 385.1884 | -386.7576 | -384.6107 | 2520.0024 | -2520.0019 | 2520.0024 | -2520.0019
0.2 | 2617.1266 | 2596.8686 | 2612.9926 | 2590.0083 | 523.4253 | 519.3737 | -522.5985 | -518.0017 | 2520.0024 | -2520.0019 | 2520.0024 | -2520.0019
0.25 | 2676.34 | 2645.6031 | 2667.782 | 2631.2388 | 669.085 | 661.4008 | -666.9455 | -657.8097 | 2520.0024 | -2520.0019 | 2520.0024 | -2520.0019
0.3 | 2735.5533 | 2694.3377 | 2722.5714 | 2672.4692 | 820.666 | 808.3013 | -816.7714 | -801.7407 | 2520.0024 | -2520.0019 | 2520.0024 | -2520.0019
0.35 | 2816.0156 | 2762.6198 | 2794.5473 | 2727.1055 | 985.6055 | 966.9169 | -978.0915 | -954.4869 | 2520.0024 | -2520.0019 | 2520.0024 | -2520.0019
0.4 | 2896.4779 | 2830.902 | 2866.5231 | 2781.7419 | 1158.5911 | 1132.3608 | -1146.6092 | -1112.6967 | 2520.0024 | -2520.0019 | 2520.0024 | -2520.0019
0.45 | 2992.3103 | 2917.7832 | 2949.6878 | 2847.216 | 1346.5396 | 1313.0024 | -1327.3595 | -1281.2472 | 2520.0024 | -2520.0019 | 2520.0024 | -2520.0019
0.5 | 3088.1426 | 3004.6644 | 3032.8525 | 2908.3054 | 1544.0713 | 1502.3322 | -1516.4262 | -1454.1527 | 2520.0024 | -2520.0019 | 2520.0024 | -2518.6664
0.51 | 3110.0634 | 3025.9173 | 3051.8959 | 2909.4978 | 1586.1323 | 1543.2178 | -1556.4669 | -1483.8439 | 2520.0024 | -2520.0019 | 2520.0024 | -2502.6755
0.52 | 3131.9841 | 3047.1702 | 3070.9393 | 2910.6901 | 1628.6317 | 1584.5285 | -1596.8884 | -1513.5589 | 2520.0024 | -2520.0019 | 2520.0024 | -2486.2133
0.53 | 3153.9049 | 3068.4231 | 3089.9827 | 2911.8825 | 1671.5696 | 1626.2643 | -1637.6909 | -1543.2977 | 2520.0024 | -2520.0019 | 2520.0024 | -2469.2695
0.54 | 3175.8256 | 3089.676 | 3109.0262 | 2913.0749 | 1714.9458 | 1668.4251 | -1678.8741 | -1573.0604 | 2520.0024 | -2520.0019 | 2520.0024 | -2451.8332
0.55 | 3197.7463 | 3110.9289 | 3128.0696 | 2914.2672 | 1758.7605 | 1711.0109 | -1720.4383 | -1602.847 | 2520.0024 | -2520.0019 | 2520.0024 | -2433.893
0.56 | 3219.6671 | 3132.1819 | 3147.113 | 2915.4596 | 1803.0136 | 1754.0218 | -1762.3833 | -1632.6574 | 2520.0024 | -2520.0019 | 2520.0024 | -2415.4367
0.57 | 3241.5878 | 3153.4348 | 3166.1564 | 2916.6519 | 1847.705 | 1797.4578 | -1804.7092 | -1662.4916 | 2520.0024 | -2520.0019 | 2520.0024 | -2396.4516
0.58 | 3263.5085 | 3174.6877 | 3185.1999 | 2917.8443 | 1892.8349 | 1841.3188 | -1847.4159 | -1692.3497 | 2520.0024 | -2520.0019 | 2520.0024 | -2376.924
0.59 | 3285.4293 | 3195.9406 | 3204.2433 | 2919.0367 | 1938.4033 | 1885.6049 | -1890.5035 | -1722.2316 | 2520.0024 | -2520.0019 | 2520.0024 | -2356.8397
0.6 | 3307.35 | 3217.1935 | 3223.2867 | 2920.229 | 1984.41 | 1930.3161 | -1933.972 | -1752.1374 | 2520.0024 | -2520.0019 | 2520.0024 | -2336.1832
0.61 | 3331.515 | 3236.7079 | 3233.3705 | 2922.6049 | 2032.2241 | 1974.3918 | -1972.356 | -1782.789 | 2520.0024 | -2520.0019 | 2520.0024 | -2315.8762
0.62 | 3355.68 | 3256.2223 | 3243.4544 | 2924.9807 | 2080.5216 | 2018.8579 | -2010.9417 | -1813.4881 | 2520.0024 | -2520.0019 | 2520.0024 | -2294.9452
0.63 | 3379.845 | 3275.7368 | 3253.5382 | 2927.3566 | 2129.3023 | 2063.7142 | -2049.7291 | -1844.2347 | 2520.0024 | -2520.0019 | 2520.0024 | -2273.3709
0.64 | 3404.01 | 3295.2512 | 3263.622 | 2929.7325 | 2178.5664 | 2108.9608 | -2088.7181 | -1875.0288 | 2520.0024 | -2520.0019 | 2507.6853 | -2251.1329
0.65 | 3428.175 | 3314.7656 | 3273.7059 | 2932.1083 | 2228.3137 | 2154.5977 | -2127.9088 | -1905.8704 | 2520.0024 | -2519.0038 | 2487.8011 | -2228.2094
0.66 | 3452.34 | 3334.2801 | 3283.7897 | 2934.4842 | 2278.5444 | 2200.6248 | -2167.3012 | -1936.7595 | 2520.0024 | -2504.9299 | 2466.9982 | -2204.577
0.67 | 3476.505 | 3353.7945 | 3284.3461 | 2936.86 | 2329.2583 | 2247.0423 | -2200.5119 | -1967.6962 | 2520.0024 | -2489.7266 | 2438.1708 | -2180.2106
0.68 | 3500.67 | 3373.3089 | 3281.4021 | 2939.2359 | 2380.4556 | 2293.8501 | -2231.3534 | -1998.6804 | 2520.0024 | -2473.351 | 2405.9637 | -2155.0833
0.69 | 3524.835 | 3392.8234 | 3278.458 | 2941.6117 | 2432.1361 | 2341.0481 | -2262.136 | -2029.7121 | 2520.0024 | -2455.7573 | 2372.9786 | -2129.1661
0.7 | 3549 | 3412.3378 | 3275.514 | 2943.9876 | 2484.3 | 2388.6365 | -2292.8598 | -2060.7913 | 2520.0024 | -2436.8966 | 2339.1849 | -2102.4277
0.71 | 3551.1 | 3422.7864 | 3272.3333 | 2947.5456 | 2521.281 | 2430.1784 | -2323.3566 | -2092.7574 | 2500.6906 | -2410.3319 | 2304.3826 | -2075.6666
0.72 | 3553.2 | 3433.2351 | 3269.1525 | 2951.1037 | 2558.304 | 2471.9292 | -2353.7898 | -2124.7947 | 2465.8286 | -2382.5761 | 2268.7071 | -2047.9894
0.73 | 3555.3 | 3443.6837 | 3265.9718 | 2954.6617 | 2595.369 | 2513.8891 | -2384.1594 | -2156.9031 | 2429.8596 | -2353.5758 | 2232.1191 | -2019.3551
0.74 | 3557.4 | 3454.1323 | 3262.791 | 2958.2198 | 2632.476 | 2556.0579 | -2414.4654 | -2189.0827 | 2392.7317 | -2323.2731 | 2194.5757 | -1989.719
0.75 | 3559.5 | 3464.581 | 3259.6103 | 2961.7779 | 2669.625 | 2598.4357 | -2444.7077 | -2221.3334 | 2354.3879 | -2291.6049 | 2156.0295 | -1959.0319
0.76 | 3561.6 | 3475.0296 | 3256.4295 | 2965.3359 | 2706.816 | 2641.0225 | -2474.8864 | -2253.6553 | 2314.766 | -2258.5019 | 2116.4287 | -1927.2402
0.77 | 3563.7 | 3485.4782 | 3253.2488 | 2968.894 | 2744.049 | 2683.8182 | -2505.0016 | -2286.0484 | 2273.797 | -2223.8881 | 2075.7155 | -1894.2846
0.78 | 3565.8 | 3495.9269 | 3250.068 | 2972.452 | 2781.324 | 2726.823 | -2535.0531 | -2318.5126 | 2231.4046 | -2187.6794 | 2033.826 | -1860.0996
0.79 | 3567.9 | 3506.3755 | 3246.8873 | 2976.0101 | 2818.641 | 2770.0366 | -2565.041 | -2351.048 | 2187.5039 | -2149.7828 | 1990.6888 | -1824.6121
0.8 | 3570 | 3516.8241 | 3243.7065 | 2979.5681 | 2856 | 2813.4593 | -2594.9652 | -2383.6545 | 2142 | -2110.0945 | 1946.2239 | -1787.7409
0.81 | 3570 | 3522.1417 | 3240.7366 | 2985.1036 | 2891.7 | 2852.9348 | -2624.9967 | -2417.934 | 2093.5547 | -2065.4891 | 1900.4648 | -1750.554
0.82 | 3570 | 3527.4593 | 3237.7667 | 2990.6392 | 2927.4 | 2892.5166 | -2654.9687 | -2452.3241 | 2043.3378 | -2018.989 | 1853.1796 | -1711.7328
0.83 | 3570 | 3532.7769 | 3234.7968 | 2996.1747 | 2963.1 | 2932.2048 | -2684.8814 | -2486.825 | 1991.2153 | -1970.4536 | 1804.2513 | -1671.1565
0.84 | 3570 | 3538.0945 | 3231.8269 | 3001.7102 | 2998.8 | 2971.9994 | -2714.7346 | -2521.4366 | 1937.0334 | -1919.7219 | 1753.5453 | -1628.6871
0.85 | 3570 | 3543.4121 | 3228.857 | 3007.2457 | 3034.5 | 3011.9003 | -2744.5285 | -2556.1588 | 1880.6142 | -1866.6081 | 1700.906 | -1584.165
0.86 | 3570 | 3548.7297 | 3225.8871 | 3012.7812 | 3070.2 | 3051.9075 | -2774.2629 | -2590.9918 | 1821.7497 | -1810.8956 | 1646.151 | -1537.4043
0.87 | 3570 | 3554.0472 | 3222.9172 | 3018.3167 | 3105.9 | 3092.0211 | -2803.938 | -2625.9355 | 1760.1946 | -1752.3291 | 1589.0649 | -1488.1863
0.88 | 3570 | 3559.3648 | 3219.9473 | 3023.8522 | 3141.6 | 3132.241 | -2833.5536 | -2660.99 | 1695.6561 | -1690.6046 | 1529.3902 | -1436.2502
0.89 | 3570 | 3564.6824 | 3216.9774 | 3029.3877 | 3177.3 | 3172.5673 | -2863.1099 | -2696.1551 | 1627.7791 | -1625.3545 | 1466.8147 | -1381.2812
0.9 | 3570 | 3570 | 3214.0075 | 3034.9232 | 3213 | 3213 | -2892.6068 | -2731.4309 | 1556.1269 | -1556.1269 | 1400.9534 | -1322.8924
0.91 | 3570 | 3570 | 3206.8478 | 3042.2648 | 3248.7 | 3248.7 | -2918.2315 | -2768.4609 | 1480.1514 | -1480.1514 | 1329.5855 | -1261.3481
0.92 | 3570 | 3570 | 3199.6881 | 3049.6063 | 3284.4 | 3284.4 | -2943.713 | -2805.6378 | 1399.1485 | -1399.1485 | 1254.0165 | -1195.1967
0.93 | 3570 | 3570 | 3192.5283 | 3056.9478 | 3320.1 | 3320.1 | -2969.0514 | -2842.9615 | 1312.1875 | -1312.1875 | 1173.4442 | -1123.6103
0.94 | 3570 | 3570 | 3185.3686 | 3064.2893 | 3355.8 | 3355.8 | -2994.2465 | -2880.432 | 1217.9928 | -1217.9928 | 1086.7664 | -1045.4572
0.95 | 3570 | 3570 | 3178.2089 | 3071.6308 | 3391.5 | 3391.5 | -3019.2984 | -2918.0493 | 1114.7321 | -1114.7321 | 992.3954 | -959.1164
0.96 | 3570 | 3570 | 3169.6616 | 3084.3992 | 3427.2 | 3427.2 | -3042.8751 | -2961.0232 | 999.6 | -999.6 | 887.5052 | -863.6318
0.97 | 3570 | 3570 | 3161.1143 | 3097.1675 | 3462.9 | 3462.9 | -3066.2809 | -3004.2525 | 867.8845 | -867.8845 | 768.4824 | -752.9366
0.98 | 3570 | 3570 | 3152.567 | 3109.9358 | 3498.6 | 3498.6 | -3089.5157 | -3047.7371 | 710.421 | -710.421 | 627.3529 | -618.8694
0.99 | 3570 | 3570 | 3144.0197 | 3122.7041 | 3534.3 | 3534.3 | -3112.5795 | -3091.4771 | 503.6105 | -503.6105 | 443.5186 | -440.5116
1 | 3570 | 3570 | 3135.4724 | 3135.4724 | 3570 | 3570 | -3135.4724 | -3135.4724 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited