## ChangeLog
# | Date | Change | Description
1 | 2022-03-23 | Adop from Summerville Project | Original version for Lancaster SF
2 | 2023-01-04 | Update to version 0a | Update the setpoint sequence: for each SCR/XR numbers, provide Q0, Q0.3 and Q0.395
Update the PSCAD v5 input
3 | 2023-03-10 | Update to version 1 | Include more setpoints in the Setpoints Tab

## ProjectDetails
HighLevelParamName | ParamIdentifier | Value
Project Name | Name | Summerville Solar Farm
Project Name short | NameShrt | SUMSF
Developer | Dev | ESCO Pacific
Abbreviation | Abbr
Type of Test | Type
Town | Town | Richmond Valley Shire
State | State | New South Wales
Lot/DP | lot_dp | TBC
Address | addrs | TBC
LGA | lga | TBC
Network Service Provider | NSP | Transgrid
POC Substation | Sub | Tee connection to 132kV line 967
Connection type | contyp | Tee connection to 132kV line 967
POC Feeder | poc_fdr | N/A
POC circuit | CCT | 132kV line between Lismore and Koolkhan
Short Circuit Ratios | SCRHigh | 900
| SCRLow | 251.5
| SCRMVA | 90
Total Plant MW at POC | PlantMW | 90
Total Plant MW at terminals | GenMW | 91
Maximum Plant MVAr at terminals | GenMVArMax | 50
Minimum Plant MVAr at terminal | GenMVArMin | -50
Total Plant Maximum MVA at POC (base for per-unitisation) | TotalMVA | 97
Nominal POC voltage (kV) | VPOCkv | 132 | VLL | VLN
Normal POC voltage (p.u.) | VPOCpu | 1 | 132 | 76.2102
Nominal voltage at Bus where test source is connected (optional) | VbaseTestSrc | 132
Normal frequency at POC | Fbase | 50
Inverter/Plant Model | plnt_mdl
Number of generator aggregates in model | Gens | 2
Generators Per Site | genPerSite1 | 26
| genPerSite2 | 36
Generator MVA | genMVA1 | 4.2
| genMVA2 | 3.6
Generator terminal voltage in kV | VTERkv | 0.63
| VTERkv2 | 0.63
Pmax | Pmax | 1
Pmax_at_Qmax | PmaxQmax | 1
Pmax_at_Qmin | PmaxQmin | 1
Pmin | Pmin | 0
Pmin_at_Qmax | PminQmax | 0
Pmin_at_Qmin | PminQmin | 0
Note on C22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Prated
Note on B26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Lancaster, the Qmax for half of SF only
Note on B31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is in case the GridSource for automated testing is connected at a different point than the POC. If this entry is left empty, VPOCpu is assumed.

## SimulationSettings
ParamIdentifier | Value | unit
Batches | test1
Name of test run | script_upgrade
model(s) for PSSE network studies | HL_dyn_genon | folder name and path relative to relative to PSSE_sim\base_model | HighLoad, LowLoad
PSSE start offset | 0 | seconds
default_sim_duration PSSE | 15
default_sim_duration PSCAD | 15
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: define which test batches should be included in next test run
Note on A3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: name of test run used for labelling the output files
Note on A4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: list of folder names of one or more network cases, used in Network fault studies and voltge control studies carried out on the wider network in PSS/E.
Note on A5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: provide a negative number to delay the PSSE simulation [second]

## ModelDetailsPSCAD
ParamIdentifier | Value
workspace_folder_path |  |  | This sheet lists all relevant information about the project file and PSCAD-specific setup
workspace_folder_name |  |  |  | Variable
Workspace File Name | Workspace_SUMSF.pswx |  | 1a. Setpoint to PPC |  | Description | Note
Projects | 1 |  |  | PoiWLimSales | Active power sales limit POI | Active Power setpoint atPOC
Project1 | SUMSF_V0 |  |  | BessWSpt | P setpoint Bess | Active Power setpoint from BESS (at BESS terminal?)
DllPath |  |  |  | PoiVArSpt | Q setpoint Poi | Reactive power setpoint POC
|  |  |  | PoiPfSpt | PF setpoint Poi | Power Factor setpoint POC
result_path |  |  |  | PoiVolSpt | V setpoint | Voltage setpoint POC
|  |  |  | 50 | freq setpoint | Frequency setpoint
default_sim_duration | 15
disturbance_offset | 5 |  | 1b. Measurement feedback to POC
POC P, Q, V, F,
max_processes | 8 |  |  | McbStt
GcbStt
pscad version | PSCAD 5.0.1 (x64) | PSCAD 4.6.2 (x64) |  | Vrms_abc_POI
compiler | Intel Fortran v2021 | Intel Fortran v2015
compiler_short | gf81_x86 |  |  | P, Q, V, H from PV and BESS
create example cases | no
1c. Feed back from INV
GridSourceID | 1927070795 |  |  | PCU1_Fb_SI |  | Include feedback at INV terminal and number of INV scalled
GridSourceCanvas (optional) |  |  |  | PCU2_Fb_SI |  | Include feedback at INV terminal and number of INV scalled
Fprofile | 270230556
Vprofile | 976319064
PHprofile | 1827520263 |  | 2a command (spnt) from PPC to PV INV
StpBlockID | 163769877 |  |  | WSpt_pu_SC | P cmd
StpBlockCanvas (optional) |  |  |  | VArSpt_pu_SC | Q cmd
Vstp_profile | 626637343 |  |  | Fsys_
Qstp_profile | 47901822 |  |  | WSptMin_pu_SCDC
Q1stp_profile | 2052650100 |  |  | HybridPwrAtDisSpntTot_pu_SC
PFstp_profile | 1775954593 |  |  | HybridPwrAtChrSpntTot_pu_SC
PF1stp_profile | 1066702073
Pstp_profile | 305157189 |  | 2b command (spnt) from PPC to BESS INV
P1stp_profile | 2104320057 |  |  | WSpt_pu_SCS | P cmd
AUX_profile | 935825497 |  |  | VArSpt_pu_SCS | Q cmd
FaultBlockID | 1591544161 |  |  | VtgNomSpntPc |  | Channel 4
FaultBlockCanvas (optional) |  |  |  | Fsys_
SCSOpCmd
plotStep_us | 5000
3 PPC Debug signals
4a. INV input
WSpt (pu)
VArSpt (pu)
PFSpt
VolSpt (pu)
HzSpt (Hz)
4b. INV fb
WRtg (kW)
VARtg (kVAr)
Waval (kW)
Qaval (kVAr)
InvMs_TotW (kW)
InvMs_TotVAr (kVAr)
WMs_DC_PV (kW)
WMs_DC_Bat (kW)
Note on B7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: contains the path to the dll files that must be copied to the directory containing the compiled files. Expressed relative to the "PSCAD_sim" directory.
Note on A19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: determines wether the test script generates an example case for each test. This can be handy for debugging or sharing the cases with third parties. However, it also takes up disk space.
Note on A23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Inside the GridSourceCanvas
Note on A28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This normally remain the same with StpBlockID for the tests.

## ModelDetailsPSSE
ParamIdentifier | Value
PSSEversion | PSS/E v34.5
savFileName | SUMSF_SMIB_V0.sav
dyrFileName | SUMSF_SMIB_V0.dyr
dll1 | SMAHYCF_G14_346_IVF150.dll
dll2 | SMAGF_G302_346_IVF150.dll
dll3 | SMASC_G188_349_IVF150.dll
savFileHigh | 20210720-180037-SubTrans-SystemNormal.sav
dyrFileHigh
savFileLow
dyrFileLow
default_sim_duration | 15
start_offset | 0
InfiniteBus | 9900
DummyTxBus | 10
FaultBus | 9910
POC | 9920
Generator1 | 9942
Generator2 | 9944
POCfromBus1 | 9920
POCtoBus1 | 9910
POCmeasBus1 | 9920
HVfromBus1 | 10
HVtoBus1 | 9900 | INF bus
HVmeasBus1 | 10 | DummyTxBus
MVfromBus1 | 9941
MVtoBus1 | 9940
MVmeasBus1 | 9941
LVfromBus1 | 9942
LVtoBus1 | 9941
LVmeasBus1 | 9942
MVfromBus2 | 9943
MVtoBus2 | 9940
MVmeasBus2 | 9943
LVfromBus2 | 9944
LVtoBus2 | 9943
LVmeasBus2 | 9944
Vset1_bus | 9920
Vset1_mac | 1
Vset1_var | 16
Vset1_model | SMAHYCF14
Vset1_type | OTHER
Pset1_bus | 9920
Pset1_mac | 1
Pset1_var | 18
Pset1_model | SMAHYCF14
Pset1_type | OTHER
Pprim1_bus | 9942
Pprim1_mac | 1
Pprim1_con | 0
Pprim1_model | SMASC188
Pprim1_type | GEN
Qset1_bus | 9920
Qset1_mac | 1
Qset1_var | 14
Qset1_model | SMAHYCF14
Qset1_type | OTHER
PFset1_bus | 9920
PFset1_mac | 1
PFset1_var | 15
PFset1_model | SMAHYCF14
PFset1_type | OTHER
Plot Channels
from bus | tobus | item | label
Note on A15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: start_offset is to delay the start of Dynamic simulation in PSSE compared to PSCAD
Note on A17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This has been fixed to 1 in run_simulation script - line805
Note on A18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is dummy bus inserted for including a dummy transformer for Vangle testing purposes DUM_TR_POC (default value: 10 line 483 in run_simulation script)
Note on A19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This has been fixed to 2 in run_simulation script - line805
Note on A20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: POC_To bus
Note on A24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The numbering of these must match the Generator numbers
Note on C24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: by default the voltages and angles will alwaye be read at the toBus. But for example for the LV it may be preferred to read at the fromBus.
Note on A43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: for the setpoints common ways are adjusting variables or writing to VREF
Note on A45: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This should be "_con" or "_var" depending on the specific OEM model
Note on A49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Active Power setpoint to HyCon
Note on A73: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Active Power setpoint to HyCon

## LargeDist
Description: For every fault, specify the impedance in Ohms and the X/R ratio. For 3-phase faults, a residual voltage can be set, instead of the fault impedance and X/R. In that case, the fault impedance will be calculated so that the voltage initially dips to the value specified under 'Vresidual'. It is important that Vpoc and SCR as well as X/R are correctly defined for this to work. If both an impedance and 'Vresidual' are defined, only the impedance value is used in the simulation. For Multifault-sequences there are two option: 1) define define the first fault as a regular fault, subsequently define all other faults of the Multifault sequence for any fault belonging to the series, do not set caseID, it will then be interpreted as belonging to the multifaul sequence. 2) select one of the pre-defined multifault sequences under "fault type". The other fault parameters (impedance, fault X_R, residual voltage, and duration will then be ignored). The "Ftime" will be interpreted as the start time of the multifault sequence.
608
38
PSSE-specific settings
CaseNr | Test Type | Ftype | Ftime | Fduration | F_Impedance | Vresidual | Fault X_R | Vpoc | Active Power | Reactive Power | SCR | X_R | SCL_post | X_R_post | setpoint ID | init_help | TimeStep | AccFactor | run in PSCAD? | run in PSS/E? | Comment/Corresponding DMAT case | test group | simulation batch
1 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 51 | 0 | 1 | 0.2 | no | no | 1 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
2 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 2 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
3 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 3 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
4 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 4 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
5 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 5 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
6 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 6 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
7 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 1 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
8 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 2 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
9 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 3 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
10 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 4 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
11 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 5 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
12 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 6 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
13 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 56 | 0 | 1 | 0.2 | no | no | 7 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
14 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 8 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
15 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 9 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
16 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 10 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
17 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 11 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
18 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 12 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
19 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 7 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
20 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 8 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
21 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 9 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
22 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 10 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
23 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 11 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
24 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 12 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
25 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 51 | 0 | 1 | 0.2 | no | no | 13 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
26 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 14 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
27 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 15 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
28 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 16 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
29 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 17 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
30 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 18 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
31 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 13 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
32 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 14 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
33 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 15 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
34 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 16 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
35 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 17 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
36 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 18 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
37 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 56 | 0 | 1 | 0.2 | no | no | 19 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
38 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 20 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
39 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 21 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
40 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 22 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
41 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 23 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
42 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 24 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
43 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 19 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
44 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 20 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
45 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 21 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
46 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 22 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
47 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 23 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
48 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 24 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
49 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 51 | 0 | 1 | 0.2 | no | no | 25 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
50 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 26 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
51 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 27 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
52 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 28 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
53 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 29 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
54 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 30 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
55 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 25 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
56 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 26 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
57 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 27 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
58 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 28 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
59 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 29 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
60 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 30 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
61 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 56 | 0 | 1 | 0.2 | no | no | 31 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
62 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 32 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
63 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 33 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
64 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 34 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
65 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 35 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
66 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 36 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
67 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 31 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
68 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 32 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
69 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 33 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
70 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 34 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
71 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 35 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
72 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 36 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
73 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 51 | 0 | 1 | 0.2 | yes | no | 37 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
74 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 38 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
75 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 39 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
76 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 40 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
77 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 41 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
78 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 42 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
79 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | no | 37 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
80 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 38 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
81 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 39 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
82 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 40 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
83 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 41 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
84 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 42 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
85 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 56 | 0 | 1 | 0.2 | yes | no | 43 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
86 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 44 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
87 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 45 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
88 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 46 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
89 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 47 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
90 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 48 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
91 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | yes | no | 43 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
92 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 44 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
93 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 45 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
94 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 46 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
95 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 47 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
96 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 48 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
97 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 51 | 0 | 1 | 0.2 | yes | no | 49 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
98 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 50 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
99 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 51 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
100 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 52 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
101 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 53 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
102 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 54 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
103 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | no | 49 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
104 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 50 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
105 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 51 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
106 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 52 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
107 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 53 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
108 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 54 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
109 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 56 | 0 | 1 | 0.2 | yes | no | 55 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
110 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 56 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
111 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 57 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
112 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 58 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
113 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 59 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
114 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 60 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
115 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | yes | no | 55 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
116 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 56 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
117 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 57 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
118 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 58 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
119 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 59 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
120 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 60 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
121 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 51 | 0 | 1 | 0.2 | yes | no | 61 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl
122 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 62 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
123 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 63 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
124 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 64 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
125 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 65 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
126 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 66 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
127 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | no | 61 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
128 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 62 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
129 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 63 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
130 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 64 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
131 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 65 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
132 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 66 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
133 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 56 | 0 | 1 | 0.2 | yes | no | 67 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
134 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 68 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
135 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 69 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
136 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 70 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
137 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 71 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
138 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 72 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
139 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | yes | no | 67 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
140 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 68 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
141 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 69 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
142 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 70 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
143 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 71 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
144 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 72 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
145 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 51 | 0 | 1 | 0.2 | yes | no | 73 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
146 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 74 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
147 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 75 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
148 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 76 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
149 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 77 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
150 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 78 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
151 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | no | 73 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
152 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 74 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
153 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 75 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
154 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 76 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
155 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 77 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
156 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 78 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
157 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 56 | 0 | 1 | 0.2 | yes | no | 79 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
158 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 80 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
159 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 81 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
160 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 82 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
161 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 83 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
162 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 84 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
163 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | yes | no | 79 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
164 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 80 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
165 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 81 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
166 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 82 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
167 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 83 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
168 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 84 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
169 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 51 | 0 | 1 | 0.2 | yes | no | 85 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
170 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 86 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
171 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 87 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
172 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 88 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
173 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 89 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
174 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 90 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
175 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | no | 85 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
176 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 86 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
177 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 87 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
178 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 88 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
179 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 89 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
180 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 90 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
181 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 56 | 0 | 1 | 0.2 | yes | no | 91 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
182 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 92 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
183 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 93 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
184 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 94 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
185 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 95 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
186 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 96 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
187 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | yes | no | 91 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
188 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 92 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
189 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 93 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
190 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 94 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
191 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 95 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
192 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 96 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
193 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 51 | 0 | 1 | 0.2 | no | no | 97 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
194 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 98 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
195 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 99 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
196 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 100 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
197 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 101 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
198 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 102 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
199 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 97 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
200 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 98 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
201 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 99 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
202 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 100 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
203 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 101 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
204 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 102 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
205 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 56 | 0 | 1 | 0.2 | no | no | 103 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
206 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 104 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
207 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 105 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
208 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 106 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
209 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 107 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
210 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 108 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
211 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 103 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
212 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 104 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
213 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 105 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
214 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 106 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
215 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 107 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
216 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 108 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
217 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 51 | 0 | 1 | 0.2 | no | no | 97 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
218 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 98 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
219 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 99 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
220 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 100 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
221 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 101 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
222 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 102 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
223 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 97 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
224 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 98 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
225 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 99 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
226 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 100 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
227 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 101 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
228 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 102 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
229 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 56 | 0 | 1 | 0.2 | no | no | 103 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
230 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 104 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
231 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 105 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
232 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 106 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
233 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 107 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
234 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 108 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
235 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 103 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
236 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 104 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
237 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 105 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
238 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 106 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
239 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 107 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
240 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 108 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
241 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 51 | 0 | 1 | 0.2 | no | no | 97 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
242 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 98 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
243 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 99 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
244 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 100 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
245 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 101 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
246 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 102 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
247 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 97 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
248 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 98 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
249 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 99 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
250 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 100 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
251 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 101 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
252 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 102 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
253 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 56 | 0 | 1 | 0.2 | no | no | 103 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
254 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 104 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
255 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 105 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
256 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 106 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
257 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 107 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
258 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 108 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
259 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 103 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
260 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 104 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
261 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 105 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
262 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 106 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
263 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 107 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
264 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 108 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
265 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 51 | 0 | 1 | 0.2 | no | no | 109 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
266 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 110 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
267 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 111 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
268 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 112 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
269 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 113 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
270 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 114 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
271 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 109 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
272 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 110 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
273 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 111 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
274 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 112 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
275 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 113 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
276 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 114 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
277 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 56 | 0 | 1 | 0.2 | no | no | 115 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
278 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 116 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
279 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 117 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
280 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 118 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
281 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 119 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
282 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 120 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
283 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 115 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
284 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 116 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
285 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 117 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
286 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 118 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
287 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 119 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
288 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 120 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
289 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 51 | 0 | 1 | 0.2 | no | no | 109 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
290 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 110 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
291 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 111 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
292 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 112 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
293 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 113 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
294 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 114 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
295 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 109 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
296 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 110 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
297 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 111 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
298 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 112 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
299 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 113 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
300 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 114 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
301 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 56 | 0 | 1 | 0.2 | no | no | 115 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
302 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 116 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
303 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 117 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
304 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 118 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
305 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 119 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
306 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 120 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
307 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 115 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
308 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 116 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
309 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 117 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
310 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 118 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
311 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 119 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
312 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 120 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
313 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 51 | 0 | 1 | 0.2 | no | no | 109 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
314 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 110 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
315 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 111 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
316 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 112 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
317 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 113 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
318 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 114 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
319 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 109 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
320 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 110 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
321 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 111 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
322 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 112 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
323 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 113 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
324 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 114 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
325 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 56 | 0 | 1 | 0.2 | no | no | 115 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
326 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 116 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
327 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 117 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
328 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 118 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
329 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 119 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
330 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 120 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
331 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 115 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
332 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 116 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
333 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 117 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
334 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 118 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
335 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 119 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
336 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 120 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
337 | Multifault | 3PHG | 5 | 0.1 |  | 0.2 | 1.13 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | no | 121 | Multiple Fault Ride Through (MFRT) test [PSCAD/EMTDC models] | DMATsl5
|  | 3PHG | 5.25 | 0.1 |  | 0.2 | 1.13 | [9 empty] | 1 |  | yes | no |  |  | DMATsl5
|  | 3PHG | 5.5 | 0.1 |  | 0.2 | 1.13 | [9 empty] | 1 |  | yes | no |  |  | DMATsl5
|  | 2PHG | 8 | 0.1 |  | 0.2 | 1.13 | [9 empty] | 1 |  | yes | no |  |  | DMATsl5
|  | 2PHG | 11 | 0.1 |  | 0.2 | 1.13 | [9 empty] | 1 |  | yes | no |  |  | DMATsl5
|  | 2PHG | 13 | 0.1 |  | 0.2 | 1.13 | [9 empty] | 1 |  | yes | no |  |  | DMATsl5
338 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | yes | no | 122 | Multiple Fault Ride Through (MFRT) test [PSCAD/EMTDC models] | DMATsl5
339 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | no | 123 | Multiple Fault Ride Through (MFRT) test [PSCAD/EMTDC models] | DMAT
340 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | no | 124 | Multiple Fault Ride Through (MFRT) test [PSCAD/EMTDC models] | DMAT
341 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | no | 125 | Multiple Fault Ride Through (MFRT) test [PSCAD/EMTDC models] | DMAT
342 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | yes | 126 | MFRT Test [PSS®E models] | DMATsl5
343 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | yes | 127 | MFRT Test [PSS®E models] | DMATsl5
344 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | no | 128 | MFRT Test [PSS®E models] | DMAT
345 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | no | 129 | MFRT Test [PSS®E models] | DMAT
346 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | no | 130 | MFRT Test [PSS®E models] | DMAT
347 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 90 | 14 | 31 | 0 | 1 | 0.2 | yes | yes | 200 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMATsl5
348 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 90 | 14 | 129 | 0 | 1 | 0.2 | no | no | 201 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
349 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 90 | 14 | 36 | 0 | 1 | 0.2 | no | no | 202 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
350 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 90 | 14 | 31 | 0 | 1 | 0.2 | yes | yes | 203 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMATsl5
351 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 90 | 14 | 129 | 0 | 1 | 0.2 | no | no | 204 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
352 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 90 | 14 | 36 | 0 | 1 | 0.2 | no | no | 205 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
353 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 90 | 3 | 41 | 0 | 1 | 0.2 | yes | yes | 200 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMATsl5
354 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 90 | 3 | 130 | 0 | 1 | 0.2 | no | no | 201 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
355 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 90 | 3 | 46 | 0 | 1 | 0.2 | no | no | 202 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
356 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 90 | 3 | 41 | 0 | 1 | 0.2 | yes | yes | 203 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMATsl5
357 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 90 | 3 | 130 | 0 | 1 | 0.2 | no | no | 204 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
358 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 90 | 3 | 46 | 0 | 1 | 0.2 | no | no | 205 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
359 | Fault | 3PHG | 5 | 0.43 |  | 0 | [8 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 206 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
360 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | [8 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 207 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
361 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | [8 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 208 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
362 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | [8 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 209 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
363 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | [8 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 210 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
364 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | [8 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 211 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
365 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | [8 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 212 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
366 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | [8 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 213 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
367 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [8 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 214 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
368 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | [8 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 215 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
369 | Fault | 3PHG | 5 | 0.43 |  | 0 | [8 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 216 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
370 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | [8 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 217 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
371 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | [8 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 218 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
372 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | [8 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 219 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
373 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | [8 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 220 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
374 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | [8 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 221 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
375 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | [8 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 222 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
376 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | [8 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 223 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
377 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [8 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 224 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
378 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | [8 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 225 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
379 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255
380 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255
381 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255
382 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255
383 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255
384 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255
385 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255
386 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255
387 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255
388 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255
389 | Multifault | 3PHG | 5 | 0.22 |  | 0.4 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Multiple Fault Ride Through (MFRT) test [PSCAD/EMTDC models] | S5255mulf
|  | 2PHG | 5.32 | 0.43 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 1PHG | 5.85 | 0.49 |  | 0.85 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 3PHG | 6.44 | 0.22 |  | 0.4 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 2PHG | 7.66 | 0.12 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 2PHG | 7.88 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 2PHG | 10.1 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 2PHG | 11.82 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 2PHG | 12.54 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 2PHG | 13.86 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 2PHG | 15.13 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 2PHG | 17.35 | 0.12 |  | 0.85 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 1PHG | 19.47 | 0.12 |  | 0.85 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 1PHG | 24.59 | 0.22 |  | 0.85 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 2PHG | 25.81 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
390 | Fault | 3PHG | 5 | 5 |  | 0 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
391 | Fault | 3PHG | 5 | 5 |  | 0.05 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
392 | Fault | 3PHG | 5 | 5 |  | 0.1 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
393 | Fault | 3PHG | 5 | 5 |  | 0.15 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
394 | Fault | 3PHG | 5 | 5 |  | 0.2 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
395 | Fault | 3PHG | 5 | 5 |  | 0.25 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
396 | Fault | 3PHG | 5 | 5 |  | 0.3 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
397 | Fault | 3PHG | 5 | 5 |  | 0.35 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
398 | Fault | 3PHG | 5 | 5 |  | 0.4 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
399 | Fault | 3PHG | 5 | 5 |  | 0.45 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
400 | Fault | 3PHG | 5 | 5 |  | 0.5 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
401 | Fault | 3PHG | 5 | 5 |  | 0.55 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
402 | Fault | 3PHG | 5 | 5 |  | 0.6 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
403 | Fault | 3PHG | 5 | 5 |  | 0.65 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
404 | Fault | 3PHG | 5 | 5 |  | 0.7 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
405 | Fault | 3PHG | 5 | 5 |  | 0.75 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
406 | Fault | 3PHG | 5 | 5 |  | 0.8 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
407 | Fault | 3PHG | 5 | 5 |  | 0.85 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
408 | Fault | 3PHG | 5 | 5 |  | 0.9 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
409 | Fault | 3PHG | 5 | 5 |  | 0.95 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
410 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | Benchmarking
411 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | Benchmarking
412 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | Benchmarking
413 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | Benchmarking
414 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | Benchmarking
415 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | Benchmarking
416 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | Benchmarking
417 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | Benchmarking
418 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | Benchmarking
419 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | Benchmarking
420 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 311 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg2
421 | Fault | 3PHG | 10 | 0.43 |  | 0.1 | 3 | [7 empty] | 311 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg2
422 | Fault | 3PHG | 10 | 0.43 |  | 0.2 | 3 | [7 empty] | 311 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg2
423 | Fault | 3PHG | 10 | 0.43 |  | 0.3 | 3 | [7 empty] | 311 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg2
424 | Fault | 3PHG | 10 | 0.43 |  | 0.4 | 3 | [7 empty] | 311 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg2
425 | Fault | 3PHG | 10 | 0.43 |  | 0.5 | 3 | [7 empty] | 311 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg2
426 | Fault | 3PHG | 10 | 0.43 |  | 0.6 | 3 | [7 empty] | 311 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg2
427 | Fault | 3PHG | 10 | 0.43 |  | 0.7 | 3 | [7 empty] | 311 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg2
428 | Fault | 3PHG | 10 | 0.43 |  | 0.8 | 3 | [7 empty] | 311 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg2
429 | Fault | 3PHG | 10 | 0.43 |  | 0.9 | 3 | [7 empty] | 311 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg2
430 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg
431 | Fault | 3PHG | 10 | 0.43 |  | 0.1 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg
432 | Fault | 3PHG | 10 | 0.43 |  | 0.2 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg
433 | Fault | 3PHG | 10 | 0.43 |  | 0.3 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg
434 | Fault | 3PHG | 10 | 0.43 |  | 0.4 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg
435 | Fault | 3PHG | 10 | 0.43 |  | 0.5 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg
436 | Fault | 3PHG | 10 | 0.43 |  | 0.6 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg
437 | Fault | 3PHG | 10 | 0.43 |  | 0.7 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg
438 | Fault | 3PHG | 10 | 0.43 |  | 0.8 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg
439 | Fault | 3PHG | 10 | 0.43 |  | 0.9 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg
440 | Fault | 3PHG | 10 | 0.01 |  | 1.019 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | no |  | Low SCR test Table 4 Appendix B SSIAG [PSCAD/EMTDC models] | S52515dbg3
441 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 314 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
442 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 315 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
443 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 316 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
444 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 317 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
445 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 318 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
446 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 319 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
447 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 320 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
448 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 321 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
449 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 322 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
450 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 323 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
451 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 324 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
452 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 325 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
453 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 326 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
454 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 327 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
455 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 328 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
456 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 329 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
457 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 330 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
458 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 331 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
459 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 332 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
460 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 333 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
461 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 334 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
462 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 335 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
463 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 336 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
464 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 337 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
465 | Fault | 3PHG | 5 | 5 |  | 0 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
466 | Fault | 3PHG | 5 | 5 |  | 0.05 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
467 | Fault | 3PHG | 5 | 5 |  | 0.1 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
468 | Fault | 3PHG | 5 | 5 |  | 0.15 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
469 | Fault | 3PHG | 5 | 5 |  | 0.2 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
470 | Fault | 3PHG | 5 | 5 |  | 0.25 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
471 | Fault | 3PHG | 5 | 5 |  | 0.3 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
472 | Fault | 3PHG | 5 | 5 |  | 0.35 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
473 | Fault | 3PHG | 5 | 5 |  | 0.4 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
474 | Fault | 3PHG | 5 | 5 |  | 0.45 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
475 | Fault | 3PHG | 5 | 5 |  | 0.5 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
476 | Fault | 3PHG | 5 | 5 |  | 0.55 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
477 | Fault | 3PHG | 5 | 5 |  | 0.6 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
478 | Fault | 3PHG | 5 | 5 |  | 0.65 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
479 | Fault | 3PHG | 5 | 5 |  | 0.7 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
480 | Fault | 3PHG | 5 | 5 |  | 0.75 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
481 | Fault | 3PHG | 5 | 5 |  | 0.8 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
482 | Fault | 3PHG | 5 | 5 |  | 0.85 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
483 | Fault | 3PHG | 5 | 5 |  | 0.9 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
484 | Fault | 3PHG | 5 | 5 |  | 0.95 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
485 | Fault | 3PHG | 5 | 5 |  | 0 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
486 | Fault | 3PHG | 5 | 5 |  | 0.05 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
487 | Fault | 3PHG | 5 | 5 |  | 0.1 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
488 | Fault | 3PHG | 5 | 5 |  | 0.15 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
489 | Fault | 3PHG | 5 | 5 |  | 0.2 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
490 | Fault | 3PHG | 5 | 5 |  | 0.25 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
491 | Fault | 3PHG | 5 | 5 |  | 0.3 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
492 | Fault | 3PHG | 5 | 5 |  | 0.35 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
493 | Fault | 3PHG | 5 | 5 |  | 0.4 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
494 | Fault | 3PHG | 5 | 5 |  | 0.45 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
495 | Fault | 3PHG | 5 | 5 |  | 0.5 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
496 | Fault | 3PHG | 5 | 5 |  | 0.55 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
497 | Fault | 3PHG | 5 | 5 |  | 0.6 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
498 | Fault | 3PHG | 5 | 5 |  | 0.65 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
499 | Fault | 3PHG | 5 | 5 |  | 0.7 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
500 | Fault | 3PHG | 5 | 5 |  | 0.75 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
501 | Fault | 3PHG | 5 | 5 |  | 0.8 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
502 | Fault | 3PHG | 5 | 5 |  | 0.85 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
503 | Fault | 3PHG | 5 | 5 |  | 0.9 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
504 | Fault | 3PHG | 5 | 5 |  | 0.95 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
Note on C6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Multifault, include a few sequences that are hard-coded. In case a multifault sequence is chosen, The Fault X_R, Impedance, residual voltage, duration and application time are ignored.
Note on A7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MAT
Note on A31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MAT
Note on A55: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MAT
Note on Y465: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be checked again: we want to change the SCR only, not after the fault is applied Reply: Assuming that the fault happens, so the SCR change, but voltage level does not change much

## SmallDist
When defining the SmallDist tests, make sure the initial values of the profiles do not contradict the Initialisation parameters in the Setpoints tab, as they will overwrite the parameters form the "Setpoints" sheet, where applicable. E.G.: When running S5.2.5.4 on an inifinite grid, and the selected initial setpoint defined in the "PSCAD setpoint ID" inisilises to 1.04pu at the POC, then the test profile selected under "Test profile" and defined in the "Profiles" sheet, should also start with 1.04pu to ensure smooth intialisation. If the profile starts at a different voltage, it might for example lead to different power flows at the POC and an incoherent transformer tap. (In the future a routine could be added that scales or offsets the profile to match the initial valuye of the profile, and notifies the user). Grid SCR and Grid X/R refer to the point where the grid source is attached, which may be differnet from the POC. For example in the case of Mulwala the grid source is connected at 132 kV level, (which is where the plant controls the voltage) but the POC is at 22 kV level. | [10 empty] | PSSE-specific settings
CaseNr | Test Type | Test profile | Vpoc | ActivePower | ReactivePower | Secondary SCL time | Secondary SCL | Secondary X_R | setpoint ID | init_help | TimeStep | AccFactor | run in PSCAD? | run in PSS/E? | Comment/Corresponding DMAT case | test group | simulation batch
1 | V_profile | FLAT_RUN_300 | [6 empty] | 81 | 0 | 1 | 0.2 | yes | no | 0.1 | Pre-requisite tests – single machine infinite bus (SMIB) flat run [PSCAD/EMTDC models] | DMATsllong
2 | V_profile | FLAT_RUN_300 | [6 empty] | 81 | 0 | 1 | 0.2 | yes | no | 0.2 | Pre-requisite tests – single machine infinite bus (SMIB) flat run [PSCAD/EMTDC models] | DMATsllong
3 | V_profile | FLAT_RUN_300 | [6 empty] | 86 | 0 | 1 | 0.2 | yes | no | 0.3 | Pre-requisite tests – single machine infinite bus (SMIB) flat run [PSCAD/EMTDC models] | DMATsllong
4 | V_profile | FLAT_RUN_5 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | no | 0.4 | Pre-requisite tests – single machine infinite bus (SMIB) flat run [PSCAD/EMTDC models] | DMATsl1
5 | V_profile | FLAT_RUN_5 | [6 empty] | 1 | 0 | 1 | 0.2 | yes | no | 0.5 | Pre-requisite tests – single machine infinite bus (SMIB) flat run [PSCAD/EMTDC models] | DMATsl1
6 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 51 | 0 | 1 | 0.2 | no | no | 149 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
7 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 61 | 0 | 1 | 0.2 | no | no | 149 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
8 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 56 | 0 | 1 | 0.2 | no | no | 150 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
9 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 150 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
10 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 151 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
11 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 41 | 0 | 1 | 0.2 | no | no | 151 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
12 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 36 | 0 | 1 | 0.2 | no | no | 152 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
13 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 46 | 0 | 1 | 0.2 | no | no | 152 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
14 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 153 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsl1
15 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 153 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsl1
16 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 16 | 0 | 1 | 0.2 | no | no | 154 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
17 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 6 | 0 | 1 | 0.2 | no | no | 154 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
18 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 51 | 0 | 1 | 0.2 | no | no | 155 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
19 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 61 | 0 | 1 | 0.2 | no | no | 155 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
20 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 56 | 0 | 1 | 0.2 | no | no | 156 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
21 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 156 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
22 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 157 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
23 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 41 | 0 | 1 | 0.2 | no | no | 157 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
24 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 36 | 0 | 1 | 0.2 | no | no | 158 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
25 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 46 | 0 | 1 | 0.2 | no | no | 158 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
26 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 159 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsl1
27 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 1 | 0 | 1 | 0.2 | no | no | 159 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
28 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 16 | 0 | 1 | 0.2 | yes | yes | 160 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsl1
29 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 6 | 0 | 1 | 0.2 | no | no | 160 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
30 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 162 | 0 | 1 | 0.2 | no | no | 161 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
31 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 166 | 0 | 1 | 0.2 | no | no | 161 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
32 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 164 | 0 | 1 | 0.2 | no | no | 162 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
33 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 168 | 0 | 1 | 0.2 | no | no | 162 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
34 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 161 | 0 | 1 | 0.2 | no | no | 163 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
35 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 165 | 0 | 1 | 0.2 | no | no | 163 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
36 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 163 | 0 | 1 | 0.2 | no | no | 164 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
37 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 167 | 0 | 1 | 0.2 | no | no | 164 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
38 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 141 | 0 | 1 | 0.2 | yes | yes | 165 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsl1
39 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 131 | 0 | 1 | 0.2 | yes | yes | 165 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsl1
40 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 146 | 0 | 1 | 0.2 | no | no | 166 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
41 | Q_stp_profile | MAT_QREF_STEP_Fig4.1 | [6 empty] | 136 | 0 | 1 | 0.2 | no | no | 166 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
42 | P_stp_profile | MAT_P_STEP_Fig5 | [6 empty] | 51 | 0 | 1 | 0.2 | no | no | 167 | Active Power Controller Reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
43 | P_stp_profile | MAT_P_STEP_Fig5 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 168 | Active Power Controller Reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
44 | P_stp_profile | MAT_P_STEP_Fig5 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 169 | Active Power Controller Reference step change [PSS®E and PSCAD/EMTDC models] | DMATsl2
45 | P_stp_profile | MAT_P_STEP_Fig5 | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 169 | Active Power Controller Reference step change [PSS®E and PSCAD/EMTDC models] | DMATsl2
46 | F_profile | F_PROFILE_Fig6_1 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 170 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
47 | F_profile | F_PROFILE_Fig6_2 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 170 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
48 | F_profile | F_PROFILE_Fig6_3 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 170 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
49 | F_profile | F_PROFILE_Fig6_4 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 170 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
50 | F_profile | F_PROFILE_Fig6_1 | [6 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 171 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
51 | F_profile | F_PROFILE_Fig6_2 | [6 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 171 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
52 | F_profile | F_PROFILE_Fig6_3 | [6 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 171 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
53 | F_profile | F_PROFILE_Fig6_4 | [6 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 171 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
54 | F_profile | F_PROFILE_Fig6_1 | [6 empty] | 123 | 0 | 1 | 0.2 | yes | yes | 172 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
55 | F_profile | F_PROFILE_Fig6_2 | [6 empty] | 123 | 0 | 1 | 0.2 | yes | yes | 172 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
56 | F_profile | F_PROFILE_Fig6_3 | [6 empty] | 123 | 0 | 1 | 0.2 | yes | yes | 172 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
57 | F_profile | F_PROFILE_Fig6_4 | [6 empty] | 123 | 0 | 1 | 0.2 | yes | yes | 172 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
58 | F_profile | F_PROFILE_Fig6_1 | [6 empty] | 127 | 0 | 1 | 0.2 | yes | yes | 173 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
59 | F_profile | F_PROFILE_Fig6_2 | [6 empty] | 127 | 0 | 1 | 0.2 | yes | yes | 173 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
60 | F_profile | F_PROFILE_Fig6_3 | [6 empty] | 127 | 0 | 1 | 0.2 | yes | yes | 173 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
61 | F_profile | F_PROFILE_Fig6_4 | [6 empty] | 127 | 0 | 1 | 0.2 | yes | yes | 173 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
62 | F_profile | F_PROFILE_Fig7_1 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 174 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
63 | F_profile | F_PROFILE_Fig7_2 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 174 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
64 | F_profile | F_PROFILE_Fig7_1 | [6 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 175 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
65 | F_profile | F_PROFILE_Fig7_2 | [6 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 175 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
66 | F_profile | F_PROFILE_Fig7_1 | [6 empty] | 123 | 0 | 1 | 0.2 | yes | yes | 176 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
67 | F_profile | F_PROFILE_Fig7_2 | [6 empty] | 123 | 0 | 1 | 0.2 | yes | yes | 176 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
68 | F_profile | F_PROFILE_Fig7_1 | [6 empty] | 127 | 0 | 1 | 0.2 | yes | yes | 177 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
69 | F_profile | F_PROFILE_Fig7_2 | [6 empty] | 127 | 0 | 1 | 0.2 | yes | yes | 177 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2 | Need to initialise with High P, then reduce to low level before applying Frequency Disturbance
70 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 51 | 0 | 1 | 0.2 | no | no | 178 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
71 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 61 | 0 | 1 | 0.2 | no | no | 178 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
72 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 179 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
73 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 41 | 0 | 1 | 0.2 | no | no | 179 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
74 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 180 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
75 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 180 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
76 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 181 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
77 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 122 | 0 | 1 | 0.2 | yes | yes | 181 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
78 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 51 | 0 | 1 | 0.2 | no | no | 182 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
79 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 61 | 0 | 1 | 0.2 | no | no | 182 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
80 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 183 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
81 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 41 | 0 | 1 | 0.2 | no | no | 183 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
82 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 184 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
83 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 184 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
84 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 185 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
85 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 122 | 0 | 1 | 0.2 | yes | yes | 185 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
86 | V_profile | MAT_V_STEP_Fig10.1 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 51 | 0 | 1 | 0.2 | no | no | 186 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
87 | V_profile | MAT_V_STEP_Fig10.1 | [6 empty] | 61 | 0 | 1 | 0.2 | no | no | 186 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
88 | V_profile | MAT_V_STEP_Fig10.1 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 187 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
89 | V_profile | MAT_V_STEP_Fig10.1 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 41 | 0 | 1 | 0.2 | no | no | 187 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
90 | V_profile | MAT_V_STEP_Fig10.1 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 11 | 0 | 1 | 0.2 | yes | yes | 188 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
91 | V_profile | MAT_V_STEP_Fig10.1 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 1 | 0 | 1 | 0.2 | yes | yes | 188 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3dbg91
92 | V_profile | MAT_V_STEP_Fig10.1 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 121 | 0 | 1 | 0.2 | yes | yes | 189 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
93 | V_profile | MAT_V_STEP_Fig10.1 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 122 | 0 | 1 | 0.2 | yes | yes | 189 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
94 | V_profile | MAT_V_STEP_Fig10.2 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 51 | 0 | 1 | 0.2 | no | no | 186 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
95 | V_profile | MAT_V_STEP_Fig10.2 | [6 empty] | 61 | 0 | 1 | 0.2 | no | no | 186 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
96 | V_profile | MAT_V_STEP_Fig10.2 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 187 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
97 | V_profile | MAT_V_STEP_Fig10.2 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 41 | 0 | 1 | 0.2 | no | no | 187 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
98 | V_profile | MAT_V_STEP_Fig10.2 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 11 | 0 | 1 | 0.2 | yes | yes | 188 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3dbg98
99 | V_profile | MAT_V_STEP_Fig10.2 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 1 | 0 | 1 | 0.2 | yes | yes | 188 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
100 | V_profile | MAT_V_STEP_Fig10.2 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 121 | 0 | 1 | 0.2 | yes | yes | 189 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
101 | V_profile | MAT_V_STEP_Fig10.2 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 122 | 0 | 1 | 0.2 | yes | yes | 189 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
102 | V_profile | MAT_V_STEP_Fig10.3 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 51 | 0 | 1 | 0.2 | no | no | 186 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
103 | V_profile | MAT_V_STEP_Fig10.3 | [6 empty] | 61 | 0 | 1 | 0.2 | no | no | 186 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
104 | V_profile | MAT_V_STEP_Fig10.3 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 187 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
105 | V_profile | MAT_V_STEP_Fig10.3 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 41 | 0 | 1 | 0.2 | no | no | 187 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
106 | V_profile | MAT_V_STEP_Fig10.3 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 11 | 0 | 1 | 0.2 | yes | yes | 188 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
107 | V_profile | MAT_V_STEP_Fig10.3 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 1 | 0 | 1 | 0.2 | yes | yes | 188 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
108 | V_profile | MAT_V_STEP_Fig10.3 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 121 | 0 | 1 | 0.2 | yes | yes | 189 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3dbg108
109 | V_profile | MAT_V_STEP_Fig10.3 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 122 | 0 | 1 | 0.2 | yes | yes | 189 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
110 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 51 | 0 | 1 | 0.2 | no | no | 193 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
111 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 61 | 0 | 1 | 0.2 | no | no | 193 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
112 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 56 | 0 | 1 | 0.2 | no | no | 194 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
113 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 194 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
114 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 195 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
115 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 41 | 0 | 1 | 0.2 | no | no | 195 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
116 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 36 | 0 | 1 | 0.2 | no | no | 196 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
117 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 46 | 0 | 1 | 0.2 | no | no | 196 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
118 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 197 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl4
119 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 197 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl4
120 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 16 | 0 | 1 | 0.2 | no | no | 198 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
121 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 6 | 0 | 1 | 0.2 | no | no | 198 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
122 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 51 | 0 | 1 | 0.2 | no | no | 193 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
123 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 61 | 0 | 1 | 0.2 | no | no | 193 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
124 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 56 | 0 | 1 | 0.2 | no | no | 194 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
125 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 194 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
126 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 195 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
127 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 41 | 0 | 1 | 0.2 | no | no | 195 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
128 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 36 | 0 | 1 | 0.2 | no | no | 196 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
129 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 46 | 0 | 1 | 0.2 | no | no | 196 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
130 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 11 | 0 | 1 | 0.2 | no | no | 197 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
131 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 1 | 0 | 1 | 0.2 | no | no | 197 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
132 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 16 | 0 | 1 | 0.2 | no | no | 198 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
133 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 6 | 0 | 1 | 0.2 | no | no | 198 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
134 | P_stp_profile | MAT_P_STEP_Fig12 | [6 empty] | 106 | 0 | 1 | 0.2 | yes | yes | 199 | POC SCR = 1 Active Power reference change test [PSS®E and PSCAD/EMTDC models] | DMATsl4
135 | P_stp_profile | MAT_P_STEP_Fig12 | [6 empty] | 116 | 0 | 1 | 0.2 | yes | yes | 199 | POC SCR = 1 Active Power reference change test [PSS®E and PSCAD/EMTDC models] | DMATsl4
136 | Auxiliary_profile | AVAIL_P_-20% | [6 empty] | 11 | 0 | 1 | 0.2 | no | no | 226 | Input power source step change test | DMAT | Need to check profile again
137 | Auxiliary_profile | AVAIL_P_-20% | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 226 | Input power source step change test | DMATsl4
138 | Auxiliary_profile | AVAIL_P_+20% | [6 empty] | 11 | 0 | 1 | 0.2 | no | no | 227 | Input power source step change test | DMAT
139 | Auxiliary_profile | AVAIL_P_+20% | [6 empty] | 1 | 0 | 1 | 0.2 | no | no | 227 | Input power source step change test | DMAT
140 | Auxiliary_profile | AVAIL_P_+20% | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 228 | Input power source step change test | DMATsl4 | Need to check profile again
141 | Auxiliary_profile | AVAIL_P_+20% | [6 empty] | 1 | 0 | 1 | 0.2 | no | no | 228 | Input power source step change test | DMAT
142 | Auxiliary_profile | AVAIL_P_-20% | [6 empty] | 11 | 0 | 1 | 0.2 | no | no | 229 | Input power source step change test | DMAT
143 | Auxiliary_profile | AVAIL_P_-20% | [6 empty] | 1 | 0 | 1 | 0.2 | no | no | 229 | Input power source step change test | DMAT
144 | F_profile | S5253_UF | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5253long
145 | F_profile | S5253_OF | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5253long
146 | F_profile | S5253_UF | [6 empty] | 6 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253long
147 | F_profile | S5253_OF | [6 empty] | 6 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253long
148 | F_profile | S5253_UF | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5253long
149 | F_profile | S5253_OF | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5253long
150 | F_profile | S5253_UF | [6 empty] | 16 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253long
151 | F_profile | S5253_OF | [6 empty] | 16 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253long
152 | F_profile | S5253_UF | [6 empty] | 131 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S5253long
153 | F_profile | S5253_OF | [6 empty] | 131 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S5253long
154 | F_profile | S5253_UF | [6 empty] | 136 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253long
155 | F_profile | S5253_OF | [6 empty] | 136 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253long
156 | F_profile | S5253_UF | [6 empty] | 141 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S5253long
157 | F_profile | S5253_OF | [6 empty] | 141 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S5253long
158 | F_profile | S5253_UF | [6 empty] | 146 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253long
159 | F_profile | S5253_OF | [6 empty] | 146 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253long
160 | F_profile | S5253_UF | [6 empty] | 171 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S5253long
161 | F_profile | S5253_OF | [6 empty] | 171 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S5253long
162 | F_profile | S5253_UF | [6 empty] | 176 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253long
163 | F_profile | S5253_OF | [6 empty] | 176 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253long
164 | F_profile | S5253_UF | [6 empty] | 181 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S5253long
165 | F_profile | S5253_OF | [6 empty] | 181 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S5253long
166 | F_profile | S5253_UF | [6 empty] | 186 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253long
167 | F_profile | S5253_OF | [6 empty] | 186 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253long
168 | F_profile | S5253_+/-1Hz_4Hzs | [6 empty] | 1 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253
169 | F_profile | S5253_+/-1Hz_4Hzs | [6 empty] | 6 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253
170 | F_profile | S5253_+/-1Hz_4Hzs | [6 empty] | 11 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253
171 | F_profile | S5253_+/-1Hz_4Hzs | [6 empty] | 16 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253
172 | F_profile | S5253_+/-1Hz_4Hzs | [6 empty] | 131 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253
173 | F_profile | S5253_+/-1Hz_4Hzs | [6 empty] | 136 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253
174 | F_profile | S5253_+/-1Hz_4Hzs | [6 empty] | 141 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253
175 | F_profile | S5253_+/-1Hz_4Hzs | [6 empty] | 146 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253
176 | F_profile | S5253_+/-1Hz_4Hzs | [6 empty] | 171 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253
177 | F_profile | S5253_+/-1Hz_4Hzs | [6 empty] | 176 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253
178 | F_profile | S5253_+/-1Hz_4Hzs | [6 empty] | 181 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253
179 | F_profile | S5253_+/-1Hz_4Hzs | [6 empty] | 186 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253
180 | F_profile | S5253_UF_short | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5253
181 | F_profile | S5253_OF_short | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5253
182 | F_profile | S5253_UF_short | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5253
183 | F_profile | S5253_OF_short | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5253
184 | V_profile | S5254_LVRT | [6 empty] | 21 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5254
185 | V_profile | S5254_HVRT | [6 empty] | 21 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5254
186 | V_profile | S5254_LVRT_Qmax | [6 empty] | 24 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254
187 | V_profile | S5254_HVRT_Qmax | [6 empty] | 24 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254
188 | V_profile | S5254_LVRT_Qmin | [6 empty] | 25 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254
189 | V_profile | S5254_HVRT_Qmin | [6 empty] | 25 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254
190 | V_profile | S5254_LVRT | [6 empty] | 26 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5254
191 | V_profile | S5254_HVRT | [6 empty] | 26 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5254
192 | V_profile | S5254_LVRT_Qmax | [6 empty] | 29 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254
193 | V_profile | S5254_HVRT_Qmax | [6 empty] | 29 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254
194 | V_profile | S5254_LVRT_Qmin | [6 empty] | 30 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254
195 | V_profile | S5254_HVRT_Qmin | [6 empty] | 30 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254
196 | V_profile | S5254_LVRT | [6 empty] | 151 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254
197 | V_profile | S5254_HVRT | [6 empty] | 151 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254
198 | V_profile | S5254_LVRT_Qmax | [6 empty] | 154 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254
199 | V_profile | S5254_HVRT_Qmax | [6 empty] | 154 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254
200 | V_profile | S5254_LVRT_Qmin | [6 empty] | 155 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254
201 | V_profile | S5254_HVRT_Qmin | [6 empty] | 155 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254
202 | V_profile | S5254_LVRT | [6 empty] | 156 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254
203 | V_profile | S5254_HVRT | [6 empty] | 156 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254
204 | V_profile | S5254_LVRT_Qmax | [6 empty] | 159 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254
205 | V_profile | S5254_HVRT_Qmax | [6 empty] | 159 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254
206 | V_profile | S5254_LVRT_Qmin | [6 empty] | 160 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254
207 | V_profile | S5254_HVRT_Qmin | [6 empty] | 160 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5254
208 | V_profile | S5254_LVRT | [6 empty] | 191 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5254
209 | V_profile | S5254_HVRT | [6 empty] | 191 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5254
210 | V_profile | S5254_LVRT_Qmax | [6 empty] | 194 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5254
211 | V_profile | S5254_HVRT_Qmax | [6 empty] | 194 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5254
212 | V_profile | S5254_LVRT_Qmin | [6 empty] | 195 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5254
213 | V_profile | S5254_HVRT_Qmin | [6 empty] | 195 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5254
214 | V_profile | S5254_LVRT | [6 empty] | 196 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5254
215 | V_profile | S5254_HVRT | [6 empty] | 196 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5254
216 | V_profile | S5254_LVRT_Qmax | [6 empty] | 199 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5254
217 | V_profile | S5254_HVRT_Qmax | [6 empty] | 199 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5254
218 | V_profile | S5254_LVRT_Qmin | [6 empty] | 200 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5254
219 | V_profile | S5254_HVRT_Qmin | [6 empty] | 200 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5254
220 | V_profile | S5254_110_CUO | [6 empty] | 24 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254long
221 | V_profile | S5254_090_CUO | [6 empty] | 25 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254long
222 | V_profile | S5254_110_CUO | [6 empty] | 29 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254long
223 | V_profile | S5254_090_CUO | [6 empty] | 30 | 0 | 1 | 0.2 | no | no |  | V control mode | S5254long
224 | V_profile | S5254_110_CUO | [6 empty] | 154 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S5254long
225 | V_profile | S5254_090_CUO | [6 empty] | 155 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S5254long
226 | V_profile | S5254_110_CUO | [6 empty] | 159 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S5254long
227 | V_profile | S5254_090_CUO | [6 empty] | 160 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S5254long
228 | V_profile | S5254_110_CUO | [6 empty] | 194 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S5254long
229 | V_profile | S5254_090_CUO | [6 empty] | 195 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S5254long
230 | V_profile | S5254_110_CUO | [6 empty] | 199 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S5254long
231 | V_profile | S5254_090_CUO_short | [6 empty] | 200 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S5254long
232 | V_profile | S5254_110_CUO_short | [6 empty] | 154 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
233 | V_profile | S5254_090_CUO_short | [6 empty] | 155 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
234 | V_profile | S5254_110_CUO_short | [6 empty] | 159 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
235 | V_profile | S5254_090_CUO_short | [6 empty] | 160 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
236 | F_profile | S5257_OF_ShedLoad | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5257
237 | F_profile | S5257_OF_ShedLoad | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5257
238 | F_profile | S5257_OF_ShedLoad | [6 empty] | 131 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5257
239 | F_profile | S5257_OF_ShedLoad | [6 empty] | 141 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5257
240 | F_profile | S5257_OF_ShedLoad | [6 empty] | 171 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5257
241 | F_profile | S5257_OF_ShedLoad | [6 empty] | 181 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5257
242 | F_profile | S5258_OF_TRIP | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5258
243 | F_profile | S5258_UF_TRIP | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5258
244 | V_profile | S5258_OV_TRIP | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5258
245 | V_profile | S5258_UV_TRIP | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5258dbg
246 | F_profile | S5258_UF_46.8Hz | [6 empty] | 11 | 0 | 1 | 0.2 | no | no |  | V control mode | S5258
247 | F_profile | S5258_OV_130 | [6 empty] | 11 | 0 | 1 | 0.2 | no | no |  | V control mode | S5258
248 | F_profile | S5258_OV_123 | [6 empty] | 11 | 0 | 1 | 0.2 | no | no |  | V control mode | S5258
249 | F_profile | S5258_OV_120 | [6 empty] | 11 | 0 | 1 | 0.2 | no | no |  | V control mode | S5258
250 | F_profile | S5258_UV_85 | [6 empty] | 11 | 0 | 1 | 0.2 | no | no |  | V control mode | S5258
251 | F_profile | S5258_UV_79 | [6 empty] | 11 | 0 | 1 | 0.2 | no | no |  | V control mode | S5258
252 | V_profile | S5258_UV_50 | [6 empty] | 11 | 0 | 1 | 0.2 | no | no |  | V control mode | S5258
253 | V_profile | S5258_OF_FreqExtr | [6 empty] | 1 | 0 | 1 | 0.2 | no | no |  | V control mode | S5258
254 | V_profile | S5258_OF_52.2Hz | [6 empty] | 1 | 0 | 1 | 0.2 | no | no |  | V control mode | S5258
255 | V_profile | S5258_OF_52Hz | [6 empty] | 1 | 0 | 1 | 0.2 | no | no |  | V control mode | S5258
256 | V_profile | S5258_UF_47Hz | [6 empty] | 1 | 0 | 1 | 0.2 | no | no |  | V control mode | S5258
257 | V_profile | S5258_UF_46.8Hz | [6 empty] | 1 | 0 | 1 | 0.2 | no | no |  | V control mode | S5258
258 | V_profile | S5258_OV_130 | [6 empty] | 1 | 0 | 1 | 0.2 | no | no |  | V control mode | S5258
259 | V_profile | S5258_OV_123 | [6 empty] | 1 | 0 | 1 | 0.2 | no | no |  | V control mode | S5258
260 | V_profile | S5258_OV_120 | [6 empty] | 1 | 0 | 1 | 0.2 | no | no |  | V control mode | S5258
261 | V_profile | S5258_UV_85 | [6 empty] | 1 | 0 | 1 | 0.2 | no | no |  | V control mode | S5258
262 | V_profile | S5258_UV_79 | [6 empty] | 1 | 0 | 1 | 0.2 | no | no |  | V control mode | S5258
263 | V_profile | S5258_UV_50 | [6 empty] | 1 | 0 | 1 | 0.2 | no | no |  | V control mode | S5258
264 | F_profile | S52511_F_db | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52511
265 | F_profile | S52511_+/-1Hz | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52511
266 | F_profile | S52511_F_db | [6 empty] | 6 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52511
267 | F_profile | S52511_+/-1Hz | [6 empty] | 6 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52511
268 | F_profile | S52511_F_db | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52511
269 | F_profile | S52511_+/-1Hz | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52511
270 | F_profile | S52511_F_db | [6 empty] | 16 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52511
271 | F_profile | S52511_+/-1Hz | [6 empty] | 16 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52511
272 | F_profile | S52511_F_db | [6 empty] | 131 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52511
273 | F_profile | S52511_+/-1Hz | [6 empty] | 131 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52511
274 | F_profile | S52511_F_db | [6 empty] | 136 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52511
275 | F_profile | S52511_+/-1Hz | [6 empty] | 136 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52511
276 | F_profile | S52511_F_db | [6 empty] | 141 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52511
277 | F_profile | S52511_+/-1Hz | [6 empty] | 141 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52511
278 | F_profile | S52511_F_db | [6 empty] | 146 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52511
279 | F_profile | S52511_+/-1Hz | [6 empty] | 146 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52511
280 | F_profile | S52511_F_db | [6 empty] | 171 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52511
281 | F_profile | S52511_+/-1Hz | [6 empty] | 171 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52511
282 | F_profile | S52511_F_db | [6 empty] | 176 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52511
283 | F_profile | S52511_+/-1Hz | [6 empty] | 176 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52511
284 | F_profile | S52511_F_db | [6 empty] | 181 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52511
285 | F_profile | S52511_+/-1Hz | [6 empty] | 181 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52511
286 | F_profile | S52511_F_db | [6 empty] | 186 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52511
287 | F_profile | S52511_+/-1Hz | [6 empty] | 186 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52511
288 | V_stp_profile | S52513_V0+/-5% | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52513
289 | V_stp_profile | S52513_Vmax-2.5%/+5% | [6 empty] | 4 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52513
290 | V_stp_profile | S52513_Vmin+2.5%/-5% | [6 empty] | 5 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52513dbg
291 | V_stp_profile | S52513_V0+/-5% | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52513
292 | V_stp_profile | S52513_Vmax-2.5%/+5% | [6 empty] | 14 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52513
293 | V_stp_profile | S52513_Vmin+2.5%/-5% | [6 empty] | 15 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52513
294 | Q_stp_profile | S52513_Q0+/-15 | [6 empty] | 131 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
295 | Q_stp_profile | S52513_Qmax-10/+20 | [6 empty] | 134 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
296 | Q_stp_profile | S52513_Qmin+10/-20 | [6 empty] | 135 | 1 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
297 | Q_stp_profile | S52513_Q0+/-15 | [6 empty] | 141 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
298 | Q_stp_profile | S52513_Qmax-10/+20 | [6 empty] | 144 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
299 | Q_stp_profile | S52513_Qmin+10/-20 | [6 empty] | 145 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
300 | PF_stp_profile | S52513_PF0+/-0.02 | [6 empty] | 171 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
301 | PF_stp_profile | S52513_PFMax-0.01/+0.03 | [6 empty] | 174 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
302 | PF_stp_profile | S52513_PFMin+0.01/-0.03 | [6 empty] | 175 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
303 | PF_stp_profile | S52513_PF0+/-0.02 | [6 empty] | 181 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
304 | PF_stp_profile | S52513_PFMax-0.01/+0.03 | [6 empty] | 184 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
305 | PF_stp_profile | S52513_PFMin+0.01/-0.03 | [6 empty] | 185 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
306 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52513
307 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 4 | 0 | 1 | 0.2 | no | no |  | V control mode | S52513
308 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 5 | 0 | 1 | 0.2 | no | no |  | V control mode | S52513
309 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52513
310 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 14 | 0 | 1 | 0.2 | no | no |  | V control mode | S52513
311 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 15 | 0 | 1 | 0.2 | no | no |  | V control mode | S52513
312 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 131 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
313 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 134 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52513
314 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 135 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52513
315 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 141 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
316 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 144 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52513
317 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 145 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52513
318 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 171 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
319 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 174 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52513
320 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 175 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52513
321 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 181 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
322 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 184 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52513
323 | V_profile | S52513_V_STEP_+/-5% | [6 empty] | 185 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52513
324 | P_stp_profile | S52514_-/+50% | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52514
325 | P_stp_profile | S52514_-/+50% | [6 empty] | 4 | 0 | 1 | 0.2 | no | no |  | V control mode | S52514
326 | P_stp_profile | S52514_-/+50% | [6 empty] | 5 | 0 | 1 | 0.2 | no | no |  | V control mode | S52514
327 | P_stp_profile | S52514_-/+50% | [6 empty] | 131 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S52514
328 | P_stp_profile | S52514_-/+50% | [6 empty] | 134 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52514
329 | P_stp_profile | S52514_-/+50% | [6 empty] | 135 | 0 | 1 | 0.2 | no | no |  | Q control mode | S52514
330 | P_stp_profile | S52514_-/+50% | [6 empty] | 171 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S52514
331 | P_stp_profile | S52514_-/+50% | [6 empty] | 174 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52514
332 | P_stp_profile | S52514_-/+50% | [6 empty] | 175 | 0 | 1 | 0.2 | no | no |  | PF control mode | S52514
333 | V_profile | LowSCR_V0-/+5% | [6 empty] | 311 | 0 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | S52515
334 | V_profile | LowSCR_V0-5% | [6 empty] | 311 | 0 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | S52515
335 | V_profile | LowSCR_V0-10% | [6 empty] | 311 | 0 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | S52515
336 | ANG_profile | MAT_ANG_STEP+/-20deg | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52516
337 | ANG_profile | MAT_ANG_STEP+/-20deg | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S52516
338 | V_stp_profile | S52513_V0+/-5% | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
339 | V_stp_profile | S52513_V0+/-5% | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
340 | Q_stp_profile | S52513_Q0+/-15 | [6 empty] | 131 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | Benchmarking
341 | Q_stp_profile | S52513_Q0+/-15 | [6 empty] | 141 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | Benchmarking
342 | PF_stp_profile | S52513_PF0+/-0.02 | [6 empty] | 171 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | Benchmarking
343 | PF_stp_profile | S52513_PF0+/-0.02 | [6 empty] | 181 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | Benchmarking
344 | V_profile | V_STEP_+/-5% | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
345 | V_profile | V_STEP_+/-5% | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
346 | P_stp_profile | S52514_-/+50% | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
347 | P_stp_profile | S52514_-/+50% | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
348 | F_profile | S52511_+/-1Hz | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
349 | F_profile | S52511_+/-1Hz | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
350 | ANG_profile | MAT_ANG_STEP | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
351 | ANG_profile | MAT_ANG_STEP | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
352 | Auxiliary_profile | AVAIL_P_-20% | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
353 | Auxiliary_profile | AVAIL_P_-20% | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
354 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 211 | 0 | 1 | 0.2 | yes | yes | 153 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsldbgBESSonly
355 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 201 | 0 | 1 | 0.2 | yes | yes | 153 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsldbgBESSonly
356 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 211 | 0 | 1 | 0.2 | yes | yes | 159 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsldbgBESSonly
357 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 201 | 0 | 1 | 0.2 | yes | yes | 160 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsldbgBESSonly
358 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 241 | 0 | 1 | 0.2 | yes | yes | 165 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsldbgBESSonly
359 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 231 | 0 | 1 | 0.2 | yes | yes | 165 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsldbgBESSonly
360 | P_stp_profile | MAT_P_STEP_Fig5 | [6 empty] | 211 | 0 | 1 | 0.2 | yes | yes | 169 | Active Power Controller Reference step change [PSS®E and PSCAD/EMTDC models] | DMATsldbgBESSonly
361 | P_stp_profile | MAT_P_STEP_Fig5 | [6 empty] | 201 | 0 | 1 | 0.2 | yes | yes | 169 | Active Power Controller Reference step change [PSS®E and PSCAD/EMTDC models] | DMATsldbgBESSonly
362 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 211 | 0 | 1 | 0.2 | yes | yes | 197 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMATsldbgBESSonly
363 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 201 | 0 | 1 | 0.2 | yes | yes | 197 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMATsldbgBESSonly
364 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 311 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCR
365 | V_stp_profile | LowSCR_V0-5% | [6 empty] | 311 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCR
366 | V_stp_profile | LowSCR_V0-10% | [6 empty] | 311 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCR
367 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 325 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
368 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 326 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
369 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 327 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
370 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 328 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
371 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 329 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
372 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 330 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
373 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 331 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
374 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 332 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
375 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 333 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
376 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 334 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
377 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 335 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
378 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 336 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
379 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 337 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
380 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 324 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
Note on A3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: review
Note on A48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: to be revisited - available P vs. setpoint --> how to adjust in model?
Note on J56: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: here the available energy from solar needs to be limited --> not sure if model can do it. And if so, how.
Note on J78: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not fully correct, MAT asks for P=0.5, which is not available in the setpoints at the moment
Note on J86: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not fully correct, MAT asks for P=0.5, which is not available in the setpoints at the moment
Note on J94: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not fully correct, MAT asks for P=0.5, which is not available in the setpoints at the moment
Note on J102: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not fully correct, MAT asks for P=0.5, which is not available in the setpoints at the moment
Note on J110: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not fully correct, MAT asks for P=0.5, which is not available in the setpoints at the moment
Note on N222: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Exclude V control mode

## ORT
PSSE-specific settings
CaseNr | Test Type | time | Disturbance Frequency | Disturbance Magnitude | Vbase | PhaseOsc Magnitude | ActivePower | ReactivePower | Grid SCR | Grid X_R | setpoint ID | TimeStep | AccFactor | run in PSCAD? | run in PSS/E? | Comment/Corresponding DMAT case | test group | simulation batch
1 | ORT | 5 | 0.1 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
2 | ORT | 5 | 0.2 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
3 | ORT | 5 | 0.3 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
4 | ORT | 5 | 0.4 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
5 | ORT | 5 | 0.5 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
6 | ORT | 5 | 0.6 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
7 | ORT | 5 | 0.7 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
8 | ORT | 5 | 0.8 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
9 | ORT | 5 | 0.9 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
10 | ORT | 5 | 1 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
11 | ORT | 5 | 2 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
12 | ORT | 5 | 3 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
13 | ORT | 5 | 4 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
14 | ORT | 5 | 5 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
15 | ORT | 5 | 6 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
16 | ORT | 5 | 7 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
17 | ORT | 5 | 8 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
18 | ORT | 5 | 9 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
19 | ORT | 5 | 10 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
20 | ORT | 5 | 11 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
21 | ORT | 5 | 12 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
22 | ORT | 5 | 13 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
23 | ORT | 5 | 14 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
24 | ORT | 5 | 15 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
25 | ORT | 5 | 16 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
26 | ORT | 5 | 17 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
27 | ORT | 5 | 18 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
28 | ORT | 5 | 19 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
29 | ORT | 5 | 20 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
30 | ORT | 5 | 21 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
31 | ORT | 5 | 22 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
32 | ORT | 5 | 23 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
33 | ORT | 5 | 24 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
34 | ORT | 5 | 25 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
35 | ORT | 5 | 26 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
36 | ORT | 5 | 27 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
37 | ORT | 5 | 28 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
38 | ORT | 5 | 29 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
39 | ORT | 5 | 30 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
40 | ORT | 5 | 31 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
41 | ORT | 5 | 32 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
42 | ORT | 5 | 33 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
43 | ORT | 5 | 34 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
44 | ORT | 5 | 35 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
45 | ORT | 5 | 36 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
46 | ORT | 5 | 37 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
47 | ORT | 5 | 38 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
48 | ORT | 5 | 39 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
49 | ORT | 5 | 40 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
50 | ORT | 5 | 41 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
51 | ORT | 5 | 42 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
52 | ORT | 5 | 43 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
53 | ORT | 5 | 44 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
54 | ORT | 5 | 45 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
55 | ORT | 5 | 0.1 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
56 | ORT | 5 | 0.2 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
57 | ORT | 5 | 0.3 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
58 | ORT | 5 | 0.4 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
59 | ORT | 5 | 0.5 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
60 | ORT | 5 | 0.6 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
61 | ORT | 5 | 0.7 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
62 | ORT | 5 | 0.8 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
63 | ORT | 5 | 0.9 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
64 | ORT | 5 | 1 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
65 | ORT | 5 | 2 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
66 | ORT | 5 | 3 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
67 | ORT | 5 | 4 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
68 | ORT | 5 | 5 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
69 | ORT | 5 | 6 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
70 | ORT | 5 | 7 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
71 | ORT | 5 | 8 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
72 | ORT | 5 | 9 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
73 | ORT | 5 | 10 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
74 | ORT | 5 | 11 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
75 | ORT | 5 | 12 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
76 | ORT | 5 | 13 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
77 | ORT | 5 | 14 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
78 | ORT | 5 | 15 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
79 | ORT | 5 | 16 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
80 | ORT | 5 | 17 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
81 | ORT | 5 | 18 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
82 | ORT | 5 | 19 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
83 | ORT | 5 | 20 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
84 | ORT | 5 | 21 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
85 | ORT | 5 | 22 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
86 | ORT | 5 | 23 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
87 | ORT | 5 | 24 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
88 | ORT | 5 | 25 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
89 | ORT | 5 | 26 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
90 | ORT | 5 | 27 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
91 | ORT | 5 | 28 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
92 | ORT | 5 | 29 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
93 | ORT | 5 | 30 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
94 | ORT | 5 | 31 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
95 | ORT | 5 | 32 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
96 | ORT | 5 | 33 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
97 | ORT | 5 | 34 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
98 | ORT | 5 | 35 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
99 | ORT | 5 | 36 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
100 | ORT | 5 | 37 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
101 | ORT | 5 | 38 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
102 | ORT | 5 | 39 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
103 | ORT | 5 | 40 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
104 | ORT | 5 | 41 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
105 | ORT | 5 | 42 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
106 | ORT | 5 | 43 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
107 | ORT | 5 | 44 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
108 | ORT | 5 | 45 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
Note on F2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: if not specified, just modulate in proportion to Vth voltage dictated by setpoint

## TOV
Overvoltage tests. Overvoltage condition is created by connecting a suitably-sized capacitor at the Connection point. The calculation is designed to take into account the power flows at POC
PSSE-specific settings
CaseNr | Test Type | time | Fduration | Capacity(F) | Vresidual | SCL_post | X_R_post | setpoint ID | TimeStep | AccFactor | run in PSCAD? | run in PSS/E? | Comment/Corresponding DMAT case | test group | simulation batch
1 | TOV | 5 | 0.9 |  | 1.15 |  |  | 51 | 1 | 0.2 | no | no | 131 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
2 | TOV | 5 | 0.9 |  | 1.15 |  |  | 53 | 1 | 0.2 | no | no | 132 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
3 | TOV | 5 | 0.9 |  | 1.15 |  |  | 52 | 1 | 0.2 | no | no | 133 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
4 | TOV | 5 | 0.9 |  | 1.15 |  |  | 31 | 1 | 0.2 | no | no | 134 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
5 | TOV | 5 | 0.9 |  | 1.15 |  |  | 43 | 1 | 0.2 | no | no | 135 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
6 | TOV | 5 | 0.9 |  | 1.15 |  |  | 42 | 1 | 0.2 | no | no | 136 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
7 | TOV | 5 | 0.9 |  | 1.15 |  |  | 11 | 1 | 0.2 | yes | yes | 137 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMATsl
8 | TOV | 5 | 0.9 |  | 1.15 |  |  | 13 | 1 | 0.2 | no | no | 138 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
9 | TOV | 5 | 0.9 |  | 1.15 |  |  | 12 | 1 | 0.2 | no | no | 139 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
10 | TOV | 5 | 0.9 |  | 1.15 |  |  | 1 | 1 | 0.2 | yes | yes | 137 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMATsl
11 | TOV | 5 | 0.9 |  | 1.15 |  |  | 3 | 1 | 0.2 | no | no | 138 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
12 | TOV | 5 | 0.9 |  | 1.15 |  |  | 2 | 1 | 0.2 | no | no | 139 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
13 | TOV | 5 | 0.1 |  | 1.2 |  |  | 51 | 1 | 0.2 | no | no | 140 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
14 | TOV | 5 | 0.1 |  | 1.2 |  |  | 53 | 1 | 0.2 | no | no | 141 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
15 | TOV | 5 | 0.1 |  | 1.2 |  |  | 52 | 1 | 0.2 | no | no | 142 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
16 | TOV | 5 | 0.1 |  | 1.2 |  |  | 31 | 1 | 0.2 | no | no | 143 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
17 | TOV | 5 | 0.1 |  | 1.2 |  |  | 43 | 1 | 0.2 | no | no | 144 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
18 | TOV | 5 | 0.1 |  | 1.2 |  |  | 42 | 1 | 0.2 | no | no | 145 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
19 | TOV | 5 | 0.1 |  | 1.2 |  |  | 11 | 1 | 0.2 | yes | yes | 146 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMATsl
20 | TOV | 5 | 0.1 |  | 1.2 |  |  | 13 | 1 | 0.2 | no | no | 147 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
21 | TOV | 5 | 0.1 |  | 1.2 |  |  | 12 | 1 | 0.2 | no | no | 148 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
22 | TOV | 5 | 0.1 |  | 1.2 |  |  | 1 | 1 | 0.2 | yes | yes | 146 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMATsl
23 | TOV | 5 | 0.1 |  | 1.2 |  |  | 3 | 1 | 0.2 | no | no | 147 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
24 | TOV | 5 | 0.1 |  | 1.2 |  |  | 2 | 1 | 0.2 | no | no | 148 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
25 | TOV | 5 | 20 |  | 1.2 |  |  | 1 | 1 | 0.2 | no | no | 137 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | Benchmarking-5.3.9
26 | TOV | 5 | 2 |  | 1.25 |  |  | 1 | 1 | 0.2 | no | no | 136 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | Benchmarking-5.3.9
27 | TOV | 5 | 0.34 |  | 1.1 |  |  | 11 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255dbg
28 | TOV | 5 | 0.34 |  | 1.2 |  |  | 11 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255dbg
29 | TOV | 5 | 0.34 |  | 1.3 |  |  | 11 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255dbg
30 | TOV | 5 | 0.34 |  | 1.4 |  |  | 11 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255dbg
31 | TOV | 5 | 0.34 |  | 1.5 |  |  | 11 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255dbg
32 | TOV | 5 | 0.34 |  | 1.6 |  |  | 11 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255dbg
33 | TOV | 5 | 0.34 |  | 1.7 |  |  | 11 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255dbg
34 | TOV | 5 | 0.34 |  | 1.8 |  |  | 11 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255dbg
35 | TOV | 5 | 0.34 |  | 1.9 |  |  | 11 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255dbg
36 | TOV | 5 | 0.34 |  | 2 |  |  | 11 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255dbg
37 | TOV | 5 | 5 |  | 1.1 |  |  | 301 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
38 | TOV | 5 | 5 |  | 1.15 |  |  | 301 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
39 | TOV | 5 | 5 |  | 1.2 |  |  | 301 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
40 | TOV | 5 | 5 |  | 1.25 |  |  | 301 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
41 | TOV | 5 | 5 |  | 1.3 |  |  | 301 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
42 | TOV | 5 | 5 |  | 1.35 |  |  | 301 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
43 | TOV | 5 | 5 |  | 1.4 |  |  | 301 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
44 | TOV | 5 | 5 |  | 1.45 |  |  | 301 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
45 | TOV | 5 | 5 |  | 1.5 |  |  | 301 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
46 | TOV | 5 | 5 |  | 1.55 |  |  | 301 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
47 | TOV | 5 | 5 |  | 1.6 |  |  | 301 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
48 | TOV | 5 | 5 |  | 1.65 |  |  | 301 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
49 | TOV | 5 | 5 |  | 1.7 |  |  | 301 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
50 | TOV | 5 | 5 |  | 1.75 |  |  | 301 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
51 | TOV | 5 | 5 |  | 1.8 |  |  | 301 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
52 | TOV | 5 | 5 |  | 1.85 |  |  | 301 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
53 | TOV | 5 | 5 |  | 1.9 |  |  | 301 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
54 | TOV | 5 | 5 |  | 1.95 |  |  | 301 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
55 | TOV | 5 | 5 |  | 2 |  |  | 301 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
56 | TOV | 5 | 5 |  | 1.1 |  |  | 304 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
57 | TOV | 5 | 5 |  | 1.15 |  |  | 304 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
58 | TOV | 5 | 5 |  | 1.2 |  |  | 304 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
59 | TOV | 5 | 5 |  | 1.25 |  |  | 304 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
60 | TOV | 5 | 5 |  | 1.3 |  |  | 304 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
61 | TOV | 5 | 5 |  | 1.35 |  |  | 304 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
62 | TOV | 5 | 5 |  | 1.4 |  |  | 304 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
63 | TOV | 5 | 5 |  | 1.45 |  |  | 304 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
64 | TOV | 5 | 5 |  | 1.5 |  |  | 304 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
65 | TOV | 5 | 5 |  | 1.55 |  |  | 304 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
66 | TOV | 5 | 5 |  | 1.6 |  |  | 304 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
67 | TOV | 5 | 5 |  | 1.65 |  |  | 304 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
68 | TOV | 5 | 5 |  | 1.7 |  |  | 304 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
69 | TOV | 5 | 5 |  | 1.75 |  |  | 304 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
70 | TOV | 5 | 5 |  | 1.8 |  |  | 304 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
71 | TOV | 5 | 5 |  | 1.85 |  |  | 304 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
72 | TOV | 5 | 5 |  | 1.9 |  |  | 304 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
73 | TOV | 5 | 5 |  | 1.95 |  |  | 304 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
74 | TOV | 5 | 5 |  | 2 |  |  | 304 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
75 | TOV | 5 | 5 |  | 1.1 |  |  | 305 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
76 | TOV | 5 | 5 |  | 1.15 |  |  | 305 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
77 | TOV | 5 | 5 |  | 1.2 |  |  | 305 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
78 | TOV | 5 | 5 |  | 1.25 |  |  | 305 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
79 | TOV | 5 | 5 |  | 1.3 |  |  | 305 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
80 | TOV | 5 | 5 |  | 1.35 |  |  | 305 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
81 | TOV | 5 | 5 |  | 1.4 |  |  | 305 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
82 | TOV | 5 | 5 |  | 1.45 |  |  | 305 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
83 | TOV | 5 | 5 |  | 1.5 |  |  | 305 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
84 | TOV | 5 | 5 |  | 1.55 |  |  | 305 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
85 | TOV | 5 | 5 |  | 1.6 |  |  | 305 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
86 | TOV | 5 | 5 |  | 1.65 |  |  | 305 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
87 | TOV | 5 | 5 |  | 1.7 |  |  | 305 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
88 | TOV | 5 | 5 |  | 1.75 |  |  | 305 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
89 | TOV | 5 | 5 |  | 1.8 |  |  | 305 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
90 | TOV | 5 | 5 |  | 1.85 |  |  | 305 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
91 | TOV | 5 | 5 |  | 1.9 |  |  | 305 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
92 | TOV | 5 | 5 |  | 1.95 |  |  | 305 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
93 | TOV | 5 | 5 |  | 2 |  |  | 305 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
Note on A7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MAT

## Setpoints
Description: This sheet is used to initialise the model at different setpoints. The "name" of the PSCAD setting to be adjusted is for readability only and is not used. The module that contains the component is separated by a colon in case is is a submodule of "Main" The value of each parameter needs to be defined for each of the setpoint IDs | [5 empty] | Setpoints | [119 empty] | various Pavail, Pini, max-min SCR/X_R | [9 empty] | Different DYR - Q setpoint | [29 empty] | various Pavail, Pini, max-min SCR/X_R | [9 empty] | Different DYR - PF setpoint | [29 empty] | Setpoints BESS Only - Vctrl | [29 empty] | Setpoints BESS Only - Qctrl | [29 empty] | Setpoints BESS Only - PFctrl | [29 empty] | Setpoints Iq Injection | [19 empty] | Low SCR demonstration |  |  | Finding Min SCR value - with BESS | [10 empty] | Finding Min BESS with SCR = 1.2
[5 empty] | ParameterName | AemoMinSCR - Pmax |  |  |  |  | AemoMinSCR - Pmin |  |  |  |  | AemoMaxSCR - Pmax |  |  |  |  | AemoMaxSCR - Pmin |  |  |  |  | INF SCR - Pmax |  |  |  |  | INF SCR - Pmin |  |  |  |  | SCR=3, X/R=14 | [9 empty] | SCR=3, X/R=3 | [9 empty] | SCR=10, X/R=14 | [9 empty] | SCR=10, X/R=3 | [9 empty] | SCR=3, X/R=6 | [9 empty] | SCR=5, X/R=6 | [9 empty] | SCR=10, X/R=6 | [9 empty] | SCR=1, X/R=14 | [9 empty] | SCR=1, X/R=3 | [9 empty] | Pavai=1, Pini=0.5 |  | P0.5 - 0.5 |  | P0.5 - 0.05 |  | P0.05 -0.05 |  | 3-14 | 3-3 | AemoMinSCR - Pmax |  |  |  |  | AemoMinSCR - Pmin |  |  |  |  | AemoMaxSCR - Pmax |  |  |  |  | AemoMaxSCR - Pmin |  |  |  |  | INF SCR - Pmax |  |  |  |  | INF SCR - Pmin |  |  |  |  | X/R = 14 |  |  |  | X/R = 3 |  |  |  | Place holder |  | AemoMinSCR - Pmax |  |  |  |  | AemoMinSCR - Pmin |  |  |  |  | AemoMaxSCR - Pmax |  |  |  |  | AemoMaxSCR - Pmin |  |  |  |  | INF SCR - Pmax |  |  |  |  | INF SCR - Pmin |  |  |  |  | AemoMinSCR - Pmax |  |  |  |  | AemoMinSCR - Pmin |  |  |  |  | AemoMaxSCR - Pmax |  |  |  |  | AemoMaxSCR - Pmin |  |  |  |  | INF SCR - Pmax |  |  |  |  | INF SCR - Pmin |  |  |  |  | AemoMinSCR - Pmax |  |  |  |  | AemoMinSCR - Pmin |  |  |  |  | AemoMaxSCR - Pmax |  |  |  |  | AemoMaxSCR - Pmin |  |  |  |  | INF SCR - Pmax |  |  |  |  | INF SCR - Pmin |  |  |  |  | AemoMinSCR - Pmax |  |  |  |  | AemoMinSCR - Pmin |  |  |  |  | AemoMaxSCR - Pmax |  |  |  |  | AemoMaxSCR - Pmin |  |  |  |  | INF SCR - Pmax |  |  |  |  | INF SCR - Pmin |  |  |  |  | AemoMinSCR - Pmax |  |  |  |  | AemoMinSCR - Pmin |  |  |  |  | AemoMaxSCR - Pmax |  |  |  |  | AemoMaxSCR - Pmin |  |  |  |  | SCR=1.2, X/R=3 | SCR=10, X/R=3 | SCR=10, X/R=3 | SCR=2.0, X/R=3 | SCR=1.9, X/R=3 | SCR=1.8, X/R=3 | SCR=1.7, X/R=3 | SCR=1.6, X/R=3 | SCR=1.5, X/R=3 | SCR=1.4, X/R=3 | SCR=1.3, X/R=3 | SCR=1.2, X/R=3 | SCR=1.1, X/R=3 | SCR=1.0, X/R=3 | SCR=1.2, X/R=3 | SCR=1.2, X/R=3 | SCR=1.2, X/R=3 | SCR=1.2, X/R=3 | SCR=1.2, X/R=3 | SCR=1.2, X/R=3 | SCR=1.2, X/R=3 | SCR=1.2, X/R=3 | SCR=1.2, X/R=3 | SCR=1.2, X/R=3 | SCR=1.2, X/R=3 | SCR=1.2, X/R=3 | SCR=1.2, X/R=3
GENERAL |  |  |  |  | Setpoint ID | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212 | 213 | 214 | 215 | 216 | 217 | 218 | 219 | 220 | 221 | 222 | 223 | 224 | 225 | 226 | 227 | 228 | 229 | 230 | 231 | 232 | 233 | 234 | 235 | 236 | 237 | 238 | 239 | 240 | 241 | 242 | 243 | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273 | 274 | 275 | 276 | 277 | 278 | 279 | 280 | 281 | 282 | 283 | 284 | 285 | 286 | 287 | 288 | 289 | 290 | 291 | 292 | 293 | 294 | 295 | 296 | 297 | 298 | 299 | 300 | 301 | 302 | 303 | 304 | 305 | 306 | 307 | 308 | 309 | 310 | 311 | 312 | 313 | 314 | 315 | 316 | 317 | 318 | 319 | 320 | 321 | 322 | 323 | 324 | 325 | 326 | 327 | 328 | 329 | 330 | 331 | 332 | 333 | 334 | 335 | 336 | 337
[5 empty] | GridMVA | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 251.5 | 839.1 | 251.5 | 839.1 | 251.5 | 839.1 | 251.5 | 839.1 | 270 | 270 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 270 | 900 | 270 | 900 | 270 | 900 | 270 | 900 | 899910 | 899910 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 108 | 900 | 108 | 180 | 171 | 162 | 153 | 144 | 135 | 126 | 117 | 108 | 99 | 90 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
system normal voltage | 1.02 |  |  |  | SCR | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2.7944 | 9.3233 | 2.7944 | 9.3233 | 2.7944 | 9.3233 | 2.7944 | 9.3233 | 3 | 3 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 3 | 10 | 3 | 10 | 3 | 10 | 3 | 10 | 9999 | 9999 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 2.7944 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 9.3233 | 1.2 | 10 | 10 | 2 | 1.9 | 1.8 | 1.7 | 1.6 | 1.5 | 1.4 | 1.3 | 1.2 | 1.1 | 1 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
droop | 0.05 |  |  |  | X_R | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3 | 3.77 | 3 | 3.77 | 3 | 3.77 | 14 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 14 | 14 | 14 | 14 | 3 | 3 | 3 | 3 | 3 | 14 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
droop base | 35.55 |  |  |  | Pini | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.5 | 0.5 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 0.05 | 0.05 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[5 empty] | P1ini | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.25 | 0.25 | 0.25 | 0.25 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
[5 empty] | Qini | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Q1ini | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Pavai | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[5 empty] | V_POC | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02
[5 empty] | P | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 45 | 45 | 45 | 45 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 4.5 | 4.5 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
[5 empty] | Q | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 27 | -27 | 35.55 | -35.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PSSE-specific |  |  |  |  | P_PV1 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.2503 | 2.2503 | 2.2503 | 2.2503 | 2.2503 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 22.5003 | 22.5003 | 22.5003 | 22.5003 | 2.2503 | 2.2503 | 2.2503 | 2.2503 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.2503 | 2.2503 | 2.2503 | 2.2503 | 2.2503 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 2.365 | 2.365 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115
[5 empty] | Q_PV1 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -4.5835 | -4.5835 | -4.5835 | -4.5835 | -5.7385 | -5.7385 | -5.7385 | -5.7385 | -4.5835 | -4.5835 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -4.5835 | -4.5835 | -4.5835 | -4.5835 | -5.7385 | -5.7385 | -5.7385 | -5.7385 | -4.5835 | -4.5835 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
Pmax | Q0 | Q0.3 | Q-0.3 | Qmax | LOC_PV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1
Ploss 33kV - POC (pu) | 0.0025556 | 0.002556 | 0.002556 | 0.002556 | BUS_PV1 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942 | 9942
Qloss 33kV - POC (pu) | -0.022222 | -0.0088777 | -0.016667 | 0.0088777 | P_PV2 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.2503 | 2.2503 | 2.2503 | 2.2503 | 2.2503 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 22.5003 | 22.5003 | 22.5003 | 22.5003 | 2.2503 | 2.2503 | 2.2503 | 2.2503 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.2503 | 2.2503 | 2.2503 | 2.2503 | 2.2503 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 2.365 | 2.365 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 2.365 | 2.365 | 2.365 | 2.365 | 2.365 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115 | 45.115
[5 empty] | Q_PV2 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -4.5835 | -4.5835 | -4.5835 | -4.5835 | -5.7385 | -5.7385 | -5.7385 | -5.7385 | -4.5835 | -4.5835 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -4.5835 | -4.5835 | -4.5835 | -4.5835 | -5.7385 | -5.7385 | -5.7385 | -5.7385 | -4.5835 | -4.5835 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | 13.1005 | -14.25 | 18.1745 | -18.525 | -5.7385 | 8.5115 | -18.4885 | 12.7865 | -22.7635 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
Pmin = 0.05 | Q0 | Q0.3 | Q-0.3 |  | LOC_PV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2
Ploss 33kV - POC (pu) | 6.3896e-06 | 6.3896e-06 | 6.3896e-06 |  | BUS_PV2 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944 | 9944
Qloss 33kV - POC (pu) | -0.12752 | -0.11086 | -0.11086 |  | offline_machines | AemoMinSCR - Pmax 201: [9942]; AemoMinSCR - Pmax 202: [9942]; AemoMinSCR - Pmax 203: [9942]; AemoMinSCR - Pmax 204: [9942]; AemoMinSCR - Pmax 205: [9942]; AemoMinSCR - Pmin 206: [9942]; AemoMinSCR - Pmin 207: [9942]; AemoMinSCR - Pmin 208: [9942]; AemoMinSCR - Pmin 209: [9942]; AemoMinSCR - Pmin 210: [9942]; AemoMaxSCR - Pmax 211: [9942]; AemoMaxSCR - Pmax 212: [9942]; AemoMaxSCR - Pmax 213: [9942]; AemoMaxSCR - Pmax 214: [9942]; AemoMaxSCR - Pmax 215: [9942]; AemoMaxSCR - Pmin 216: [9942]; AemoMaxSCR - Pmin 217: [9942]; AemoMaxSCR - Pmin 218: [9942]; AemoMaxSCR - Pmin 219: [9942]; AemoMaxSCR - Pmin 220: [9942]; INF SCR - Pmax 221: [9942]; INF SCR - Pmax 222: [9942]; INF SCR - Pmax 223: [9942]; INF SCR - Pmax 224: [9942]; INF SCR - Pmax 225: [9942]; INF SCR - Pmin 226: [9942]; INF SCR - Pmin 227: [9942]; INF SCR - Pmin 228: [9942]; INF SCR - Pmin 229: [9942]; INF SCR - Pmin 230: [9942]; AemoMinSCR - Pmax 231: [9942]; AemoMinSCR - Pmax 232: [9942]; AemoMinSCR - Pmax 233: [9942]; AemoMinSCR - Pmax 234: [9942]; AemoMinSCR - Pmax 235: [9942]; AemoMinSCR - Pmin 236: [9942]; AemoMinSCR - Pmin 237: [9942]; AemoMinSCR - Pmin 238: [9942]; AemoMinSCR - Pmin 239: [9942]; AemoMinSCR - Pmin 240: [9942]; AemoMaxSCR - Pmax 241: [9942]; AemoMaxSCR - Pmax 242: [9942]; AemoMaxSCR - Pmax 243: [9942]; AemoMaxSCR - Pmax 244: [9942]; AemoMaxSCR - Pmax 245: [9942]; AemoMaxSCR - Pmin 246: [9942]; AemoMaxSCR - Pmin 247: [9942]; AemoMaxSCR - Pmin 248: [9942]; AemoMaxSCR - Pmin 249: [9942]; AemoMaxSCR - Pmin 250: [9942]; INF SCR - Pmax 251: [9942]; INF SCR - Pmax 252: [9942]; INF SCR - Pmax 253: [9942]; INF SCR - Pmax 254: [9942]; INF SCR - Pmax 255: [9942]; INF SCR - Pmin 256: [9942]; INF SCR - Pmin 257: [9942]; INF SCR - Pmin 258: [9942]; INF SCR - Pmin 259: [9942]; INF SCR - Pmin 260: [9942]; AemoMinSCR - Pmax 261: [9942]; AemoMinSCR - Pmax 262: [9942]; AemoMinSCR - Pmax 263: [9942]; AemoMinSCR - Pmax 264: [9942]; AemoMinSCR - Pmax 265: [9942]; AemoMinSCR - Pmin 266: [9942]; AemoMinSCR - Pmin 267: [9942]; AemoMinSCR - Pmin 268: [9942]; AemoMinSCR - Pmin 269: [9942]; AemoMinSCR - Pmin 270: [9942]; AemoMaxSCR - Pmax 271: [9942]; AemoMaxSCR - Pmax 272: [9942]; AemoMaxSCR - Pmax 273: [9942]; AemoMaxSCR - Pmax 274: [9942]; AemoMaxSCR - Pmax 275: [9942]; AemoMaxSCR - Pmin 276: [9942]; AemoMaxSCR - Pmin 277: [9942]; AemoMaxSCR - Pmin 278: [9942]; AemoMaxSCR - Pmin 279: [9942]; AemoMaxSCR - Pmin 280: [9942]; INF SCR - Pmax 281: [9942]; INF SCR - Pmax 282: [9942]; INF SCR - Pmax 283: [9942]; INF SCR - Pmax 284: [9942]; INF SCR - Pmax 285: [9942]; INF SCR - Pmin 286: [9942]; INF SCR - Pmin 287: [9942]; INF SCR - Pmin 288: [9942]; INF SCR - Pmin 289: [9942]; INF SCR - Pmin 290: [9942]
[5 empty] | disconnect_buses | AemoMinSCR - Pmax 201: [9942, 9941]; AemoMinSCR - Pmax 202: [9942, 9941]; AemoMinSCR - Pmax 203: [9942, 9941]; AemoMinSCR - Pmax 204: [9942, 9941]; AemoMinSCR - Pmax 205: [9942, 9941]; AemoMinSCR - Pmin 206: [9942, 9941]; AemoMinSCR - Pmin 207: [9942, 9941]; AemoMinSCR - Pmin 208: [9942, 9941]; AemoMinSCR - Pmin 209: [9942, 9941]; AemoMinSCR - Pmin 210: [9942, 9941]; AemoMaxSCR - Pmax 211: [9942, 9941]; AemoMaxSCR - Pmax 212: [9942, 9941]; AemoMaxSCR - Pmax 213: [9942, 9941]; AemoMaxSCR - Pmax 214: [9942, 9941]; AemoMaxSCR - Pmax 215: [9942, 9941]; AemoMaxSCR - Pmin 216: [9942, 9941]; AemoMaxSCR - Pmin 217: [9942, 9941]; AemoMaxSCR - Pmin 218: [9942, 9941]; AemoMaxSCR - Pmin 219: [9942, 9941]; AemoMaxSCR - Pmin 220: [9942, 9941]; INF SCR - Pmax 221: [9942, 9941]; INF SCR - Pmax 222: [9942, 9941]; INF SCR - Pmax 223: [9942, 9941]; INF SCR - Pmax 224: [9942, 9941]; INF SCR - Pmax 225: [9942, 9941]; INF SCR - Pmin 226: [9942, 9941]; INF SCR - Pmin 227: [9942, 9941]; INF SCR - Pmin 228: [9942, 9941]; INF SCR - Pmin 229: [9942, 9941]; INF SCR - Pmin 230: [9942, 9941]; AemoMinSCR - Pmax 231: [9942, 9941]; AemoMinSCR - Pmax 232: [9942, 9941]; AemoMinSCR - Pmax 233: [9942, 9941]; AemoMinSCR - Pmax 234: [9942, 9941]; AemoMinSCR - Pmax 235: [9942, 9941]; AemoMinSCR - Pmin 236: [9942, 9941]; AemoMinSCR - Pmin 237: [9942, 9941]; AemoMinSCR - Pmin 238: [9942, 9941]; AemoMinSCR - Pmin 239: [9942, 9941]; AemoMinSCR - Pmin 240: [9942, 9941]; AemoMaxSCR - Pmax 241: [9942, 9941]; AemoMaxSCR - Pmax 242: [9942, 9941]; AemoMaxSCR - Pmax 243: [9942, 9941]; AemoMaxSCR - Pmax 244: [9942, 9941]; AemoMaxSCR - Pmax 245: [9942, 9941]; AemoMaxSCR - Pmin 246: [9942, 9941]; AemoMaxSCR - Pmin 247: [9942, 9941]; AemoMaxSCR - Pmin 248: [9942, 9941]; AemoMaxSCR - Pmin 249: [9942, 9941]; AemoMaxSCR - Pmin 250: [9942, 9941]; INF SCR - Pmax 251: [9942, 9941]; INF SCR - Pmax 252: [9942, 9941]; INF SCR - Pmax 253: [9942, 9941]; INF SCR - Pmax 254: [9942, 9941]; INF SCR - Pmax 255: [9942, 9941]; INF SCR - Pmin 256: [9942, 9941]; INF SCR - Pmin 257: [9942, 9941]; INF SCR - Pmin 258: [9942, 9941]; INF SCR - Pmin 259: [9942, 9941]; INF SCR - Pmin 260: [9942, 9941]; AemoMinSCR - Pmax 261: [9942, 9941]; AemoMinSCR - Pmax 262: [9942, 9941]; AemoMinSCR - Pmax 263: [9942, 9941]; AemoMinSCR - Pmax 264: [9942, 9941]; AemoMinSCR - Pmax 265: [9942, 9941]; AemoMinSCR - Pmin 266: [9942, 9941]; AemoMinSCR - Pmin 267: [9942, 9941]; AemoMinSCR - Pmin 268: [9942, 9941]; AemoMinSCR - Pmin 269: [9942, 9941]; AemoMinSCR - Pmin 270: [9942, 9941]; AemoMaxSCR - Pmax 271: [9942, 9941]; AemoMaxSCR - Pmax 272: [9942, 9941]; AemoMaxSCR - Pmax 273: [9942, 9941]; AemoMaxSCR - Pmax 274: [9942, 9941]; AemoMaxSCR - Pmax 275: [9942, 9941]; AemoMaxSCR - Pmin 276: [9942, 9941]; AemoMaxSCR - Pmin 277: [9942, 9941]; AemoMaxSCR - Pmin 278: [9942, 9941]; AemoMaxSCR - Pmin 279: [9942, 9941]; AemoMaxSCR - Pmin 280: [9942, 9941]; INF SCR - Pmax 281: [9942, 9941]; INF SCR - Pmax 282: [9942, 9941]; INF SCR - Pmax 283: [9942, 9941]; INF SCR - Pmax 284: [9942, 9941]; INF SCR - Pmax 285: [9942, 9941]; INF SCR - Pmin 286: [9942, 9941]; INF SCR - Pmin 287: [9942, 9941]; INF SCR - Pmin 288: [9942, 9941]; INF SCR - Pmin 289: [9942, 9941]; INF SCR - Pmin 290: [9942, 9941]
P = 0.5 | Q0 | Q0.3 | Q-0.3 |  | TR1_from | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930 | 9930
Ploss 33kV - POC (pu) | 6.3896e-06 | 6.3896e-06 | 6.3896e-06 |  | TR1_to | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940 | 9940
Qloss 33kV - POC (pu) | -0.10186 | -0.11086 | -0.11086 |  | TR1_tap | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025
[5 empty] | dyr | AemoMinSCR - Pmax 131: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmax 132: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmax 133: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmax 134: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmax 135: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmin 136: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmin 137: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmin 138: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmin 139: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmin 140: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmax 141: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmax 142: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmax 143: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmax 144: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmax 145: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmin 146: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmin 147: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmin 148: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmin 149: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmin 150: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmax 151: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmax 152: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmax 153: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmax 154: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmax 155: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmin 156: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmin 157: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmin 158: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmin 159: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmin 160: SUMSF_SMIB_V0_Qctrl.dyr; X/R = 14 161: SUMSF_SMIB_V0_Qctrl.dyr; X/R = 14 162: SUMSF_SMIB_V0_Qctrl.dyr; X/R = 14 163: SUMSF_SMIB_V0_Qctrl.dyr; X/R = 14 164: SUMSF_SMIB_V0_Qctrl.dyr; X/R = 3 165: SUMSF_SMIB_V0_Qctrl.dyr; X/R = 3 166: SUMSF_SMIB_V0_Qctrl.dyr; X/R = 3 167: SUMSF_SMIB_V0_Qctrl.dyr; X/R = 3 168: SUMSF_SMIB_V0_Qctrl.dyr; Place holder 169: SUMSF_SMIB_V0_Qctrl.dyr; Place holder 170: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmax 171: SUMSF_SMIB_V0_PFctrl.dyr; AemoMinSCR - Pmax 172: SUMSF_SMIB_V0_PFctrl.dyr; AemoMinSCR - Pmax 173: SUMSF_SMIB_V0_PFctrl.dyr; AemoMinSCR - Pmax 174: SUMSF_SMIB_V0_PFctrl.dyr; AemoMinSCR - Pmax 175: SUMSF_SMIB_V0_PFctrl.dyr; AemoMinSCR - Pmin 176: SUMSF_SMIB_V0_PFctrl.dyr; AemoMinSCR - Pmin 177: SUMSF_SMIB_V0_PFctrl.dyr; AemoMinSCR - Pmin 178: SUMSF_SMIB_V0_PFctrl.dyr; AemoMinSCR - Pmin 179: SUMSF_SMIB_V0_PFctrl.dyr; AemoMinSCR - Pmin 180: SUMSF_SMIB_V0_PFctrl.dyr; AemoMaxSCR - Pmax 181: SUMSF_SMIB_V0_PFctrl.dyr; AemoMaxSCR - Pmax 182: SUMSF_SMIB_V0_PFctrl.dyr; AemoMaxSCR - Pmax 183: SUMSF_SMIB_V0_PFctrl.dyr; AemoMaxSCR - Pmax 184: SUMSF_SMIB_V0_PFctrl.dyr; AemoMaxSCR - Pmax 185: SUMSF_SMIB_V0_PFctrl.dyr; AemoMaxSCR - Pmin 186: SUMSF_SMIB_V0_PFctrl.dyr; AemoMaxSCR - Pmin 187: SUMSF_SMIB_V0_PFctrl.dyr; AemoMaxSCR - Pmin 188: SUMSF_SMIB_V0_PFctrl.dyr; AemoMaxSCR - Pmin 189: SUMSF_SMIB_V0_PFctrl.dyr; AemoMaxSCR - Pmin 190: SUMSF_SMIB_V0_PFctrl.dyr; INF SCR - Pmax 191: SUMSF_SMIB_V0_PFctrl.dyr; INF SCR - Pmax 192: SUMSF_SMIB_V0_PFctrl.dyr; INF SCR - Pmax 193: SUMSF_SMIB_V0_PFctrl.dyr; INF SCR - Pmax 194: SUMSF_SMIB_V0_PFctrl.dyr; INF SCR - Pmax 195: SUMSF_SMIB_V0_PFctrl.dyr; INF SCR - Pmin 196: SUMSF_SMIB_V0_PFctrl.dyr; INF SCR - Pmin 197: SUMSF_SMIB_V0_PFctrl.dyr; INF SCR - Pmin 198: SUMSF_SMIB_V0_PFctrl.dyr; INF SCR - Pmin 199: SUMSF_SMIB_V0_PFctrl.dyr; INF SCR - Pmin 200: SUMSF_SMIB_V0_PFctrl.dyr; AemoMinSCR - Pmax 231: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmax 232: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmax 233: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmax 234: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmax 235: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmin 236: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmin 237: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmin 238: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmin 239: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmin 240: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmax 241: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmax 242: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmax 243: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmax 244: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmax 245: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmin 246: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmin 247: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmin 248: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmin 249: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmin 250: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmax 251: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmax 252: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmax 253: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmax 254: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmax 255: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmin 256: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmin 257: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmin 258: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmin 259: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmin 260: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmax 261: SUMSF_SMIB_V0_PFctrl.dyr; AemoMinSCR - Pmax 262: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmax 263: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmax 264: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmax 265: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmin 266: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmin 267: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmin 268: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmin 269: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmin 270: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmax 271: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmax 272: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmax 273: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmax 274: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmax 275: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmin 276: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmin 277: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmin 278: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmin 279: SUMSF_SMIB_V0_Qctrl.dyr; AemoMaxSCR - Pmin 280: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmax 281: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmax 282: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmax 283: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmax 284: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmax 285: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmin 286: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmin 287: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmin 288: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmin 289: SUMSF_SMIB_V0_Qctrl.dyr; INF SCR - Pmin 290: SUMSF_SMIB_V0_Qctrl.dyr; AemoMinSCR - Pmax 291: SUMSF_SMIB_V0_Iq.dyr; AemoMinSCR - Pmax 292: SUMSF_SMIB_V0_Iq.dyr; AemoMinSCR - Pmax 293: SUMSF_SMIB_V0_Iq.dyr; AemoMinSCR - Pmax 294: SUMSF_SMIB_V0_Iq.dyr; AemoMinSCR - Pmax 295: SUMSF_SMIB_V0_Iq.dyr; AemoMinSCR - Pmin 296: SUMSF_SMIB_V0_Iq.dyr; AemoMinSCR - Pmin 297: SUMSF_SMIB_V0_Iq.dyr; AemoMinSCR - Pmin 298: SUMSF_SMIB_V0_Iq.dyr; AemoMinSCR - Pmin 299: SUMSF_SMIB_V0_Iq.dyr; AemoMinSCR - Pmin 300: SUMSF_SMIB_V0_Iq.dyr; AemoMaxSCR - Pmax 301: SUMSF_SMIB_V0_Iq.dyr; AemoMaxSCR - Pmax 302: SUMSF_SMIB_V0_Iq.dyr; AemoMaxSCR - Pmax 303: SUMSF_SMIB_V0_Iq.dyr; AemoMaxSCR - Pmax 304: SUMSF_SMIB_V0_Iq.dyr; AemoMaxSCR - Pmax 305: SUMSF_SMIB_V0_Iq.dyr; AemoMaxSCR - Pmin 306: SUMSF_SMIB_V0_Iq.dyr; AemoMaxSCR - Pmin 307: SUMSF_SMIB_V0_Iq.dyr; AemoMaxSCR - Pmin 308: SUMSF_SMIB_V0_Iq.dyr; AemoMaxSCR - Pmin 309: SUMSF_SMIB_V0_Iq.dyr; AemoMaxSCR - Pmin 310: SUMSF_SMIB_V0_Iq.dyr
PSCAD-specific | Name | ProjectNo | Module | PSCAD ID | Symbol
| GridSource | Project1 | Main | 1927070795 | SCL | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 251.5 | 839.1 | 251.5 | 839.1 | 251.5 | 839.1 | 251.5 | 839.1 | 270 | 270 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 270 | 900 | 270 | 900 | 270 | 900 | 270 | 900 | 899910 | 899910 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 251.5 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 108 | 900 | 108 | 180 | 171 | 162 | 153 | 144 | 135 | 126 | 117 | 108 | 99 | 90 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
| GridSource | Project1 | Main | 1927070795 | X_R | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3 | 3.77 | 3 | 3.77 | 3 | 3.77 | 14 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 14 | 14 | 14 | 14 | 3 | 3 | 3 | 3 | 3 | 14 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| V setpoint | Project1 | Main | 163769877 | VstpDefault | 1.02 | 1.058 | 0.98203 | 1.073 | 0.967 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.073 | 0.967 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.073 | 0.967 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.073 | 0.967 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.073 | 0.967 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.073 | 0.967 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.073 | 0.967 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.073 | 0.967 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.073 | 0.967 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.073 | 0.967 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.073 | 0.967 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.073 | 0.967 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.07 | 0.97 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.07 | 0.97 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.07 | 0.97 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.07 | 0.97 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.07 | 0.97 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.07 | 0.97 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.07 | 0.97 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.07 | 0.97 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.07 | 0.97 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.07 | 0.97 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.07 | 0.97 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.07 | 0.97 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.07 | 0.97 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.07 | 0.97 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.07 | 0.97 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.07 | 0.97 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.058 | 0.98203 | 1.07 | 0.97 | 1.02 | 1.058 | 0.98203 | 1.07 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02
| Q setpoint | Project1 | Main | 163769877 | QstpDefault | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PF setpoint | Project1 | Main | 163769877 | PFstpDefault | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| P setpoint | Project1 | Main | 163769877 | PstpDefault | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.5 | 0.5 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 0.05 | 0.05 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| P1 setpoint | Project1 | Main | 163769877 | P1stpDefault | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.25 | 0.25 | 0.25 | 0.25 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.45833 | 0.41667 | 0.375 | 0.33333 | 0.29167 | 0.25 | 0.20833 | 0.16667 | 0.125 | 0.083333 | 0.041667 | 0.013889
| Irradiance | Project1 | Main | 163769877 | AUXstpDefault | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 500 | 500 | 500 | 500 | 50 | 50 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
| PV Breaker | Project1 | Main | 1857394408 | Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PV switch | Project1 | Main | 2080782626 | Value | bar: AemoMinSCR - Pmax 1 to SCR=1.2, X/R=3 337
| BESS Breaker | Project1 | Main | 1279062394 | Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| INF bus Breaker time | Project1 | Main | 1406746118 | Value | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
| HV_tap | Project1 | Main | 534238275 | Pos0 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
| Q Control Mode | Project1 | Main | 1899582292 | FileNum | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Number of BESS INVs | Project1 | Main | 1248158520 | Value | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 33 | 30 | 27 | 24 | 21 | 18 | 15 | 12 | 9 | 6 | 3 | 1
| Initial P BESS | Project1 | Main | 1899582292 | BatPwrAtInit | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 22500 | 22500 | 22500 | 22500 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 2250 | 2250 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000
| Initial Q BESS | Project1 | Main | 1899582292 | BatPwrRtInit | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Initial P PV | Project1 | Main | 1899582292 | PvPwrAtInit | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 22500 | 22500 | 22500 | 22500 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 2250 | 2250 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 2250 | 2250 | 2250 | 2250 | 2250 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000
| Initial Q PV | Project1 | Main | 1899582292 | PvPwrRtInit | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 13500 | -13500 | 17775 | -17775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on G4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on LE4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on LG4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on LH4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on LI4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on LJ4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on LK4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on LL4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on LM4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on LN4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on LO4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on LP4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on LQ4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on LR4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on LS4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on LT4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on LU4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on LV4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on LW4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on LX4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on LY4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on LZ4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on MA4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on MB4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on MC4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on MD4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on ME4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on F13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: to be specified in MW Reply: P at POC
Note on F25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: transformer tap settinngs are not required to be provided, but can be provided explicitly in the given format to enforce a specific tap setting.
Note on G38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on GY38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on IC38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on JG38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on KK38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LE38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LH38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LI38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LJ38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LK38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LL38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LM38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LN38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LO38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LP38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LQ38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LR38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LS38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LT38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LU38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LV38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LW38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LX38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LY38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LZ38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on MA38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on MB38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on MC38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on MD38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on ME38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on G39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on GY39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on IC39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on JG39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on KK39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on LE39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on LH39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on LI39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on LJ39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on LK39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on LL39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on LM39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on LN39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on LO39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on LP39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on LQ39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on LR39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on LS39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on LT39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on LU39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on LV39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on LW39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on LX39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on LY39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on LZ39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on MA39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on MB39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on MC39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on MD39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on ME39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on G40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on GY40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on IC40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on JG40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on KK40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LE40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LH40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LI40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LJ40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LK40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LL40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LM40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LN40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LO40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LP40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LQ40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LR40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LS40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LT40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LU40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LV40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LW40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LX40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LY40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LZ40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on MA40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on MB40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on MC40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on MD40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on ME40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on G41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on GY41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on IC41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on JG41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on KK41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LE41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on LH41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on LI41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on LJ41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on LK41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on LL41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on LM41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on LN41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on LO41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on LP41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on LQ41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on LR41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on LS41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on LT41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on LU41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on LV41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on LW41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on LX41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on LY41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on LZ41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on MA41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on MB41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on MC41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on MD41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on ME41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)

## Profiles
category
profile name | MAT_V_STEP_Fig3 |  | MAT_V_STEP_Fig8 |  | MAT_V_STEP_Fig9 |  | MAT_V_STEP_Fig10.1 |  | MAT_V_STEP_Fig10.2 |  | MAT_V_STEP_Fig10.3 |  | MAT_VREF_STEP_Fig2 |  | MAT_QREF_STEP_Fig4 |  | MAT_QREF_STEP_Fig4.1 |  | MAT_P_STEP_Fig5 |  | MAT_ANG_STEP+/-20deg |  | MAT_ANG_STEP+/-40deg |  | MAT_ANG_STEP+/-60deg |  | MAT_ANG_STEP |  | MAT_P_STEP_Fig12 |  | AVAIL_P_-20% |  | AVAIL_P_+20% |  | MAT_F_RAMP_4Hzs |  | MAT_F_RAMP_2Hzs |  | MAT_P_STEP |  | V_STP_STEP_+/-5% |  | V_STEP_+/-5% |  | V_STP_STEP_-/+5% |  | V_STEP_-/+5% |  | P_STEP_+25% |  | P_STEP_+75% |  | P_STEP_-25% |  | P_STEP_-75% |  | F_RAMP_+/-1Hz_4Hzs |  | F_PROFILE_Fig6_1 |  | F_PROFILE_Fig6_2 |  | F_PROFILE_Fig6_3 |  | F_PROFILE_Fig6_4 |  | F_PROFILE_Fig7_1 |  | F_PROFILE_Fig7_2 |  | S5.2.5.3_47Hz |  | FLAT_RUN_300 |  | FLAT_RUN_5 |  | S5253_UF |  | S5253_OF |  | S5253_UF_short |  | S5253_OF_short |  | S5253_+/-1Hz_4Hzs |  | S5254_LVRT |  | S5254_LVRT_Qmin |  | S5254_LVRT_Qmax |  | S5254_HVRT |  | S5254_HVRT_Qmin |  | S5254_HVRT_Qmax |  | S5254_090_CUO |  | S5254_110_CUO |  | S5254_090_CUO_short |  | S5254_110_CUO_short |  | S5254_115 |  | S5257_OF_ShedLoad |  | S5258_OF_TRIP |  | S5258_UF_TRIP |  | S5258_OV_TRIP |  | S5258_UV_TRIP |  | S5258_UF_46.8Hz |  | S5258_OV_130 |  | S5258_OV_123 |  | S5258_OV_120 |  | S5258_UV_85 |  | S5258_UV_79 |  | S5258_UV_50 |  | S52511_F_db_up |  | S52511_F_db_dwn |  | S52511_+1Hz |  | S52511_-1Hz |  | S52511_F_db |  | S52511_+/-1Hz |  | S52513_V0+/-5% |  | S52513_Vmax-2.5%/+5% |  | S52513_Vmin+2.5%/-5% |  | S52513_Q0+/-15 |  | S52513_Qmax-10/+20 |  | S52513_Qmin+10/-20 |  | S52513_PF0+/-0.02 |  | S52513_PFMax-0.01/+0.03 |  | S52513_PFMin+0.01/-0.03 |  | S52513_V_STEP_+/-5% |  | S52514_-/+50% |  | LowSCR_V0-/+5% |  | LowSCR_V0-5% |  | LowSCR_V0-10% |  | LowSCR_V_inf |  | S52513_Network_up |  | S52513_Network_down
Scaling: the setpoint profiles: will be scaled using the bases defined in the context menu of the Setpoint block if the selected option is "absolute". If the selected option is "relative", the profile will be based on the initial value from the "setpoints" sheet. This can be useful for applying X% variation to a quantity. For the Grid source profiles: the voltage will be scaled on basekV defined in the context menu of the GridSourceBlock (absolute) or based on the initial voltage (relative). The frequency is always absolute and expressed in Hz and the setting is ignored THe Angle Profile will always be in degrees relative to the initial value, henve the setting is also ignored | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | absolute |  | absolute |  | relative |  | relative |  | relative |  | relative |  |  |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | relative |  | absolute |  | relative |  | absolute |  | relative |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute | [15 empty] | relative |  | relative | [9 empty] | absolute |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative | [47 empty] | relative |  | relative |  | relative |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | relative |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | relative |  | relative
scaling factor (PSCAD / PSSE) |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | 1 | 1 | 1 | 90000 | 1 | 90000 | 1 | 1 | [8 empty] | 1 | 90000 | 0.33578 | 0.00041667 | 0.3415 | 0.00041667 | [5 empty] | 1 | [110 empty] | 0.011111 | 1000 | 0.011111 | 1000 | 0.011111 | 1000 |  | 1 |  | 1 |  | 1 |  |  |  | 90000
offset (PSCAD / PSSE) | [30 empty] | 0 |  | 0
| time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y
point 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 1000 | 0 | 1000 | 0 | 50 | 0 | 50 | 0 | 1 | 0 | 1.06 | 0 | 1 | 0 | 1.06 | 0 | 1 | 0 | 0.05 | 0 | 0.05 | 0 | 1 | 0 | 1 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 1 | 0 | 1 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 50 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 1 | 0 | 1 | 0 | 50 | 0 | 0.99917 | 0 | 0.99917 | 0 | 0.99917 | 0 | 0.99917 | 0 | 0.99917 | 0 | 0.99917 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 35.55 | 0 | -35.55 | 0 | 1 | 0 | 0.93 | 0 | -0.93 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0.95 | 0 | 1 | 0 | 1
point 2 | 7 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 0 | 5 | 0 | 5 | 1 | 5 | 20 | 5 | 40 | 5 | 60 | 5 | 20 | 5 | 0.05 | 5 | 1000 | 0.5 | 1000 | 5 | 50 | 5 | 50 | 5 | 1 | 5 | 1.06 | 5 | 1 | 5 | 1.06 | 5 | 1 | 5 | 0.05 | 5 | 0.05 | 5 | 1 | 5 | 1 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 2 | 1 | 2 | 1 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 50 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 1 | 5 | 1 | 5 | 50 | 5 | 0.99917 | 5 | 0.99917 | 5 | 0.99917 | 5 | 0.99917 | 5 | 0.99917 | 5 | 0.99917 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 0 | 5 | 35.55 | 5 | -35.55 | 5 | 1 | 5 | 0.93 | 5 | -0.93 | 5 | 1 | 5 | 1 | 10 | 1 | 10 | 1 | 10 | 1 | 5 | 0.95 | 5 | 1 | 5 | 1
. | 7.001 | 1.05 | 11 | 0.9 | 5.001 | 1.1 | 5.001 | 0.1 | 5.001 | 0.5 | 5.001 | 0.8 | 5.001 | 1.05 | 5.001 | -0.3 | 5.001 | -0.15 | 5.001 | 0.5 | 15 | 0 | 15 | 0 | 15 | 0 | 15 | 0 | 5.001 | 0.2 | 15 | 800 | 0.51 | 500 | 5.5 | 52 | 6 | 52 | 7 | 1 | 5.001 | 1.114 | 5.001 | 1.05 | 5.001 | 1.007 | 5.001 | 0.95 | 5.001 | 0.3 | 5.001 | 0.8 | 5.001 | 0.75 | 5.001 | 0.25 | 5.5 | 51 | 5.5 | 52 | 5.4375 | 51.75 | 5.375 | 51.5 | 8 | 52 | 5.75 | 47 | 8 | 47 | 5.75 | 47 | 300 | 1 | 5 | 1 | 5.75 | 47 | 5.5 | 52 | 5.75 | 47 | 5.5 | 52 | 5.25 | 51 | 5.001 | 0.7 | 5.001 | 0.7 | 5.001 | 0.7 | 5.001 | 1.35 | 5.001 | 1.35 | 5.001 | 1.35 | 5.001 | 0.9 | 5.001 | 1.1 | 5.001 | 0.9 | 5.001 | 1.1 | 5.001 | 1.15 | 5.5 | 50.5 | 5.5 | 53 | 5.5 | 46 | 5.5 | 1.8 | 5.5 | 0.1 | 5.5 | 46.8 | 5.001 | 1.4 | 5.001 | 1.3 | 5.001 | 1.2 | 5.001 | 0.8 | 5.001 | 0.6 | 5.001 | 0.3 | 5.5 | 50.015 | 5.5 | 49.985 | 5.5 | 51 | 5.5 | 49 | 5.5 | 50.015 | 5.5 | 51 | 5.001 | 1.05 | 5.001 | 0.975 | 5.001 | 1.025 | 5.001 | -15 | 5.001 | 25.55 | 5.001 | -25.55 | 5.001 | 0.98 | 5.001 | 0.94 | 5.001 | -0.94 | 5.001 | 1.05 | 15 | 0.5 | 10.001 | 0.95 | 10.001 | 0.95 | 10.001 | 0.9 | 5.001 | 1.02 | 5.001 | 1.05 | 5.001 | 0.95
. | 17 | 1.05 | 20 | 0.9 | 15 | 1.1 | 5.43 | 0.1 | 5.43 | 0.5 | 5.43 | 0.8 | 15 | 1.05 | 15 | -0.3 | 15 | -0.15 | 15 | 0.5 | 30 | 0 | 30 | 0 | 30 | 0 | 30 | 0 | 10 | 0.2 | 20 | 800 | 5 | 500 | 15 | 52 | 15 | 52 | 7.001 | 0.8 | 12.5 | 1.113 | 12.5 | 1.05 | 12.5 | 1.007 | 12.5 | 0.95 | 10 | 0.3 | 10 | 0.8 | 10 | 0.75 | 10 | 0.25 | 15 | 51 | 15 | 52 | 15 | 51.75 | 15 | 51.5 | 15 | 52 | 15 | 47 | 15 | 47 | 600.75 | 47 |  |  |  |  | 125.75 | 47 | 605.5 | 52 | 15.75 | 47 | 15.5 | 52 | 15 | 51 | 7 | 0.7 | 7 | 0.7 | 7 | 0.7 | 5.02 | 1.35 | 5.02 | 1.35 | 5.02 | 1.35 | 605 | 0.9 | 605 | 1.1 | 30 | 0.9 | 30 | 1.1 | 605 | 1.15 | 15.5 | 50.5 | 70.5 | 53 | 70.5 | 46 | 15.5 | 1.8 | 15.5 | 0.1 | 6.5 | 46.8 | 10 | 1.4 | 10 | 1.3 | 30 | 1.2 | 20 | 0.8 | 10 | 0.6 | 10 | 0.3 | 10.5 | 50.015 | 10.5 | 49.985 | 10.5 | 51 | 10.5 | 49 | 10.5 | 50.015 | 10.5 | 51 | 12.5 | 1.05 | 12.5 | 0.975 | 12.5 | 1.025 | 12.5 | -15 | 12.5 | 25.55 | 12.5 | -25.55 | 12.5 | 0.98 | 12.5 | 0.94 | 12.5 | -0.94 | 12.5 | 1.05 | 25 | 0.5 | 15 | 0.95 | 10.04 | 0.95 | 10.04 | 0.9 | 20 | 1.02 | 15 | 1.05 | 15 | 0.95
. | 17.001 | 1 | 26 | 1.1 | 15.01 | 0.9 | 5.431 | 0.8 | 5.431 | 0.8 | 5.431 | 0.8 | 15.001 | 1 | 15.001 | 0 | 15.001 | 0 | 15.001 | 0.05 | [8 empty] | 10.001 | 0.4 |  |  | 15 | 700 | 15.5 | 50 | 16 | 50 | 12 | 0.8 | 12.5001 | 1.06 | 12.5001 | 1 | 12.5001 | 1.06 | 12.5001 | 1 | 10.001 | 0.05 | 10.001 | 0.05 | 10.001 | 1 | 10.001 | 1 | 15.5 | 50 | 15.5 | 50 | 15.4375 | 50 | 15.375 | 50 | 18 | 50 | 15.75 | 50 | 18 | 50 | 606.5 | 50 |  |  |  |  | 126 | 48 | 606 | 50 | 16 | 48 | 16 | 50 | 15.25 | 50 | 7.001 | 0.8 | 7.001 | 0.8 | 7.001 | 0.8 | 5.021 | 1.3 | 5.021 | 1.3 | 5.021 | 1.3 | 605.01 | 50 | 605.01 | 1 | 30.01 | 1 | 30.01 | 1 | 605.01 | 1 | 16 | 50 | 71 | 50 | 71 | 50 | 16 | 1 | 16 | 1 | 7 | 50 | 10.01 | 0.99917 | 10.01 | 0.99917 | 30.01 | 0.99917 | 20.01 | 0.99917 | 10.01 | 0.99917 | 10.01 | 0.99917 | 11 | 50 | 11 | 50 | 11 | 50 | 11 | 50 | 11 | 50 | 11 | 50 | 12.5001 | 1 | 12.5001 | 1.05 | 12.5001 | 0.95 | 12.5001 | 0 | 12.5001 | 45.55 | 12.5001 | -45.55 | 12.5001 | 1 | 12.5001 | 0.9 | 12.5001 | -0.9 | 12.5001 | 1 | 35 | 1 | 15.001 | 1 | 10.041 | 1 | 10.041 | 1
. | 27 | 1 | 35 | 1.1 | 25 | 0.9 | 6.43 | 1 | 6.43 | 1 | 6.43 | 1 | 25 | 1 | 25 | 0 | 25 | 0 | 25 | 0.05 | [8 empty] | 15 | 0.4 |  |  | 20 | 700 | 25 | 50 | 25 | 50 | 12.001 | 0.6 | 20 | 1.06 | 20 | 1 | 20 | 1.06 | 20 | 1 | 15 | 0.05 | 15 | 0.05 | 15 | 1 | 15 | 1 | 25 | 50 | 28.001 | 50 | 28.001 | 50 | 28.001 | 50 | 28.001 | 50 | 28.001 | 50 | 28.001 | 50 | 616 | 50 |  |  |  |  | 605.75 | 48 | 700 | 50 | 25.75 | 48 | 25.5 | 50 | 25 | 50 | 15 | 0.8 | 15 | 0.8 | 15 | 0.8 | 5.2 | 1.3 | 5.2 | 1.3 | 5.2 | 1.3 | 650 | 50 | 650 | 1 | 40 | 1 | 40 | 1 | 700 | 1 | 20 | 50 | 75 | 50 | 75 | 50 | 20 | 1 | 20 | 1 | 11 | 50 | 15 | 0.99917 | 15 | 0.99917 | 35 | 0.99917 | 25 | 0.99917 | 15 | 0.99917 | 15 | 0.99917 | 15 | 50 | 15 | 50 | 15 | 50 | 15 | 50 | 15 | 50 | 15 | 50 | 20 | 1 | 20 | 1.05 | 20 | 0.95 | 20 | 0 | 20 | 45.55 | 20 | -45.55 | 20 | 1 | 20 | 0.9 | 20 | -0.9 | 20 | 1 | 45 | 1 | 20 | 1 | 20 | 1 | 20 | 1
. | 27.001 | 0.95 | 41 | 0.9 | 25.01 | 1.1 | 12 | 1 | 12 | 1 | 12 | 1 | 25.001 | 0.95 | 25.001 | 0.3 | 25.001 | 0.15 | 25.001 | 1 | [8 empty] | 15.001 | 0.6 | [8 empty] | 17 | 0.6 | [36 empty] | 606.25 | 49.5 |  |  | 26.25 | 49.5 |  |  |  |  | 15.001 | 0.9 | 15.001 | 0.9 | 15.001 | 0.9 | 5.201 | 1.25 | 5.201 | 1.25 | 5.201 | 1.25 | [42 empty] | 15.5 | 49.985 | 15.5 | 49 | 20.001 | 0.95 | 20.001 | 1 | 20.001 | 1 | 20.001 | 15 | 20.001 | 35.55 | 20.001 | -35.55 | 20.001 | -0.98 | 20.001 | 0.93 | 20.001 | -0.93 | 20.001 | 0.95
. | 37 | 0.95 | 50 | 0.9 | 35 | 1.1 | [6 empty] | 35 | 0.95 | 35 | 0.3 | 35 | 0.15 | 50 | 1 | [8 empty] | 20 | 0.6 | [8 empty] | 17.001 | 0.4 | [36 empty] | 700 | 49.5 |  |  | 35.75 | 49.5 |  |  |  |  | 35 | 0.9 | 35 | 0.9 | 35 | 0.9 | 7 | 1.25 | 7 | 1.25 | 7 | 1.25 | [42 empty] | 20.5 | 49.985 | 20.5 | 49 | 27.5 | 0.95 | 25 | 1 | 25 | 1 | 27.5 | 15 | 25 | 35.55 | 25 | -35.55 | 27.5 | -0.98 | 25 | 0.93 | 25 | -0.93 | 27.5 | 0.95
. | 37.001 | 1 | 56 | 1 | 35.001 | 1 | [6 empty] | 35.001 | 1 | 35.001 | 0 | 35.001 | 0 | [10 empty] | 20.001 | 0.8 | [8 empty] | 22 | 0.4 | [46 empty] | 35.01 | 1 | 35.01 | 1 | 35.01 | 1 | 7.001 | 1.2 | 7.001 | 1.2 | 7.001 | 1.2 | [42 empty] | 21 | 50 | 21 | 50 | 27.5001 | 1 |  |  |  |  | 27.5001 | 0 |  |  |  |  | 27.5001 | 1 |  |  |  |  | 27.5001 | 1
. | 47 | 1 | 65 | 1 | 45 | 1 | [6 empty] | 45 | 1 | 43 | 0 | 43 | 0 | [10 empty] | 25 | 0.8 | [8 empty] | 22.001 | 0.2 | [46 empty] | 43 | 1 | 43 | 1 | 43 | 1 | 25 | 1.2 | 25 | 1.2 | 25 | 1.2 | [42 empty] | 25 | 50 | 25 | 50 | 35 | 1 |  |  |  |  | 35 | 0 |  |  |  |  | 35 | 1 |  |  |  |  | 35 | 1
. | [28 empty] | 25.001 | 1 | [8 empty] | 27 | 0.2 | [52 empty] | 25.001 | 1.15 | 25.001 | 1.15 | 25.001 | 1.15
. | [28 empty] | 30 | 1 | [8 empty] | 27.001 | 1 | [52 empty] | 35 | 1.15 | 35 | 1.15 | 35 | 1.15
. | [38 empty] | 42 | 1 | [52 empty] | 35.001 | 1 | 35.001 | 1 | 35.001 | 1
point n | [92 empty] | 43 | 1 | 43 | 1 | 43 | 1
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Category always has to be defined in the first column belonging to a new category. Every profile defined in this sheet must have a corresponging category assigned. This is used for the labelling of the output data generated by the test script.
Note on A4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: will only be used if profile type is "absolute" Reply: Used for SMA model as the voltage to be controlled at absolute Volt value
Note on A5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: will only be applied if profile type is "absolute"
Note on FC7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: PSSE: 0 -> Q = tan(0) = 0 PSCAD: 1 -> cos(phi) = 1 -> Q = 0
Note on FC9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: PSSE input: 0.2 -> tan(0.2) PSCAD input: 0.980580676 -> cos(0.980580676)

## NetworkScenarios
For the contingency comes along with the runback scheme: + Define the contingency with the CaseNr as normal + In the following row, change the option Runback? To 1
CaseNr | Test Type | Test profile | Runback? | Event_Element | Event_Type | Event_Time | F resistance | F reactance | i_bus | j_bus | k_bus | id | location | trip_near | trip_far | arc_time | arc_success | base_kV | run in PSS/E? | CaseDescription | Case_Code | test group | simulation batch
01 | Fault | - | no | Line | 3PHG | 3 |  |  | 226893 | 250491 |  | 1 |  | 0.23 | 0.25 | 15 | -1 | 330 | no | Line fault COFF_330 - LSM_330 -- 3PHG | Coffs Harbour 330kV_Lismore 330kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
02 | Fault | - | no | Line | 3PHG | 3 |  |  | 235640 | 211640 |  | 1 |  | 0.33 | 0.73 | 5 | -1 | 132 | yes | Line fault 2GLENIN_132A - ARM_132 -- 3PHG | Glen Innes 132kV_Armidale 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
03 | Fault | - | no | Line | 3PHG | 3 |  |  | 235640 | 276041 |  | 1 |  | 0.33 | 0.43 | 5 | -1 | 132 | no | Line fault 2GLENIN_132A - 2TENTFD_132B -- 3PHG | Glen Innes 132kV_Tenterfield 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
04 | Fault | - | no | Line | 3PHG | 3 |  |  | 276041 | 294840 |  | 1 |  | 0.33 | 0.43 | 5 | -1 | 132 | no | Line fault 2TENTFD_132B - CASN_132 -- 3PHG | Tenterfield 132kV_Casino 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
05 | Fault | - | no | Line | 3PHG | 3 |  |  | 294840 | 250401 |  | 1 |  | 0.33 | 0.43 | 5 | -1 | 132 | no | Line fault CASN_132 - LSM_132 -- 3PHG | Casino 132kV_Lismore 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
06 | Fault | - | no | Line | 3PHG | 3 |  |  | 800000 | 245641 |  | 1 |  | 0.33 | 0.43 | 5 | -1 | 132 | no | Line fault MSF_132 - KOLK_132 -- 3PHG | Metz SF POC_Koolkhan 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NWdbg
07 | Fault | - | no | Line | 3PHG | 3 |  |  | 245641 | 236942 |  | 1 |  | 0.33 | 0.43 | 5 | -1 | 132 | no | Line fault KOLK_132 - GRAF_132 -- 3PHG | Koolkhan 132kV_Graffton East 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
08 | Fault | - | no | Line | 3PHG | 3 |  |  | 800009 | 250401 |  | 1 |  | 0.33 | 0.43 | 5 | -1 | 132 | no | Line fault SUM_POC_DUM - LSM_132 -- 3PHG | SUMSF DM 132kV_Lismore 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
09 | Fault | - | no | Line | 3PHG | 3 |  |  | 800009 | 245641 |  | 1 |  | 0.33 | 0.43 | 5 | -1 | 132 | no | Line fault SUM_POC_DUM - KOLK_132 -- 3PHG | SUMSF DM 132kV_Koolkhan 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
10 | Fault | - | no | Tx_2w | 3PHG | 3 |  |  | 250490 | 250401 |  | 1 |  | 0.33 | - | - | - | - | no | Tx_2w fault LSM_330 - LSM_132 -- 3PHG | Lismore 330kV_A_Lismore 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
11 | V_stp_profile | S52513_Network_up | no |  | var_change_rel | - | [12 empty] | no | Voltage setpoint change test | S52513_Network | S52513_Network | S52513_NW
12 | V_stp_profile | S52513_Network_down | no |  | var_change_rel | - | [12 empty] | no | Voltage setpoint change test | S52513_Network | S52513_Network | S52513_NW
13 | Tx_tap_profile |  | no | Tx_2w |  | 3 |  |  | 9930 | 9940 |  | 1 | [6 empty] | no | Voltage disturbance test | S52513_Network | S52513_Network | S52513_NW
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Consecutive cases. leave empty if it belong to / associated with previous contingency case
Note on B2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Test type must be selected from the pre-defined drop-list for studies to run.
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1. Test profile not applicable for Fault 2. Test profile is used in Vstp change test
Note on D2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Runback is defined as any dependent event(s) which is required following a particular event. When Runback is "yes", associated Case number should be empty.
Note on E2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1. Event Element depends on the Test Type: Tx_2W is only option for Tx_tap_profile 2. With Tx_3w is selected, k_bus should be provided
Note on F2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Event_Type depends on the selected Test Type 1. Options ON, OFF are only applicable for Switching studies 2. Options var_change_rel, var_change_abs are only applicable for the control
Note on N2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Distance from i_bus in pu. Default: 0.001
Note on A3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Consecutive cases. leave empty if it belong to / associated with previous contingency case
Note on J8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: LL: 101502 HL: 800000

## PowerCapability
category
profile name | Dis-OE_35_0.9 |  | Dis-UE_35_0.9 |  | Cha-OE_35_0.9 |  | Cha-UE_35_0.9 |  | Dis-OE_35_1.0 |  | Dis-UE_35_1.0 |  | Cha-OE_35_1.0 |  | Cha-UE_35_1.0 |  | Dis-OE_35_1.1 |  | Dis-UE_35_1.1 |  | Cha-OE_35_1.1 |  | Cha-UE_35_1.1 |  | Dis-OE_50_0.9 |  | Dis-UE_50_0.9 |  | Cha-OE_50_0.9 |  | Cha-UE_50_0.9 |  | Dis-OE_50_1.0 |  | Dis-UE_50_1.0 |  | Cha-OE_50_1.0 |  | Cha-UE_50_1.0 |  | Dis-OE_50_1.1 |  | Dis-UE_50_1.1 |  | Cha-OE_50_1.1 |  | Cha-UE_50_1.1 |  | PV_OE_35_0.9 |  | PV_UE_35_0.9 |  | PV_OE_35_1.0 |  | PV_UE_35_1.0 |  | PV_OE_35_1.1 |  | PV_UE_35_1.1 |  | PV_OE_50_0.9 |  | PV_UE_50_0.9 |  | PV_OE_50_1.0 |  | PV_UE_50_1.0 |  | PV_OE_50_1.1 |  | PV_UE_50_1.1
Scaling: the setpoint profiles: will be scaled using the bases defined in the context menu of the Setpoint block if the selected option is "absolute". If the selected option is "relative", the profile will be based on the initial value from the "setpoints" sheet. This can be useful for applying X% variation to a quantity. For the Grid source profiles: the voltage will be scaled on basekV defined in the context menu of the GridSourceBlock (absolute) or based on the initial voltage (relative). The frequency is always absolute and expressed in Hz and the setting is ignored THe Angle Profile will always be in degrees relative to the initial value, henve the setting is also ignored | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative
scaling factor (PSCAD / PSSE) |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03 |  | 0.03
offset (PSCAD / PSSE)
| active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating | active power | derating
point 1 | 0 | 0.63 | 0 | 0.63 | 0 | 0.63 | 0 | 0.63 | 0 | 0.7 | 0 | 0.7 | 0 | 0.7 | 0 | 0.7 | 0 | 0.7 | 0 | 0.7 | 0 | 0.7 | 0 | 0.7 | 0 | 0.63 | 0 | 0.63 | 0 | 0.63 | 0 | 0.63 | 0 | 0.7 | 0 | 0.7 | 0 | 0.7 | 0 | 0.7 | 0 | 0.7 | 0 | 0.7 | 0 | 0.7 | 0 | 0.7 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0.9 | 0 | 0.9 | 0 | 0.9 | 0 | 0.9 | 0 | 0.9 | 0 | 0.9
point 2 | 0.02268 | 0.63 | 0.02268 | 0.63 | -0.02268 | 0.63 | -0.02268 | 0.63 | 0.0252 | 0.7 | 0.0252 | 0.7 | -0.0252 | 0.7 | -0.0252 | 0.7 | 0.0252 | 0.7 | 0.0252 | 0.7 | -0.0252 | 0.7 | -0.0252 | 0.7 | 0.02268 | 0.63 | 0.02268 | 0.63 | -0.02268 | 0.63 | -0.02268 | 0.63 | 0.0252 | 0.7 | 0.0252 | 0.7 | -0.0252 | 0.7 | -0.0252 | 0.7 | 0.0252 | 0.7 | 0.0252 | 0.7 | -0.0252 | 0.7 | -0.0252 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 0.9 | 1 | 0.9 | 1 | 0.9 | 1 | 0.9 | 1 | 0.9
. | 114.0198 | 0.63344 | 113.8959 | 0.63276 | -113.938 | 0.63299 | -113.8254 | 0.63236 | 126.6886 | 0.70383 | 126.551 | 0.70306 | -126.5978 | 0.70332 | -126.4727 | 0.70263 | 126.7445 | 0.70414 | 126.5821 | 0.70323 | -126.731 | 0.70406 | -126.5575 | 0.7031 | 113.9038 | 0.6328 | 113.7987 | 0.63221 | -113.8303 | 0.63239 | -113.7398 | 0.63189 | 126.5598 | 0.70311 | 126.443 | 0.70246 | -126.4781 | 0.70266 | -126.3775 | 0.7021 | 126.5598 | 0.70311 | 126.443 | 0.70246 | -126.4781 | 0.70266 | -126.3775 | 0.7021
. | 229.2791 | 0.63689 | 228.7837 | 0.63551 | -228.9521 | 0.63598 | -228.5018 | 0.63473 | 254.7545 | 0.70765 | 254.2042 | 0.70612 | -254.3912 | 0.70664 | -253.8908 | 0.70525 | 254.9778 | 0.70827 | 254.3283 | 0.70647 | -254.9241 | 0.70812 | -254.2301 | 0.70619 | 228.8153 | 0.6356 | 228.3947 | 0.63443 | -228.5213 | 0.63478 | -228.1592 | 0.63378 | 254.2392 | 0.70622 | 253.7719 | 0.70492 | -253.9125 | 0.70531 | -253.5102 | 0.70419 | 254.2392 | 0.70622 | 253.7719 | 0.70492 | -253.9125 | 0.70531 | -253.5102 | 0.70419
. | 349.4411 | 0.64711 | 347.6956 | 0.64388 | -348.1024 | 0.64463 | -346.3786 | 0.64144 | 388.2678 | 0.71901 | 386.3284 | 0.71542 | -386.7805 | 0.71626 | -384.8651 | 0.71271 | 389.14 | 0.72063 | 386.7859 | 0.71627 | -388.7568 | 0.71992 | -386.1447 | 0.71508 | 347.7369 | 0.64396 | 346.2599 | 0.64122 | -346.542 | 0.64174 | -345.1424 | 0.63915 | 386.3743 | 0.71551 | 384.7332 | 0.71247 | -385.0466 | 0.71305 | -383.4915 | 0.71017 | 386.3743 | 0.71551 | 384.7332 | 0.71247 | -385.0466 | 0.71305 | -383.4915 | 0.71017
. | 473.2847 | 0.65734 | 469.6208 | 0.65225 | -470.369 | 0.65329 | -466.6728 | 0.64816 | 525.8719 | 0.73038 | 521.8009 | 0.72472 | -522.6322 | 0.72588 | -518.5254 | 0.72017 | 527.7511 | 0.73299 | 522.7725 | 0.72607 | -526.8366 | 0.73172 | -521.2589 | 0.72397 | 469.6677 | 0.65232 | 466.5702 | 0.64801 | -467.0694 | 0.64871 | -464.0613 | 0.64453 | 521.853 | 0.7248 | 518.4114 | 0.72002 | -518.966 | 0.72079 | -515.6237 | 0.71614 | 521.853 | 0.7248 | 518.4114 | 0.72002 | -518.966 | 0.72079 | -515.6237 | 0.71614
. | 606.6106 | 0.67401 | 599.6328 | 0.66626 | -600.3394 | 0.66704 | -592.9075 | 0.65879 | 674.0118 | 0.7489 | 666.2587 | 0.74029 | -667.0438 | 0.74116 | -658.7861 | 0.73198 | 677.4256 | 0.7527 | 668.3584 | 0.74262 | -675.2054 | 0.75023 | -664.2662 | 0.73807 | 599.3708 | 0.66597 | 593.5258 | 0.65947 | -593.7789 | 0.65975 | -587.7506 | 0.65306 | 665.9676 | 0.73996 | 659.4732 | 0.73275 | -659.7543 | 0.73306 | -653.0562 | 0.72562 | 665.9676 | 0.73996 | 659.4732 | 0.73275 | -659.7543 | 0.73306 | -653.0562 | 0.72562
. | 745.9385 | 0.69068 | 734.6876 | 0.68027 | -735.2611 | 0.6808 | -722.9687 | 0.66942 | 828.8206 | 0.76743 | 816.3196 | 0.75585 | -816.9568 | 0.75644 | -803.2986 | 0.74379 | 834.1948 | 0.7724 | 819.9015 | 0.75917 | -830.238 | 0.76874 | -812.3506 | 0.75218 | 733.9883 | 0.67962 | 724.6067 | 0.67093 | -724.4653 | 0.6708 | -714.5095 | 0.66158 | 815.5426 | 0.75513 | 805.1185 | 0.74548 | -804.9614 | 0.74533 | -793.8994 | 0.73509 | 815.5426 | 0.75513 | 805.1185 | 0.74548 | -804.9614 | 0.74533 | -793.8994 | 0.73509
. | 898.9229 | 0.71343 | 881.7211 | 0.69978 | -880.4901 | 0.6988 | -861.2427 | 0.68353 | 998.8032 | 0.7927 | 979.6902 | 0.77753 | -978.3223 | 0.77645 | -956.9363 | 0.75947 | 1006.2893 | 0.79864 | 985.3641 | 0.78204 | -998.6807 | 0.7926 | -970.8998 | 0.77056 | 880.3358 | 0.69868 | 865.5858 | 0.68697 | -863.6634 | 0.68545 | -837.3638 | 0.66457 | 978.1509 | 0.77631 | 961.762 | 0.7633 | -959.626 | 0.76161 | -930.4042 | 0.73842 | 978.1509 | 0.77631 | 961.762 | 0.7633 | -959.626 | 0.76161 | -930.4042 | 0.73842
. | 1060.0962 | 0.73618 | 1035.7791 | 0.71929 | -1032.2006 | 0.71681 | -1004.5964 | 0.69764 | 1177.8846 | 0.81798 | 1150.8657 | 0.79921 | -1146.8895 | 0.79645 | -1116.2183 | 0.77515 | 1187.8301 | 0.82488 | 1159.0589 | 0.8049 | -1175.7148 | 0.81647 | -1136.0655 | 0.78893 | 1033.545 | 0.71774 | 1012.3395 | 0.70301 | -1008.1342 | 0.70009 | -961.2952 | 0.66757 | 1148.3833 | 0.79749 | 1124.8217 | 0.78113 | -1120.1491 | 0.77788 | -1068.1058 | 0.74174 | 1148.3833 | 0.79749 | 1124.8217 | 0.78113 | -1120.1491 | 0.77788 | -1068.1058 | 0.74174
. | 1236.5735 | 0.76332 | 1205.4877 | 0.74413 | -1196.011 | 0.73828 | -1152.1851 | 0.71123 | 1373.9706 | 0.84813 | 1339.4308 | 0.82681 | -1328.9011 | 0.82031 | -1280.2056 | 0.79025 | 1387.1786 | 0.85628 | 1350.8203 | 0.83384 | -1368.4228 | 0.84471 | -1314.0411 | 0.81114 | 1199.7842 | 0.74061 | 1171.9784 | 0.72344 | -1162.8205 | 0.71779 | -1077.127 | 0.66489 | 1333.0936 | 0.8229 | 1302.1983 | 0.80383 | -1292.0228 | 0.79754 | -1196.8077 | 0.73877 | 1333.0936 | 0.8229 | 1302.1983 | 0.80383 | -1292.0228 | 0.79754 | -1196.8077 | 0.73877
. | 1422.821 | 0.79046 | 1384.1377 | 0.76897 | -1367.5515 | 0.75975 | -1304.6657 | 0.72481 | 1580.9122 | 0.87828 | 1537.9307 | 0.85441 | -1519.5017 | 0.84417 | -1449.6286 | 0.80535 | 1597.8315 | 0.88768 | 1552.9992 | 0.86278 | -1571.296 | 0.87294 | -1500.0094 | 0.83334 | 1374.2559 | 0.76348 | 1338.9721 | 0.74387 | -1323.8778 | 0.73549 | -1191.9965 | 0.66222 | 1526.951 | 0.84831 | 1487.7468 | 0.82653 | -1470.9753 | 0.81721 | -1324.4405 | 0.7358 | 1526.951 | 0.84831 | 1487.7468 | 0.82653 | -1470.9753 | 0.81721 | -1324.4405 | 0.7358
. | 1462.8332 | 0.79675 | 1422.7349 | 0.77491 | -1403.6671 | 0.76452 | -1334.0683 | 0.72662 | 1625.3702 | 0.88528 | 1580.8166 | 0.86101 | -1559.6302 | 0.84947 | -1482.2981 | 0.80735 | 1642.9707 | 0.89486 | 1596.8004 | 0.86972 | -1614.1204 | 0.87915 | -1539.967 | 0.83876 | 1411.5476 | 0.76882 | 1375.0275 | 0.74893 | -1353.5125 | 0.73721 | -1216.3437 | 0.6625 | 1568.3862 | 0.85424 | 1527.8083 | 0.83214 | -1503.9028 | 0.81912 | -1351.4929 | 0.73611 | 1568.3862 | 0.85424 | 1527.8083 | 0.83214 | -1503.9028 | 0.81912 | -1351.4929 | 0.73611
point n | 1503.2986 | 0.80304 | 1461.7602 | 0.78085 | -1440.1265 | 0.7693 | -1363.6006 | 0.72842 | 1670.3318 | 0.89227 | 1624.178 | 0.86762 | -1600.1405 | 0.85478 | -1515.1118 | 0.80935 | 1688.6269 | 0.90204 | 1641.1013 | 0.87666 | -1657.3919 | 0.88536 | -1580.315 | 0.84419 | 1449.2239 | 0.77416 | 1411.4467 | 0.75398 | -1383.271 | 0.73893 | -1240.7107 | 0.66277 | 1610.2488 | 0.86018 | 1568.2741 | 0.83775 | -1536.9678 | 0.82103 | -1378.5675 | 0.73641 | 1610.2488 | 0.86018 | 1568.2741 | 0.83775 | -1536.9678 | 0.82103 | -1378.5675 | 0.73641
| 1544.2172 | 0.80934 | 1501.2135 | 0.7868 | -1476.9295 | 0.77407 | -1393.2627 | 0.73022 | 1715.7969 | 0.89926 | 1668.015 | 0.87422 | -1641.0328 | 0.86008 | -1548.0696 | 0.81136 | 1734.8 | 0.90922 | 1685.9019 | 0.8836 | -1701.1103 | 0.89157 | -1621.0535 | 0.84961 | 1487.2847 | 0.7795 | 1448.2296 | 0.75903 | -1413.1533 | 0.74065 | -1265.0977 | 0.66305 | 1652.5386 | 0.86611 | 1609.144 | 0.84337 | -1570.1704 | 0.82294 | -1405.6641 | 0.73672 | 1652.5386 | 0.86611 | 1609.144 | 0.84337 | -1570.1704 | 0.82294 | -1405.6641 | 0.73672
| 1585.5889 | 0.81563 | 1541.0949 | 0.79274 | -1514.0763 | 0.77885 | -1423.0546 | 0.73202 | 1761.7655 | 0.90626 | 1712.3276 | 0.88083 | -1682.307 | 0.86538 | -1581.1717 | 0.81336 | 1781.4901 | 0.9164 | 1731.2021 | 0.89054 | -1745.2758 | 0.89778 | -1662.1825 | 0.85503 | 1525.7301 | 0.78484 | 1485.3763 | 0.76408 | -1443.1594 | 0.74237 | -1289.5045 | 0.66333 | 1695.2557 | 0.87205 | 1650.4181 | 0.84898 | -1603.5105 | 0.82485 | -1432.7828 | 0.73703 | 1695.2557 | 0.87205 | 1650.4181 | 0.84898 | -1603.5105 | 0.82485 | -1432.7828 | 0.73703
| 1627.4138 | 0.82193 | 1581.4042 | 0.79869 | -1551.5667 | 0.78362 | -1452.9762 | 0.73383 | 1808.2376 | 0.91325 | 1757.1158 | 0.88743 | -1723.9631 | 0.87069 | -1614.418 | 0.81536 | 1828.6972 | 0.92358 | 1777.0019 | 0.89748 | -1789.8882 | 0.90398 | -1703.702 | 0.86046 | 1564.5601 | 0.79018 | 1522.8867 | 0.76913 | -1473.2894 | 0.74409 | -1313.9313 | 0.6636 | 1738.4001 | 0.87798 | 1692.0964 | 0.85459 | -1636.9882 | 0.82676 | -1459.9236 | 0.73734 | 1738.4001 | 0.87798 | 1692.0964 | 0.85459 | -1636.9882 | 0.82676 | -1459.9236 | 0.73734
| 1669.6919 | 0.82822 | 1622.1416 | 0.80463 | -1589.4009 | 0.78839 | -1483.0276 | 0.73563 | 1855.2132 | 0.92024 | 1802.3796 | 0.89404 | -1766.001 | 0.87599 | -1647.8085 | 0.81737 | 1876.4212 | 0.93076 | 1823.3014 | 0.90442 | -1834.9477 | 0.91019 | -1745.612 | 0.86588 | 1603.7746 | 0.79552 | 1560.7609 | 0.77419 | -1503.5431 | 0.74581 | -1338.3779 | 0.66388 | 1781.9718 | 0.88391 | 1734.1788 | 0.86021 | -1670.6035 | 0.82867 | -1487.0865 | 0.73764 | 1781.9718 | 0.88391 | 1734.1788 | 0.86021 | -1670.6035 | 0.82867 | -1487.0865 | 0.73764
| 1712.4232 | 0.83451 | 1663.307 | 0.81058 | -1627.5788 | 0.79317 | -1513.2088 | 0.73743 | 1902.6924 | 0.92724 | 1848.1189 | 0.90064 | -1808.4209 | 0.8813 | -1681.3431 | 0.81937 | 1924.6621 | 0.93794 | 1870.1006 | 0.91136 | -1880.4542 | 0.9164 | -1787.9125 | 0.8713 | 1643.3738 | 0.80086 | 1598.9989 | 0.77924 | -1533.9207 | 0.74752 | -1362.8444 | 0.66415 | 1825.9708 | 0.88985 | 1776.6655 | 0.86582 | -1704.3563 | 0.83058 | -1514.2716 | 0.73795 | 1825.9708 | 0.88985 | 1776.6655 | 0.86582 | -1704.3563 | 0.83058 | -1514.2716 | 0.73795
| 1755.6076 | 0.84081 | 1704.9004 | 0.81652 | -1666.1004 | 0.79794 | -1543.5198 | 0.73923 | 1950.6751 | 0.93423 | 1894.3338 | 0.90725 | -1851.2227 | 0.8866 | -1715.022 | 0.82137 | 1973.4201 | 0.94512 | 1917.3994 | 0.91829 | -1926.4076 | 0.92261 | -1830.6034 | 0.87673 | 1683.3575 | 0.80621 | 1637.6006 | 0.78429 | -1564.422 | 0.74924 | -1387.3308 | 0.66443 | 1870.3972 | 0.89578 | 1819.5563 | 0.87143 | -1738.2467 | 0.83249 | -1541.4787 | 0.73826 | 1870.3972 | 0.89578 | 1819.5563 | 0.87143 | -1738.2467 | 0.83249 | -1541.4787 | 0.73826
| 1799.2452 | 0.8471 | 1746.9219 | 0.82247 | -1704.9657 | 0.80271 | -1573.9605 | 0.74104 | 1999.1613 | 0.94122 | 1941.0243 | 0.91385 | -1894.4063 | 0.89191 | -1748.845 | 0.82337 | 2022.695 | 0.9523 | 1965.1979 | 0.92523 | -1972.8081 | 0.92882 | -1873.6848 | 0.88215 | 1723.7257 | 0.81155 | 1676.5661 | 0.78934 | -1595.0472 | 0.75096 | -1411.8371 | 0.66471 | 1915.2508 | 0.90172 | 1862.8513 | 0.87705 | -1772.2747 | 0.8344 | -1568.7079 | 0.73856 | 1915.2508 | 0.90172 | 1862.8513 | 0.87705 | -1772.2747 | 0.8344 | -1568.7079 | 0.73856
| 1843.3359 | 0.8534 | 1789.3713 | 0.82841 | -1744.1747 | 0.80749 | -1604.5311 | 0.74284 | 2048.151 | 0.94822 | 1988.1904 | 0.92046 | -1937.9719 | 0.89721 | -1782.8123 | 0.82538 | 2072.4869 | 0.95948 | 2013.4961 | 0.93217 | -2019.6555 | 0.93503 | -1917.1568 | 0.88757 | 1764.4786 | 0.81689 | 1715.8954 | 0.7944 | -1625.7962 | 0.75268 | -1436.3633 | 0.66498 | 1960.5317 | 0.90765 | 1906.5505 | 0.88266 | -1806.4402 | 0.83631 | -1595.9592 | 0.73887 | 1960.5317 | 0.90765 | 1906.5505 | 0.88266 | -1806.4402 | 0.83631 | -1595.9592 | 0.73887
| 1889.4496 | 0.86041 | 1834.7716 | 0.83551 | -1778.5785 | 0.80992 | -1633.2424 | 0.74374 | 2099.3884 | 0.95601 | 2038.6351 | 0.92834 | -1976.1984 | 0.89991 | -1814.7138 | 0.82637 | 2124.5244 | 0.96745 | 2065.1108 | 0.9404 | -2068.1977 | 0.9418 | -1955.3006 | 0.89039 | 1806.0398 | 0.82242 | 1751.1177 | 0.79741 | -1651.4198 | 0.75201 | -1461.4889 | 0.66552 | 2006.7109 | 0.9138 | 1945.6863 | 0.88601 | -1834.9109 | 0.83557 | -1623.8766 | 0.73947 | 2006.7109 | 0.9138 | 1945.6863 | 0.88601 | -1834.9109 | 0.83557 | -1623.8766 | 0.73947
| 1936.0679 | 0.86741 | 1880.6826 | 0.8426 | -1813.1572 | 0.81235 | -1662.0184 | 0.74463 | 2151.1865 | 0.96379 | 2089.6473 | 0.93622 | -2014.6191 | 0.90261 | -1846.6871 | 0.82737 | 2177.1357 | 0.97542 | 2117.3175 | 0.94862 | -2117.2277 | 0.94858 | -1993.6475 | 0.89321 | 1847.9995 | 0.82796 | 1786.5572 | 0.80043 | -1676.9951 | 0.75134 | -1486.6534 | 0.66606 | 2053.3328 | 0.91995 | 1985.0636 | 0.88937 | -1863.3278 | 0.83482 | -1651.8371 | 0.74007 | 2053.3328 | 0.91995 | 1985.0636 | 0.88937 | -1863.3278 | 0.83482 | -1651.8371 | 0.74007
| 1983.1908 | 0.87442 | 1927.1044 | 0.84969 | -1847.9108 | 0.81478 | -1690.8589 | 0.74553 | 2203.5454 | 0.97158 | 2141.2271 | 0.9441 | -2053.2343 | 0.90531 | -1878.7321 | 0.82837 | 2230.3205 | 0.98339 | 2170.1162 | 0.95684 | -2166.7456 | 0.95536 | -2032.1974 | 0.89603 | 1890.3577 | 0.83349 | 1822.2139 | 0.80345 | -1702.522 | 0.75067 | -1511.8567 | 0.6666 | 2100.3975 | 0.9261 | 2024.6821 | 0.89272 | -1891.6912 | 0.83408 | -1679.8408 | 0.74067 | 2100.3975 | 0.9261 | 2024.6821 | 0.89272 | -1891.6912 | 0.83408 | -1679.8408 | 0.74067
| 2030.8184 | 0.88143 | 1974.0368 | 0.85679 | -1882.8393 | 0.8172 | -1719.764 | 0.74643 | 2256.4649 | 0.97937 | 2193.3743 | 0.95199 | -2092.0437 | 0.90801 | -1910.8489 | 0.82936 | 2284.079 | 0.99135 | 2223.5069 | 0.96506 | -2216.7515 | 0.96213 | -2070.9503 | 0.89885 | 1933.1144 | 0.83903 | 1858.0877 | 0.80646 | -1728.0007 | 0.75 | -1537.099 | 0.66714 | 2147.9049 | 0.93225 | 2064.5419 | 0.89607 | -1920.0008 | 0.83333 | -1707.8878 | 0.74127 | 2147.9049 | 0.93225 | 2064.5419 | 0.89607 | -1920.0008 | 0.83333 | -1707.8878 | 0.74127
| 2078.9506 | 0.88844 | 2021.4801 | 0.86388 | -1917.9427 | 0.81963 | -1748.7336 | 0.74732 | 2309.9451 | 0.98716 | 2246.0889 | 0.95987 | -2131.0474 | 0.9107 | -1943.0374 | 0.83036 | 2338.4112 | 0.99932 | 2277.4897 | 0.97329 | -2267.2452 | 0.96891 | -2109.9061 | 0.90167 | 1976.2695 | 0.84456 | 1894.1788 | 0.80948 | -1753.4311 | 0.74933 | -1562.3801 | 0.66768 | 2195.855 | 0.9384 | 2104.6431 | 0.89942 | -1948.2568 | 0.83259 | -1735.9779 | 0.74187 | 2195.855 | 0.9384 | 2104.6431 | 0.89942 | -1948.2568 | 0.83259 | -1735.9779 | 0.74187
| 2127.5875 | 0.89545 | 2069.434 | 0.87097 | -1953.221 | 0.82206 | -1777.7678 | 0.74822 | 2363.9861 | 0.99494 | 2299.3711 | 0.96775 | -2170.2455 | 0.9134 | -1975.2976 | 0.83135 | 2393.317 | 1.0073 | 2332.0644 | 0.98151 | -2318.2269 | 0.97568 | -2149.065 | 0.90449 | 2019.8231 | 0.85009 | 1930.487 | 0.81249 | -1778.8132 | 0.74866 | -1587.7002 | 0.66822 | 2244.2479 | 0.94455 | 2144.9855 | 0.90277 | -1976.4591 | 0.83184 | -1764.1113 | 0.74247 | 2244.2479 | 0.94455 | 2144.9855 | 0.90277 | -1976.4591 | 0.83184 | -1764.1113 | 0.74247
| 2176.7289 | 0.90246 | 2117.8987 | 0.87807 | -1988.6741 | 0.82449 | -1806.8666 | 0.74912 | 2418.5877 | 1.0027 | 2353.2208 | 0.97563 | -2209.6379 | 0.9161 | -2007.6296 | 0.83235 | 2448.7964 | 1.0153 | 2387.2312 | 0.98973 | -2369.6964 | 0.98246 | -2188.4268 | 0.90731 | 2063.7752 | 0.85563 | 1967.0124 | 0.81551 | -1804.147 | 0.74799 | -1613.0591 | 0.66876 | 2293.0835 | 0.9507 | 2185.5693 | 0.90612 | -2004.6078 | 0.8311 | -1792.2879 | 0.74307 | 2293.0835 | 0.9507 | 2185.5693 | 0.90612 | -2004.6078 | 0.8311 | -1792.2879 | 0.74307
| 2226.3751 | 0.90947 | 2166.8741 | 0.88516 | -2024.3022 | 0.82692 | -1836.0299 | 0.75001 | 2473.7501 | 1.0105 | 2407.6379 | 0.98351 | -2249.2247 | 0.9188 | -2040.0333 | 0.83335 | 2504.8495 | 1.0232 | 2442.99 | 0.99795 | -2421.6539 | 0.98924 | -2227.9916 | 0.91013 | 2108.1257 | 0.86116 | 2003.755 | 0.81853 | -1829.4325 | 0.74732 | -1638.4569 | 0.6693 | 2342.3619 | 0.95685 | 2226.3944 | 0.90947 | -2032.7028 | 0.83035 | -1820.5077 | 0.74367 | 2342.3619 | 0.95685 | 2226.3944 | 0.90947 | -2032.7028 | 0.83035 | -1820.5077 | 0.74367
| 2276.5258 | 0.91648 | 2216.3603 | 0.89225 | -2060.1052 | 0.82935 | -1865.2578 | 0.75091 | 2529.4731 | 1.0183 | 2462.6225 | 0.99139 | -2289.0057 | 0.9215 | -2072.5087 | 0.83434 | 2561.4763 | 1.0312 | 2499.3408 | 1.0062 | -2474.0993 | 0.99601 | -2267.7595 | 0.91295 | 2152.8747 | 0.8667 | 2040.7147 | 0.82154 | -1854.6697 | 0.74665 | -1663.8936 | 0.66984 | 2392.083 | 0.963 | 2267.4608 | 0.91283 | -2060.7441 | 0.82961 | -1848.7707 | 0.74427 | 2392.083 | 0.963 | 2267.4608 | 0.91283 | -2060.7441 | 0.82961 | -1848.7707 | 0.74427
| 2327.1812 | 0.92348 | 2266.3572 | 0.89935 | -2096.083 | 0.83178 | -1894.5503 | 0.75181 | 2585.7569 | 1.0261 | 2518.1746 | 0.99928 | -2328.9811 | 0.9242 | -2105.0559 | 0.83534 | 2618.6766 | 1.0392 | 2556.2836 | 1.0144 | -2527.0325 | 1.0028 | -2307.7303 | 0.91577 | 2198.0222 | 0.87223 | 2077.8917 | 0.82456 | -1879.8586 | 0.74598 | -1689.3692 | 0.67038 | 2442.2468 | 0.96915 | 2308.7685 | 0.91618 | -2088.7318 | 0.82886 | -1877.0769 | 0.74487 | 2442.2468 | 0.96915 | 2308.7685 | 0.91618 | -2088.7318 | 0.82886 | -1877.0769 | 0.74487
| 2372.3846 | 0.92816 | 2309.2265 | 0.90345 | -2124.3336 | 0.83112 | -1923.7021 | 0.75262 | 2635.9828 | 1.0313 | 2565.8073 | 1.0038 | -2360.3707 | 0.92346 | -2137.4467 | 0.83625 | 2670.7857 | 1.0449 | 2608.8857 | 1.0207 | -2566.2772 | 1.004 | -2343.4541 | 0.91684 | 2231.7932 | 0.87316 | 2113.3411 | 0.82682 | -1904.8652 | 0.74525 | -1715.5722 | 0.67119 | 2479.7702 | 0.97018 | 2348.1567 | 0.91868 | -2116.5169 | 0.82806 | -1906.1913 | 0.74577 | 2479.7702 | 0.97018 | 2348.1567 | 0.91868 | -2116.5169 | 0.82806 | -1906.1913 | 0.74577
| 2417.9248 | 0.93284 | 2352.3915 | 0.90756 | -2152.5365 | 0.83045 | -1952.9126 | 0.75344 | 2686.5831 | 1.0365 | 2613.7683 | 1.0084 | -2391.7072 | 0.92273 | -2169.9029 | 0.83715 | 2723.3088 | 1.0507 | 2661.9407 | 1.027 | -2605.6104 | 1.0053 | -2379.2556 | 0.91792 | 2265.6311 | 0.87409 | 2148.9529 | 0.82907 | -1929.8198 | 0.74453 | -1741.8334 | 0.672 | 2517.3678 | 0.97121 | 2387.7254 | 0.92119 | -2144.2442 | 0.82725 | -1935.3705 | 0.74667 | 2517.3678 | 0.97121 | 2387.7254 | 0.92119 | -2144.2442 | 0.82725 | -1935.3705 | 0.74667
| 2463.8018 | 0.93752 | 2395.852 | 0.91166 | -2180.6917 | 0.82979 | -1982.182 | 0.75425 | 2737.5576 | 1.0417 | 2662.0577 | 1.013 | -2422.9908 | 0.92199 | -2202.4244 | 0.83806 | 2776.2459 | 1.0564 | 2715.4489 | 1.0333 | -2645.0321 | 1.0065 | -2415.1348 | 0.919 | 2299.5357 | 0.87501 | 2184.7271 | 0.83133 | -1954.7222 | 0.74381 | -1768.153 | 0.67281 | 2555.0396 | 0.97224 | 2427.4746 | 0.9237 | -2171.9136 | 0.82645 | -1964.6144 | 0.74757 | 2555.0396 | 0.97224 | 2427.4746 | 0.9237 | -2171.9136 | 0.82645 | -1964.6144 | 0.74757
| 2510.0157 | 0.9422 | 2439.6081 | 0.91577 | -2208.7992 | 0.82913 | -2011.5101 | 0.75507 | 2788.9063 | 1.0469 | 2710.6756 | 1.0175 | -2454.2213 | 0.92125 | -2235.0112 | 0.83897 | 2829.5972 | 1.0622 | 2769.4101 | 1.0396 | -2684.5425 | 1.0077 | -2451.0916 | 0.92008 | 2333.5071 | 0.87594 | 2220.6637 | 0.83358 | -1979.5726 | 0.74308 | -1794.5308 | 0.67362 | 2592.7857 | 0.97327 | 2467.4041 | 0.9262 | -2199.5251 | 0.82565 | -1993.9231 | 0.74847 | 2592.7857 | 0.97327 | 2467.4041 | 0.9262 | -2199.5251 | 0.82565 | -1993.9231 | 0.74847
| 2556.5664 | 0.94688 | 2483.6597 | 0.91987 | -2236.859 | 0.82847 | -2040.897 | 0.75589 | 2840.6293 | 1.0521 | 2759.6219 | 1.0221 | -2485.3989 | 0.92052 | -2267.6633 | 0.83988 | 2883.3625 | 1.0679 | 2823.8243 | 1.0459 | -2724.1414 | 1.0089 | -2487.126 | 0.92116 | 2367.5453 | 0.87687 | 2256.7627 | 0.83584 | -2004.371 | 0.74236 | -1820.9669 | 0.67443 | 2630.6059 | 0.9743 | 2507.5141 | 0.92871 | -2227.0788 | 0.82484 | -2023.2966 | 0.74937 | 2630.6059 | 0.9743 | 2507.5141 | 0.92871 | -2227.0788 | 0.82484 | -2023.2966 | 0.74937
| 2603.454 | 0.95155 | 2528.0069 | 0.92398 | -2264.8711 | 0.8278 | -2070.3427 | 0.7567 | 2892.7266 | 1.0573 | 2808.8966 | 1.0266 | -2516.5234 | 0.91978 | -2300.3807 | 0.84078 | 2937.5419 | 1.0737 | 2878.6916 | 1.0522 | -2763.8288 | 1.0102 | -2523.238 | 0.92224 | 2401.6502 | 0.8778 | 2293.0242 | 0.83809 | -2029.1172 | 0.74164 | -1847.4613 | 0.67524 | 2668.5003 | 0.97533 | 2547.8046 | 0.93122 | -2254.5747 | 0.82404 | -2052.7348 | 0.75027 | 2668.5003 | 0.97533 | 2547.8046 | 0.93122 | -2254.5747 | 0.82404 | -2052.7348 | 0.75027
| 2650.6784 | 0.95623 | 2572.6497 | 0.92808 | -2292.8355 | 0.82714 | -2099.8471 | 0.75752 | 2945.1982 | 1.0625 | 2858.4997 | 1.0312 | -2547.595 | 0.91905 | -2333.1635 | 0.84169 | 2992.1353 | 1.0794 | 2934.012 | 1.0584 | -2802.3545 | 1.011 | -2559.4278 | 0.92331 | 2435.822 | 0.87872 | 2329.448 | 0.84035 | -2053.8114 | 0.74091 | -1874.014 | 0.67605 | 2706.4689 | 0.97636 | 2588.2755 | 0.93372 | -2282.0126 | 0.82324 | -2082.2378 | 0.75117 | 2706.4689 | 0.97636 | 2588.2755 | 0.93372 | -2282.0126 | 0.82324 | -2082.2378 | 0.75117
| 2698.2396 | 0.96091 | 2617.5881 | 0.93219 | -2320.7521 | 0.82648 | -2129.4104 | 0.75834 | 2998.044 | 1.0677 | 2908.4312 | 1.0358 | -2578.6135 | 0.91831 | -2366.0115 | 0.8426 | 3047.1428 | 1.0852 | 2989.7855 | 1.0647 | -2836.4748 | 1.0101 | -2595.6951 | 0.92439 | 2470.0605 | 0.87965 | 2366.0342 | 0.8426 | -2078.4535 | 0.74019 | -1900.625 | 0.67686 | 2744.5117 | 0.97739 | 2628.9269 | 0.93623 | -2309.3928 | 0.82243 | -2111.8055 | 0.75207 | 2744.5117 | 0.97739 | 2628.9269 | 0.93623 | -2309.3928 | 0.82243 | -2111.8055 | 0.75207
| 2746.1377 | 0.96559 | 2662.822 | 0.93629 | -2348.6211 | 0.82582 | -2159.0324 | 0.75915 | 3051.2641 | 1.0729 | 2958.6912 | 1.0403 | -2609.579 | 0.91757 | -2398.9249 | 0.8435 | 3102.5644 | 1.0909 | 3046.012 | 1.071 | -2870.5369 | 1.0093 | -2632.0401 | 0.92547 | 2504.3658 | 0.88058 | 2402.7828 | 0.84486 | -2103.0435 | 0.73947 | -1927.2942 | 0.67767 | 2782.6287 | 0.97842 | 2669.7587 | 0.93873 | -2336.715 | 0.82163 | -2141.438 | 0.75297 | 2782.6287 | 0.97842 | 2669.7587 | 0.93873 | -2336.715 | 0.82163 | -2141.438 | 0.75297
| 2794.3727 | 0.97027 | 2708.3516 | 0.9404 | -2376.4424 | 0.82515 | -2188.7132 | 0.75997 | 3104.8585 | 1.0781 | 3009.2795 | 1.0449 | -2640.4916 | 0.91684 | -2431.9036 | 0.84441 | 3158.4 | 1.0967 | 3102.6915 | 1.0773 | -2904.5407 | 1.0085 | -2668.4627 | 0.92655 | 2538.7379 | 0.88151 | 2439.6938 | 0.84712 | -2127.5815 | 0.73874 | -1954.0217 | 0.67848 | 2820.8199 | 0.97945 | 2710.7709 | 0.94124 | -2363.9794 | 0.82083 | -2171.1353 | 0.75387 | 2820.8199 | 0.97945 | 2710.7709 | 0.94124 | -2363.9794 | 0.82083 | -2171.1353 | 0.75387
| 2832.1656 | 0.97125 | 2749.4204 | 0.94287 | -2403.7934 | 0.82435 | -2219.87 | 0.76127 | 3146.8507 | 1.0792 | 3054.9115 | 1.0476 | -2670.8816 | 0.91594 | -2466.5222 | 0.84586 | 3197.88 | 1.0967 | 3147.1157 | 1.0793 | -2937.9697 | 1.0075 | -2706.3936 | 0.92812 | 2573.6779 | 0.88261 | 2478.1047 | 0.84983 | -2152.1944 | 0.73806 | -1982.1105 | 0.67974 | 2859.6422 | 0.98067 | 2753.4497 | 0.94426 | -2391.3271 | 0.82007 | -2202.345 | 0.75526 | 2859.6422 | 0.98067 | 2753.4497 | 0.94426 | -2391.3271 | 0.82007 | -2202.345 | 0.75526
| 2870.0293 | 0.97223 | 2790.6673 | 0.94535 | -2431.0863 | 0.82354 | -2251.1205 | 0.76257 | 3188.9215 | 1.0803 | 3100.7415 | 1.0504 | -2701.207 | 0.91504 | -2501.245 | 0.84731 | 3237.36 | 1.0967 | 3191.6791 | 1.0812 | -2971.3276 | 1.0065 | -2744.4374 | 0.92969 | 2608.6971 | 0.8837 | 2516.711 | 0.85254 | -2176.7583 | 0.73738 | -2010.2898 | 0.68099 | 2898.5523 | 0.98189 | 2796.3456 | 0.94727 | -2418.6203 | 0.81932 | -2233.6553 | 0.75666 | 2898.5523 | 0.98189 | 2796.3456 | 0.94727 | -2418.6203 | 0.81932 | -2233.6553 | 0.75666
| 2907.9637 | 0.97321 | 2832.0924 | 0.94782 | -2458.321 | 0.82273 | -2282.4648 | 0.76388 | 3231.0708 | 1.0813 | 3146.7694 | 1.0531 | -2731.4678 | 0.91415 | -2536.072 | 0.84875 | 3276.84 | 1.0967 | 3236.3817 | 1.0831 | -3004.6145 | 1.0056 | -2782.5942 | 0.93126 | 2643.7954 | 0.8848 | 2555.5127 | 0.85526 | -2201.2733 | 0.7367 | -2038.5594 | 0.68225 | 2937.5505 | 0.98312 | 2839.4586 | 0.95029 | -2445.8592 | 0.81856 | -2265.0661 | 0.75805 | 2937.5505 | 0.98312 | 2839.4586 | 0.95029 | -2445.8592 | 0.81856 | -2265.0661 | 0.75805
| 2945.9688 | 0.9742 | 2873.6957 | 0.9503 | -2485.4976 | 0.82192 | -2313.9029 | 0.76518 | 3273.2987 | 1.0824 | 3192.9952 | 1.0559 | -2761.664 | 0.91325 | -2571.0032 | 0.8502 | 3316.32 | 1.0967 | 3281.2237 | 1.0851 | -3037.8304 | 1.0046 | -2820.864 | 0.93283 | 2678.9729 | 0.8859 | 2594.5099 | 0.85797 | -2225.7394 | 0.73602 | -2066.9196 | 0.68351 | 2976.6366 | 0.98434 | 2882.7887 | 0.9533 | -2473.0437 | 0.81781 | -2296.5773 | 0.75945 | 2976.6366 | 0.98434 | 2882.7887 | 0.9533 | -2473.0437 | 0.81781 | -2296.5773 | 0.75945
| 2984.0446 | 0.97518 | 2915.477 | 0.95277 | -2512.616 | 0.82112 | -2345.4348 | 0.76648 | 3315.6051 | 1.0835 | 3239.4189 | 1.0586 | -2791.7956 | 0.91235 | -2606.0386 | 0.85165 | 3355.8 | 1.0967 | 3326.2049 | 1.087 | -3070.9751 | 1.0036 | -2859.2467 | 0.93439 | 2714.2295 | 0.887 | 2633.7024 | 0.86069 | -2250.1565 | 0.73535 | -2095.3702 | 0.68476 | 3015.8106 | 0.98556 | 2926.336 | 0.95632 | -2500.1739 | 0.81705 | -2328.1891 | 0.76085 | 3015.8106 | 0.98556 | 2926.336 | 0.95632 | -2500.1739 | 0.81705 | -2328.1891 | 0.76085
| 3022.1911 | 0.97616 | 2957.4365 | 0.95524 | -2539.6763 | 0.82031 | -2377.0604 | 0.76778 | 3357.9901 | 1.0846 | 3286.0406 | 1.0614 | -2821.8626 | 0.91145 | -2641.1782 | 0.85309 | 3395.28 | 1.0967 | 3371.3254 | 1.0889 | -3104.0488 | 1.0026 | -2897.7424 | 0.93596 | 2749.5653 | 0.8881 | 2673.0904 | 0.8634 | -2274.5247 | 0.73467 | -2123.9113 | 0.68602 | 3055.0726 | 0.98678 | 2970.1005 | 0.95933 | -2527.2497 | 0.8163 | -2359.9014 | 0.76224 | 3055.0726 | 0.98678 | 2970.1005 | 0.95933 | -2527.2497 | 0.8163 | -2359.9014 | 0.76224
| 3060.4083 | 0.97714 | 2999.5742 | 0.95772 | -2566.6785 | 0.8195 | -2408.7798 | 0.76909 | 3400.4536 | 1.0857 | 3332.8602 | 1.0641 | -2851.865 | 0.91056 | -2676.422 | 0.85454 | 3434.76 | 1.0967 | 3416.5851 | 1.0909 | -3137.0515 | 1.0016 | -2936.3511 | 0.93753 | 2784.9803 | 0.8892 | 2712.6738 | 0.86612 | -2298.844 | 0.73399 | -2152.5428 | 0.68727 | 3094.4225 | 0.988 | 3014.0821 | 0.96235 | -2554.2711 | 0.81554 | -2391.7142 | 0.76364 | 3094.4225 | 0.988 | 3014.0821 | 0.96235 | -2554.2711 | 0.81554 | -2391.7142 | 0.76364
| 3098.6962 | 0.97812 | 3041.8899 | 0.96019 | -2593.6225 | 0.81869 | -2440.593 | 0.77039 | 3442.9957 | 1.0868 | 3379.8777 | 1.0669 | -2881.8028 | 0.90966 | -2711.77 | 0.85599 | 3474.24 | 1.0967 | 3461.9841 | 1.0928 | -3169.9831 | 1.0006 | -2975.0727 | 0.9391 | 2820.4743 | 0.8903 | 2752.4527 | 0.86883 | -2323.1143 | 0.73331 | -2181.2648 | 0.68853 | 3133.8604 | 0.98922 | 3058.2808 | 0.96537 | -2581.2381 | 0.81478 | -2423.6275 | 0.76503 | 3133.8604 | 0.98922 | 3058.2808 | 0.96537 | -2581.2381 | 0.81478 | -2423.6275 | 0.76503
| 3137.0548 | 0.97911 | 3084.3838 | 0.96267 | -2620.5084 | 0.81789 | -2472.5 | 0.77169 | 3485.6164 | 1.0879 | 3427.0932 | 1.0696 | -2911.6761 | 0.90876 | -2747.2222 | 0.85744 | 3513.72 | 1.0967 | 3507.5224 | 1.0947 | -3202.8437 | 0.99964 | -3013.9073 | 0.94067 | 2856.0476 | 0.8914 | 2792.427 | 0.87154 | -2347.3357 | 0.73263 | -2210.0772 | 0.68979 | 3173.3862 | 0.99045 | 3102.6966 | 0.96838 | -2608.1507 | 0.81403 | -2455.6413 | 0.76643 | 3173.3862 | 0.99045 | 3102.6966 | 0.96838 | -2608.1507 | 0.81403 | -2455.6413 | 0.76643
| 3175.484 | 0.98009 | 3127.0559 | 0.96514 | -2647.3362 | 0.81708 | -2504.5007 | 0.77299 | 3528.3156 | 1.089 | 3474.5065 | 1.0724 | -2941.4847 | 0.90787 | -2782.7786 | 0.85888 | 3553.2 | 1.0967 | 3553.2 | 1.0967 | -3235.6332 | 0.99865 | -3052.8548 | 0.94224 | 2891.7 | 0.8925 | 2832.5967 | 0.87426 | -2371.5081 | 0.73195 | -2238.9801 | 0.69104 | 3213 | 0.99167 | 3147.3296 | 0.9714 | -2635.009 | 0.81327 | -2487.7557 | 0.76783 | 3213 | 0.99167 | 3147.3296 | 0.9714 | -2635.009 | 0.81327 | -2487.7557 | 0.76783
| 3213.7988 | 0.98101 | 3170.428 | 0.96777 | -2671.1464 | 0.81537 | -2538.113 | 0.77476 | 3570.8875 | 1.09 | 3522.6978 | 1.0753 | -2967.9404 | 0.90596 | -2820.1255 | 0.86084 | 3592.68 | 1.0967 | 3592.68 | 1.0967 | -3264.7345 | 0.99656 | -3095.2967 | 0.94484 | 2923.83 | 0.8925 | 2873.2834 | 0.87707 | -2392.4656 | 0.7303 | -2269.3298 | 0.69271 | 3248.7 | 0.99167 | 3192.5371 | 0.97452 | -2658.2951 | 0.81145 | -2521.4776 | 0.76968 | 3248.7 | 0.99167 | 3192.5371 | 0.97452 | -2658.2951 | 0.81145 | -2521.4776 | 0.76968
| 3252.1801 | 0.98194 | 3213.9898 | 0.97041 | -2694.8334 | 0.81366 | -2571.8524 | 0.77653 | 3613.5335 | 1.091 | 3571.0997 | 1.0782 | -2994.2593 | 0.90406 | -2857.6138 | 0.86281 | 3632.16 | 1.0967 | 3632.16 | 1.0967 | -3293.6852 | 0.99447 | -3137.9259 | 0.94744 | 2955.96 | 0.8925 | 2914.1726 | 0.87988 | -2413.3045 | 0.72865 | -2299.7998 | 0.69438 | 3284.4 | 0.99167 | 3237.9696 | 0.97765 | -2681.4495 | 0.80962 | -2555.3331 | 0.77154 | 3284.4 | 0.99167 | 3237.9696 | 0.97765 | -2681.4495 | 0.80962 | -2555.3331 | 0.77154
| 3290.6281 | 0.98286 | 3257.7411 | 0.97304 | -2718.3972 | 0.81195 | -2605.7189 | 0.77829 | 3656.2534 | 1.0921 | 3619.7124 | 1.0812 | -3020.4413 | 0.90216 | -2895.2433 | 0.86477 | 3671.64 | 1.0967 | 3671.64 | 1.0967 | -3322.4855 | 0.99238 | -3180.7424 | 0.95004 | 2988.09 | 0.8925 | 2955.2643 | 0.8827 | -2434.0249 | 0.72701 | -2330.39 | 0.69605 | 3320.1 | 0.99167 | 3283.627 | 0.98077 | -2704.4722 | 0.80779 | -2589.3222 | 0.77339 | 3320.1 | 0.99167 | 3283.627 | 0.98077 | -2704.4722 | 0.80779 | -2589.3222 | 0.77339
| 3329.1427 | 0.98379 | 3301.6821 | 0.97567 | -2741.8378 | 0.81024 | -2639.7126 | 0.78006 | 3699.0474 | 1.0931 | 3668.5357 | 1.0841 | -3046.4865 | 0.90026 | -2933.014 | 0.86673 | 3711.12 | 1.0967 | 3711.12 | 1.0967 | -3351.1351 | 0.99029 | -3223.7462 | 0.95264 | 3020.22 | 0.8925 | 2996.5585 | 0.88551 | -2454.6268 | 0.72536 | -2361.1005 | 0.69772 | 3355.8 | 0.99167 | 3329.5095 | 0.9839 | -2727.3632 | 0.80596 | -2623.445 | 0.77525 | 3355.8 | 0.99167 | 3329.5095 | 0.9839 | -2727.3632 | 0.80596 | -2623.445 | 0.77525
| 3367.7239 | 0.98471 | 3345.8127 | 0.97831 | -2765.1553 | 0.80852 | -2673.8334 | 0.78182 | 3741.9155 | 1.0941 | 3717.5696 | 1.087 | -3072.3948 | 0.89836 | -2970.926 | 0.86869 | 3750.6 | 1.0967 | 3750.6 | 1.0967 | -3379.6342 | 0.9882 | -3266.9372 | 0.95524 | 3052.35 | 0.8925 | 3038.0552 | 0.88832 | -2475.1102 | 0.72372 | -2391.9313 | 0.6994 | 3391.5 | 0.99167 | 3375.6169 | 0.98702 | -2750.1225 | 0.80413 | -2657.7014 | 0.77711 | 3391.5 | 0.99167 | 3375.6169 | 0.98702 | -2750.1225 | 0.80413 | -2657.7014 | 0.77711
| 3404.7533 | 0.98517 | 3387.0398 | 0.98005 | -2786.4993 | 0.80628 | -2712.6728 | 0.78492 | 3783.0592 | 1.0946 | 3763.3776 | 1.0889 | -3096.1104 | 0.89587 | -3014.0809 | 0.87213 | 3790.08 | 1.0967 | 3790.08 | 1.0967 | -3405.7214 | 0.98545 | -3315.489 | 0.95934 | 3084.48 | 0.8925 | 3072.9238 | 0.88916 | -2494.4305 | 0.72177 | -2427.1869 | 0.70231 | 3427.2 | 0.99167 | 3414.3598 | 0.98795 | -2771.5895 | 0.80196 | -2696.8744 | 0.78035 | 3427.2 | 0.99167 | 3414.3598 | 0.98795 | -2771.5895 | 0.80196 | -2696.8744 | 0.78035
| 3441.8156 | 0.98563 | 3428.3921 | 0.98178 | -2807.6816 | 0.80403 | -2751.735 | 0.78801 | 3824.2396 | 1.0951 | 3809.3246 | 1.0909 | -3119.6462 | 0.89337 | -3057.4833 | 0.87557 | 3829.56 | 1.0967 | 3829.56 | 1.0967 | -3431.6109 | 0.98271 | -3363.2316 | 0.96312 | 3116.61 | 0.8925 | 3107.8526 | 0.88999 | -2513.6105 | 0.71982 | -2462.6525 | 0.70523 | 3462.9 | 0.99167 | 3453.1695 | 0.98888 | -2792.9006 | 0.7998 | -2736.2806 | 0.78359 | 3462.9 | 0.99167 | 3453.1695 | 0.98888 | -2792.9006 | 0.7998 | -2736.2806 | 0.78359
| 3478.9108 | 0.98609 | 3469.8696 | 0.98352 | -2828.7022 | 0.80179 | -2791.0199 | 0.79111 | 3865.4565 | 1.0957 | 3855.4106 | 1.0928 | -3143.0024 | 0.89087 | -3101.1332 | 0.87901 | 3869.04 | 1.0967 | 3869.04 | 1.0967 | -3457.3027 | 0.97996 | -3411.2466 | 0.96691 | 3148.74 | 0.8925 | 3142.8415 | 0.89083 | -2532.6503 | 0.71787 | -2498.328 | 0.70814 | 3498.6 | 0.99167 | 3492.0461 | 0.98981 | -2814.0559 | 0.79763 | -2775.92 | 0.78683 | 3498.6 | 0.99167 | 3492.0461 | 0.98981 | -2814.0559 | 0.79763 | -2775.92 | 0.78683
| 3516.039 | 0.98654 | 3511.4722 | 0.98526 | -2849.561 | 0.79954 | -2830.5276 | 0.7942 | 3906.71 | 1.0962 | 3901.6358 | 1.0947 | -3166.1789 | 0.88838 | -3145.0307 | 0.88244 | 3908.52 | 1.0967 | 3908.52 | 1.0967 | -3482.7968 | 0.97722 | -3459.5338 | 0.97069 | 3180.87 | 0.8925 | 3177.8907 | 0.89166 | -2551.5497 | 0.71592 | -2534.2135 | 0.71106 | 3534.3 | 0.99167 | 3530.9896 | 0.99074 | -2835.0553 | 0.79547 | -2815.7928 | 0.79007 | 3534.3 | 0.99167 | 3530.9896 | 0.99074 | -2835.0553 | 0.79547 | -2815.7928 | 0.79007
| 3553.2 | 0.987 | 3553.2 | 0.987 | -2870.2582 | 0.79729 | -2870.2582 | 0.79729 | 3948 | 1.0967 | 3948 | 1.0967 | -3189.1757 | 0.88588 | -3189.1757 | 0.88588 | 3948 | 1.0967 | 3948 | 1.0967 | -3508.0933 | 0.97447 | -3508.0933 | 0.97447 | 3213 | 0.8925 | 3213 | 0.8925 | -2570.3089 | 0.71397 | -2570.3089 | 0.71397 | 3570 | 0.99167 | 3570 | 0.99167 | -2855.8988 | 0.79331 | -2855.8988 | 0.79331 | 3570 | 0.99167 | 3570 | 0.99167 | -2855.8988 | 0.79331 | -2855.8988 | 0.79331
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Category always has to be defined in the first column belonging to a new category. Every profile defined in this sheet must have a corresponging category assigned. This is used for the labelling of the output data generated by the test script.
Note on A4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: will only be used if profile type is "absolute" Reply: Used for SMA model as the voltage to be controlled at absolute Volt value
Note on A5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: will only be applied if profile type is "absolute"

## SteadyStateStudies
This sheet lists the contingency scenarios to be considered in Steady State studies. + CaseNr: name of the contingency scenarios; If left blank, the event occuring on that row is considered to be in the same scenario above it. + TestType: Contingency or Generation output changes *note: If generation output change test, the generation level before and after contingency must be provided in collumn Intitial and Final respectively. + Element: the element to which contingency is apply + i_bus, j_bus, k_bus, id: Connected buses and identification number of the element. If contingency element is a machine or a Shunt, the j_bus and k_bus are not needed. Similarly, k_bus is only used for three winding transformer contingency. + status: either 1 or 0: the element is activated or not
Run? | CaseNr | CaseRef | TestType | Element | i_bus | j_bus | k_bus | id | status | Initial | Final |  |  | path | [max_sfon,max_sfoff,min_sfon,min_sfoff]
0 | 1 | COFF_330 - LSM_330_id1 | Contingency | Line | 226893 | 250491 |  | 1 | 0 |  |  | Trip Line COFF_330 to LSM_330_id1 | Trip Line between Coffs Harbour 330kV and Lismore 330kV_id1
1 | 2 | 2GLENIN_132A - ARM_132_id1 | Contingency | Line | 235640 | 211640 |  | 1 | 0 |  |  | Trip Line 2GLENIN_132A to ARM_132_id1
0 | 3 | 2GLENIN_132A - 2TENTFD_132B_id1 | Contingency | Line | 235640 | 276041 |  | 1 | 0 |  |  | Trip Line 2GLENIN_132A to 2TENTFD_132B_id1
0 | 4 | 2TENTFD_132B - CASN_132_id1 | Contingency | Line | 276041 | 294840 |  | 1 | 0 |  |  | Trip Line 2TENTFD_132B to CASN_132_id1
0 | 5 | CASN_132 - LSM_132_id1 | Contingency | Line | 294840 | 250401 |  | 1 | 0 |  |  | Trip Line CASN_132 to LSM_132_id1
0 | 6 | MSF_132 - KOLK_132_id1 | Contingency | Line | 800000 | 245641 |  | 1 | 0 |  |  | Trip Line MSF_132 to KOLK_132_id1
0 | 7 | KOLK_132 - GRAF_132_id1 | Contingency | Line | 245641 | 236942 |  | 1 | 0 |  |  | Trip Line KOLK_132 to GRAF_132_id1
0 | 8 | LSM_132 - SUM_POC_DUM_id1 | Contingency | Line | 250401 | 800009 |  | 1 | 0 |  |  | Trip Line LSM_132 to SUM_POC_DUM_id1
0 | 9 | SUM_POC_DUM - KOLK_132_id1 | Contingency | Line | 800009 | 245641 |  | 1 | 0 |  |  | Trip Line SUM_POC_DUM to KOLK_132_id1
0 | 10 | LSM_330 - LSM_132_id1 | Contingency | Tx_2w | 250490 | 250401 |  | 1 | 0 |  |  | Trip Tx_2w LSM_330 to LSM_132_id1
0 | 11 | GenChange (100% to 75%) | GenChange | Machine | 9942 |  |  | 1 | 1 | 91 | 68.25 | GenChange - 90MW to 67.5MW(100% to 75%)
0 | 12 | GenChange (100% to 50%) | GenChange | Machine | 9942 |  |  | 1 | 1 | 91 | 45.5 | GenChange - 90MW to 45MW(100% to 50%)
0 | 13 | GenChange (100% to 25%) | GenChange | Machine | 9942 |  |  | 1 | 1 | 91 | 22.75 | GenChange - 90MW to 22.5MW(100% to 25%)
0 | 14 | GenChange (-100% to -75%) | GenChange | Machine | 9942 |  |  | 1 | 1 | -46 | -34.5 | GenChange - -90MW to -67.5MW(-100% to -75%)
0 | 15 | GenChange (-100% to -50%) | GenChange | Machine | 9942 |  |  | 1 | 1 | -46 | -23 | GenChange - -90MW to -45MW(-100% to -50%)
0 | 16 | GenChange (-100% to -25%) | GenChange | Machine | 9942 |  |  | 1 | 1 | -46 | -11.5 | GenChange - -90MW to -22.5MW(-100% to -25%)
0 | 17 | GenTrip (100% to 0%) | GenTrip | Machine | 9942 |  |  | 1 | 1 | 91 | 0 | GenTrip - 90MW to 0MW (100% to 0%)
0 |  |  |  | Shunt | 9940 |  |  | 1 | 1 |  | 0
0 |  |  |  | Shunt | 9940 |  |  | 2 | 1 |  | 0
0 | 18 | GenTrip (75% to 0%) | GenTrip | Machine | 9942 |  |  | 1 | 1 | 68.25 | 0 | GenTrip - 67.5MW to 0MW (75% to 0%)
0 |  |  |  | Shunt | 9940 |  |  | 1 | 1 |  | 0
0 |  |  |  | Shunt | 9940 |  |  | 2 | 1 |  | 0
0 | 19 | GenTrip (50% to 0%) | GenTrip | Machine | 9942 |  |  | 1 | 1 | 45.5 | 0 | GenTrip - 45MW to 0MW (50% to 0%)
0 |  |  |  | Shunt | 9940 |  |  | 1 | 1 |  | 0
0 |  |  |  | Shunt | 9940 |  |  | 2 | 1 |  | 0
0 | 20 | GenTrip (25% to 0%) | GenTrip | Machine | 9942 |  |  | 1 | 1 | 22.75 | 0 | GenTrip - 22.5MW to 0MW (25% to 0%)
0 |  |  |  | Shunt | 9940 |  |  | 1 | 1 |  | 0
0 |  |  |  | Shunt | 9940 |  |  | 2 | 1 |  | 0
0 | 21 | GenTrip (-100% to 0%) | GenTrip | Machine | 9942 |  |  | 1 | 1 | -46 | 0 | GenTrip - -90MW to 0MW (-100% to 0%)
0 |  |  |  | Shunt | 9940 |  |  | 1 | 1 |  | 0
0 |  |  |  | Shunt | 9940 |  |  | 2 | 1 |  | 0
0 | 22 | GenTrip (50% to 0%) | GenTrip | Machine | 9942 |  |  | 1 | 1 | -23 | 0 | GenTrip - -45MW to 0MW (50% to 0%)
0 |  |  |  | Shunt | 9940 |  |  | 1 | 1 |  | 0
0 |  |  |  | Shunt | 9940 |  |  | 2 | 1 |  | 0
0 | 23 | GenChange Machine SUM_LV_PV_id1 | GenChange | Machine | 9942 |  |  | 1 | 1 | 45 | 22.5
0 | 24 | GenChange Machine SUM_LV_BESS_id1 | GenChange | Machine | 9944 |  |  | 1 | 1 | 45 | 22.5
0 | 25 | GenTrip Machine SUM_LV_PV_id1 | GenTrip | Machine | 9942 |  |  | 1 | 1
0 |  | GenTrip Machine SUM_LV_BESS_id1 | GenTrip | Machine | 9944 |  |  | 1 | 1
0 |  | Contingency Shunt SUM_MV_id1 | Contingency | Shunt | 9940 |  |  | 1 | 0
0 |  | Contingency Shunt SUM_MV_id2 | Contingency | Shunt | 9940 |  |  | 2 | 0
0 | 26 | SUMSF_high_genon.sav | Fault | Bus | 9910
0 |  |  |  | Bus | 9920
0 |  |  |  | Bus | 9930
0 |  |  |  | Bus | 9940
0 |  |  |  | Bus | 9941
0 |  |  |  | Bus | 9942
0 |  |  |  | Bus | 9943
0 |  |  |  | Bus | 9944
Note on B2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Consecutive cases. leave empty if it belong to / associated with previous contingency case
Note on E2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: if Element is a Machine, shunt or Bus, then J_bus = empty
Note on K2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: dedicated for generation output before contingency occurs
Note on L2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: dedicated for generation output after contingency occurs
Note on B6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Added as with bus 294840 in middle
Note on B7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not avaible as with bus 294840 in middle
Note on B8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: added contingency - nearby network
Note on B9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: added contingency - nearby network
Note on B10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: added contingency - nearby network
Note on B11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: added contingency - nearby network
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: added contingency - nearby network

## TestTypes
layers (optional) | Layer 1 | Layer 2
Test Type
Steady_State | 0 | 1
F_profile | 0 | 1
ANG_profile | 0 | 1
V_profile | 0 | 1
V_stp_profile | 0 | 1
Q_stp_profile | 0 | 1
PF_stp_profile | 0 | 1
P_stp_profile | 0 | 0
ORT | 0 | 0
Fault | 4 | 0
Fault_TOV | 0 | 0
Multifault_random | 0 | 1
Multifault | 0 | 1
P_prim_lim_profile | 0 | 0
Auxiliary_profile | 0 | 0
Note on A5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Angle change profile is defined as a step profile and not as a linear interpolated profile. The reason is that the profile cannot be programmes into a test source but rather needs to be written vie the PSS/E API. A step profile limits the number or changes that need to be made during runtime.
Note on A11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Oscillatory rejection test
Note on A12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: inductive or ohmic fault, different types. to be specified by residual voltage at POC+X/R or resistance+reactcance or Impedance+X/R ratio.
Note on A13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: capacitive fault to increase voltage

## Bus Lib
Num | Bus_num_PSSE | Bus_name_PSSE | Bus_name_full | Bus_name_PSSE | Bus_name_full
1 | 0 | N/A | N/A | 2LSMORE_330A | Lismore 330kV_A
1 | 250490 | LSM_330 | Lismore 330kV_A | 2LISMOR_132A | Lismore 132kV_2
2 | 250040 | LSM_132_B | Lismore 132kV_2 | 2_COFFS_132D | Coffs Harbour 132kV
3 | 226843 | COFF_132 | Coffs Harbour 132kV | 2GRAFTN_132C | Graffton East 132kV
4 | 236942 | GRAF_132 | Graffton East 132kV | 2KOLKHN_132B | Koolkhan 132kV
5 | 245641 | KOLK_132 | Koolkhan 132kV | 2KOLKHN__66B | Koolkhan 66kV
6 | 245631 | 2KOLKHN__66B | Koolkhan 66kV | 2MULUMB__DC2 | 2MULUMB__DC2
7 | 258402 | 2MULUMB__DC2 | 2MULUMB__DC2 | 2MULUMB__DC3 | 2MULUMB__DC3
8 | 258403 | 2MULUMB__DC3 | 2MULUMB__DC3 | 2DUNOON_132A | 2DUNOON_132A
9 | 232040 | 2DUNOON_132A | 2DUNOON_132A | 2CASN_T_132A | Casino 132kV
10 | 294840 | CASN_132 | Casino 132kV | 2BAYSWT_500A | Bayswater 500kV
11 | 215290 | 2BAYSWT_500A | Bayswater 500kV | 2WOLLAR_500A | Wollar 500kV
12 | 288090 | 2WOLLAR_500A | Wollar 500kV | 2MTPIPR_500A | Mt Piper 500kV
13 | 257690 | 2MTPIPR_500A | Mt Piper 500kV | 2TAMWTH_330A | Tamworth 330kV
14 | 275290 | 2TAMWTH_330A | Tamworth 330kV | 2TAMWTH_330B | Tamworth 330kV
15 | 275291 | 2TAMWTH_330B | Tamworth 330kV | 2TAMWTH_330C | Tamworth 330kV
16 | 275292 | 2TAMWTH_330C | Tamworth 330kV | 2ARMIDL_330A | Armidale 330kV
17 | 211690 | 2ARMIDL_330A | Armidale 330kV | 2ARMIDL_330B | Armidale 330kV
18 | 211691 | 2ARMIDL_330B | Armidale 330kV | 2ARMIDL_330C | Armidale 330kV
19 | 211692 | 2ARMIDL_330C | Armidale 330kV | 2ARMIDL_330D | Armidale 330kV
20 | 211693 | 2ARMIDL_330D | Armidale 330kV | 2ARMIDL_330E | Armidale 330kV
21 | 211694 | 2ARMIDL_330E | Armidale 330kV | 2DUMARQ_330A | Dumaresq 330kV
22 | 231690 | 2DUMARQ_330A | Dumaresq 330kV | 2DUMARQ_330B | Dumaresq 330kV
23 | 231691 | 2DUMARQ_330B | Dumaresq 330kV | 2DUMARQ_330C | Dumaresq 330kV
24 | 231692 | 2DUMARQ_330C | Dumaresq 330kV | 2DUMARQ_330D | Dumaresq 330kV
25 | 231693 | 2DUMARQ_330D | Dumaresq 330kV | 2DUMARQ_330E | Dumaresq 330kV
26 | 231694 | 2DUMARQ_330E | Dumaresq 330kV | 2MUSWLB_330A | Muswellbrook 330kV
27 | 260890 | 2MUSWLB_330A | Muswellbrook 330kV | 2_COFFS_330D | Coffs Harbour 330kV
28 | 226893 | COFF_330 | Coffs Harbour 330kV | 2LIDDEL_330A | Liddell 330kV
29 | 249290 | 2LIDDEL_330A | Liddell 330kV | 2SAPHIR_330A | Sapphire WF 330kV
30 | 270390 | 2SAPHIR_330A | Sapphire WF 330kV | 2LSMORE_330B | Lismore 330kV
31 | 250491 | LSM_330 | Lismore 330kV | 2TAMWTH_132A | Tamworth 132kV
32 | 275240 | 2TAMWTH_132A | Tamworth 132kV | 2GUNDAH_132B | Gunnedah 132kV
33 | 238441 | 2GUNDAH_132B | Gunnedah 132kV | 2NARABR_132A | Narrabri 132kV
34 | 261640 | 2NARABR_132A | Narrabri 132kV | 2BOGABR_132G | Boggabri East 132kV
35 | 209446 | 2BOGABR_132G | Boggabri East 132kV | 2BGNBRY_132A | Boggabri North 132kV
36 | 218640 | 2BGNBRY_132A | Boggabri North 132kV | 2NARABR_132A | Narrabri 132kV
37 | 261640 | 2NARABR_132A | Narrabri 132kV | 2_MOREE_132A | Moree 132kV
38 | 257240 | 2_MOREE_132A | Moree 132kV | 2INVERL_132A | Inverell 132kV
39 | 242040 | 2INVERL_132A | Inverell 132kV | 2WHITER_132A | White Rock 132kV
40 | 287040 | 2WHITER_132A | White Rock 132kV | 2GLENIN_132A | Glen Innes 132kV
41 | 235640 | 2GLENIN_132A | Glen Innes 132kV | 2ARMIDL_132A | Armidale 132kV
42 | 211640 | ARM_132 | Armidale 132kV | 2TENTFD_132B | Tenterfield 132kV
43 | 276041 | 2TENTFD_132B | Tenterfield 132kV | 2LSMORE___S1 | Lismore 132kV
44 | 250401 | LSM_132 | Lismore 132kV | Metz_SF_POC | Metz SF POC
45 | 800000 | MSF_132 | Metz SF POC | Gunnedah_SF_POC | Gunnedah SF POC
46 | 800001 | Gunnedah_SF_POC | Gunnedah SF POC | New_England_SF_POC | New England SF POC
47 | 800002 | New_England_SF_POC | New England SF POC | Tamworth_SF_POC | Tamworth SF POC
48 | 800003 | Tamworth_SF_POC | Tamworth SF POC | 2GUN_BO_132A | Gunnedah East
49 | 238740 | 2GUN_BO_132A | Gunnedah East | 2CASN_T_132A | Casino 132kV
50 | 294840 | 2CASN_T_132A | Casino 132kV | Summerville_SF_132kV | Summerville SF 132kV
51 | 800009 | SUM_POC_DUM | SUMSF DM 132kV | SUM_POC_to | SUM_POC_to
52 | 9910 | SUM_POC | SUM_POC 132kV | SUM_POC_from | SUM_POC_from
53 | 9920 | SUM_POC_from | SUM_POC_from | SUM_HV | SUM_HV
54 | 9930 | SUM_HV | SUM_HV | SUM_MV | SUM_MV
55 | 9940 | SUM_MV | SUM_MV | SUM_MV_PV | SUM_MV_PV
56 | 9941 | SUM_MV_PV | SUM_MV_PV | SUM_LV_PV | SUM_LV_PV
57 | 9942 | SUM_LV_PV | SUM_LV_PV | SUM_MV_BESS | SUM_MV_BESS
58 | 9943 | SUM_MV_BESS | SUM_MV_BESS | SUM_LV_BESS | SUM_LV_BESS
59 | 9944 | SUM_LV_BESS | SUM_LV_BESS
| 2200 | GUNSF_POC | GUNSF_POC
| 2300 | GUNSF_MV2 | GUNSF_MV2
| 2400 | GUNSF_MV1 | GUNSF_MV1
| 2500 | GUNSF_GEN | GUNSF_GEN
| 106 | TAMSF_POC | TAMSF_POC
| 105 | TAMSF_BUS1 | TAMSF_BUS1
| 103 | TAMSF_BUS2 | TAMSF_BUS2
| 1031 | TAMSF_BUS3 | TAMSF_BUS3
| 1032 | TAMSF_BUS4 | TAMSF_BUS4
| 102 | TAMSF_BUS5 | TAMSF_BUS5
| 101 | TAMSF_BUS6 | TAMSF_BUS6
| 100 | TAMSF_GEN | TAMSF_GEN
| 249201 | LID_GEN1 | LID_GEN1
| 101502 | MSF_132 | Metz SF POC
Note on B75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Only for LL

## MonitorBuses
bus_number | bus_name | bus_code
250490 | LSM_330 | Lismore 330kV_A | LSM_330 = 250490 # Lismore 330kV_A | LSM_330 = 250490 # Lismore 330kV_A
226893 | COFF_330 | Coffs Harbour 330kV | COFF_330 = 226893 # Coffs Harbour 330kV | COFF_330 = 226893 # Coffs Harbour 330kV
250401 | LSM_132 | Lismore 132kV | LSM_132 = 250401 # Lismore 132kV | LSM_132 = 250401 # Lismore 132kV
245641 | KOLK_132 | Koolkhan 132kV | KOLK_132 = 245641 # Koolkhan 132kV | KOLK_132 = 245641 # Koolkhan 132kV
226843 | COFF_132 | Coffs Harbour 132kV | COFF_132 = 226843 # Coffs Harbour 132kV | COFF_132 = 226843 # Coffs Harbour 132kV
250040 | LSM_132_B | Lismore 132kV_2 | LSM_132_B = 250040 # Lismore 132kV_2 | LSM_132_B = 250040 # Lismore 132kV_2
294840 | CASN_132 | Casino 132kV | CASN_132 = 294840 # Casino 132kV | CASN_132 = 294840 # Casino 132kV
211640 | ARM_132 | Armidale 132kV | ARM_132 = 211640 # Armidale 132kV | ARM_132 = 211640 # Armidale 132kV
800009 | SUM_POC_DUM | SUMSF DM 132kV | SUM_POC_DUM = 800009 # SUMSF DM 132kV | SUM_POC_DUM = 800009 # SUMSF DM 132kV
9910 | SUM_POC | SUM_POC 132kV | SUM_POC = 9910 # SUM_POC 132kV | SUM_POC = 9910 # SUM_POC 132kV

## MonitorBranches
brch_from | brch_to | brch_id | brch_name | brch_code | brch_name | brch_code | brch_name
250491 | 226893 | 1 | LSM_330 - COFF_330 | LSM_330 - COFF_330 | LSM_330 - COFF_330 | Lismore 330kV - Coffs Harbour 330kV | 89-0
250490 | 250401 | 1 | LSM_330 - LSM_132 | LSM_330 - LSM_132 | LSM_330 - LSM_132 | Lismore 330kV_A - Lismore 132kV | LISMORE_1H
250490 | 250401 | 2 | LSM_330 - LSM_132 | LSM_330 - LSM_132 | LSM_330 - LSM_132 | Lismore 330kV_A - Lismore 132kV | LISMORE_2H
250401 | 250040 | 1 | LSM_132 - LSM_132_B | LSM_132 - LSM_132_B | LSM_132 - LSM_132_B | Lismore 132kV - Lismore 132kV_2 | 9U8-0
250401 | 250040 | 2 | LSM_132 - LSM_132_B | LSM_132 - LSM_132_B | LSM_132 - LSM_132_B | Lismore 132kV - Lismore 132kV_2 | 9U9-0
250401 | 250040 | 3 | LSM_132 - LSM_132_B | LSM_132 - LSM_132_B | LSM_132 - LSM_132_B | Lismore 132kV - Lismore 132kV_2 | 9W1-0
250401 | 294840 | 1 | LSM_132 - CASN_132 | LSM_132 - CASN_132 | LSM_132 - CASN_132 | Lismore 132kV - Casino 132kV | 96L/2-0
800000 | 245641 | 1 | MSF_132 - KOLK_132 | MSF_132 - KOLK_132 | MSF_132 - KOLK_132 | Metz SF POC - Koolkhan 132kV | 966-0
245641 | 236942 | 1 | KOLK_132 - GRAF_132 | KOLK_132 - GRAF_132 | KOLK_132 - GRAF_132 | Koolkhan 132kV - Graffton East 132kV | 9W0-0
800009 | 250401 | 1 | SUM_POC_DUM - LSM_132 | SUM_POC_DUM - LSM_132 | SUM_POC_DUM - LSM_132 | SUMSF DM 132kV - Lismore 132kV | 967-1
800009 | 245641 | 1 | SUM_POC_DUM - KOLK_132 | SUM_POC_DUM - KOLK_132 | SUM_POC_DUM - KOLK_132 | SUMSF DM 132kV - Koolkhan 132kV | 967-0