## ChangeLog
# | Date | Change | Description
1 | 2022-03-23 | Adop from Summerville Project | Original version for Lancaster SF
2 | 2023-01-04 | Update to version 0a | Update the setpoint sequence: for each SCR/XR numbers, provide Q0, Q0.3 and Q0.395
Update the PSCAD v5 input
3 | 2023-03-10 | Update to version 1 | Include more setpoints in the Setpoints Tab

## ProjectDetails
HighLevelParamName | ParamIdentifier | Value
Project Name | Name | Horsham Solar Farm and BESS
Project Name short | NameShrt | HSFBESS
Developer | Dev | OX2 Australia
Abbreviation | Abbr
Type of Test | Type
Town | Town | Horsham
State | State | Victoria
Lot/DP | lot_dp | TBC
Address | addrs | TBC
LGA | lga | TBC
Network Service Provider | NSP | Ausnet
POC Substation | Sub | Horsham Terminal Station
Connection type | contyp | Direct connection into the Horsham Terminal Station
POC Feeder | poc_fdr | N/A
POC circuit | CCT | N/A
Short Circuit Ratios | SCRHigh | 1109
| SCRLow | 483
| SCRMVA | 90
Total Plant MW at POC | PlantMW | 119
Total Plant MW at terminals | GenMW | 121
Maximum Plant MVAr at terminals | GenMVArMax | 90.72
Minimum Plant MVAr at terminal | GenMVArMin | -90.72
Total Plant Maximum MVA at POC (base for per-unitisation) | TotalMVA | 119
Nominal POC voltage (kV) | VPOCkv | 220 | VLL | VLN
Normal POC voltage (p.u.) | VPOCpu | 1.02 | 224.4 | 129.5574
Nominal voltage at Bus where test source is connected (optional) | VbaseTestSrc | 132
Normal frequency at POC | Fbase | 50
Inverter/Plant Model | plnt_mdl
Number of generator aggregates in model | Gens | 2
Generators Per Site | genPerSite1 | 36
| genPerSite2 | 40
Generator MVA | genMVA1 | 4.2
| genMVA2 | 3.6
Generator terminal voltage in kV | VTERkv | 0.63
| VTERkv2 | 0.63
Pmax | Pmax | 1
Pmax_at_Qmax | PmaxQmax | 1
Pmax_at_Qmin | PmaxQmin | 1
Pmin | Pmin | 0
Pmin_at_Qmax | PminQmax | 0
Pmin_at_Qmin | PminQmin | 0
Note on C22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Prated
Note on B26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Lancaster, the Qmax for half of SF only
Note on B31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is in case the GridSource for automated testing is connected at a different point than the POC. If this entry is left empty, VPOCpu is assumed.

## SimulationSettings
ParamIdentifier | Value | unit
Batches | test1
Name of test run | script_upgrade
model(s) for PSSE network studies | LowLoad_genon | folder name and path relative to relative to PSSE_sim\base_model | HighLoad, LowLoad
PSSE start offset | 0 | seconds
default_sim_duration PSSE | 15
default_sim_duration PSCAD | 15
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: define which test batches should be included in next test run
Note on A3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: name of test run used for labelling the output files
Note on A4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: list of folder names of one or more network cases, used in Network fault studies and voltge control studies carried out on the wider network in PSS/E.
Note on A5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: provide a negative number to delay the PSSE simulation [second]

## ModelDetailsPSCAD
ParamIdentifier | Value
workspace_folder_path |  |  | This sheet lists all relevant information about the project file and PSCAD-specific setup
workspace_folder_name |  |  |  | Variable
Workspace File Name | Workspace_HSFBESS.pswx |  | 1a. Setpoint to PPC |  | Description | Note
Projects | 1 |  |  | PoiWLimSales | Active power sales limit POI | Active Power setpoint atPOC
Project1 | HSFBESS_V1 |  |  | BessWSpt | P setpoint Bess | Active Power setpoint from BESS (at BESS terminal?)
DllPath |  |  |  | PoiVArSpt | Q setpoint Poi | Reactive power setpoint POC
|  |  |  | PoiPfSpt | PF setpoint Poi | Power Factor setpoint POC
result_path |  |  |  | PoiVolSpt | V setpoint | Voltage setpoint POC
|  |  |  | 50 | freq setpoint | Frequency setpoint
default_sim_duration | 15
disturbance_offset | 5 |  | 1b. Measurement feedback to POC
POC P, Q, V, F,
max_processes | 8 |  |  | McbStt
GcbStt
pscad version | PSCAD 5.0.1 (x64) | PSCAD 4.6.2 (x64) |  | Vrms_abc_POI
compiler | Intel Fortran v2021 | Intel Fortran v2015
compiler_short | if18_x86 |  |  | P, Q, V, H from PV and BESS
create example cases | no
1c. Feed back from INV
GridSourceID | 1927070795 |  |  | PCU1_Fb_SI |  | Include feedback at INV terminal and number of INV scalled
GridSourceCanvas (optional) |  |  |  | PCU2_Fb_SI |  | Include feedback at INV terminal and number of INV scalled
Fprofile | 270230556
Vprofile | 976319064
PHprofile | 1827520263 |  | 2a command (spnt) from PPC to PV INV
StpBlockID | 163769877 |  |  | WSpt_pu_SC | P cmd
StpBlockCanvas (optional) |  |  |  | VArSpt_pu_SC | Q cmd
Vstp_profile | 626637343 |  |  | Fsys_
Qstp_profile | 47901822 |  |  | WSptMin_pu_SCDC
Q1stp_profile | 2052650100 |  |  | HybridPwrAtDisSpntTot_pu_SC
PFstp_profile | 1775954593 |  |  | HybridPwrAtChrSpntTot_pu_SC
PF1stp_profile | 1066702073
Pstp_profile | 305157189 |  | 2b command (spnt) from PPC to BESS INV
P1stp_profile | 2104320057 |  |  | WSpt_pu_SCS | P cmd
AUX_profile | 935825497 |  |  | VArSpt_pu_SCS | Q cmd
FaultBlockID | 1591544161 |  |  | VtgNomSpntPc |  | Channel 4
FaultBlockCanvas (optional) |  |  |  | Fsys_
SCSOpCmd
plotStep_us | 5000
3 PPC Debug signals
4a. INV input
WSpt (pu)
VArSpt (pu)
PFSpt
VolSpt (pu)
HzSpt (Hz)
4b. INV fb
WRtg (kW)
VARtg (kVAr)
Waval (kW)
Qaval (kVAr)
InvMs_TotW (kW)
InvMs_TotVAr (kVAr)
WMs_DC_PV (kW)
WMs_DC_Bat (kW)
Note on B7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: contains the path to the dll files that must be copied to the directory containing the compiled files. Expressed relative to the "PSCAD_sim" directory.
Note on B18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This one needs to reflect the ending of the folders auto-created by PSCAD during compilation
Note on A19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: determines wether the test script generates an example case for each test. This can be handy for debugging or sharing the cases with third parties. However, it also takes up disk space.
Note on A23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Inside the GridSourceCanvas
Note on A28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This normally remain the same with StpBlockID for the tests.

## ModelDetailsPSSE
ParamIdentifier | Value
PSSEversion | PSS/E v34.5
savFileName | HSFBESS_SMIB_V1.sav
dyrFileName | HSFBESS_SMIB_V1.dyr
dll1 | SMAHYCF_G20_344_IVF150.dll
dll2 | SMAGF_G303_344_IVF150.dll
dll3 | SMASC_G190_344_IVF150.dll
PPC_model | SMAHYCF20
INV1_model | SMASC190
INV2_model | SMAGF303
STAT_model
default_sim_duration | 15
start_offset | 0
InfiniteBus | 10000
DummyTxBus | 10
FaultBus | 334081
POC | 334081
POC_to | 334090
Generator1 | 334094
Generator2 | 334095
POCfromBus1 | 334081 |  | 9920
POCtoBus1 | 334090 |  | 9910
POCmeasBus1 | 334081 |  | 9920
HVfromBus1 | 10 |  | 10
HVtoBus1 | 10000 | INF bus | 9900
HVmeasBus1 | 10 | DummyTxBus | 10
MVfromBus1 | 334092 |  | 9941
MVtoBus1 | 334091 |  | 9940
MVmeasBus1 | 334092 |  | 9941
LVfromBus1 | 334094 |  | 9942
LVtoBus1 | 334092 |  | 9941
LVmeasBus1 | 334094 |  | 9942
MVfromBus2 | 334093
MVtoBus2 | 334091
MVmeasBus2 | 334093
LVfromBus2 | 334095
LVtoBus2 | 334093
LVmeasBus2 | 334095
Vset1_bus | 334081
Vset1_mac | 1
Vset1_var | 16
Vset1_model | SMAHYCF20
Vset1_type | OTHER
Pset1_bus | 334081
Pset1_mac | 1
Pset1_var | 18
Pset1_model | SMAHYCF20
Pset1_type | OTHER
Pprim1_bus | 334094
Pprim1_mac | 1
Pprim1_con | 0
Pprim1_model | SMASC190
Pprim1_type | GEN
Qset1_bus | 334081
Qset1_mac | 1
Qset1_var | 14
Qset1_model | SMAHYCF19
Qset1_type | OTHER
PFset1_bus | 334081
PFset1_mac | 1
PFset1_var | 15
PFset1_model | SMAHYCF20
PFset1_type | OTHER
Output/Plot Channels
Name | tobus | item | label
Note on A15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: start_offset is to delay the start of Dynamic simulation in PSSE compared to PSCAD
Note on A17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This has been fixed to 1 in run_simulation script - line805
Note on A18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is dummy bus inserted for including a dummy transformer for Vangle testing purposes DUM_TR_POC (default value: 10 line 483 in run_simulation script)
Note on A19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This has been fixed to 2 in run_simulation script - line805
Note on A20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: POC bus
Note on A21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: POC_to bus: back to the SF side
Note on A25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The numbering of these must match the Generator numbers
Note on C25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: by default the voltages and angles will alwaye be read at the toBus. But for example for the LV it may be preferred to read at the fromBus.
Note on A44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: for the setpoints common ways are adjusting variables or writing to VREF
Note on A46: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This should be "_con" or "_var" depending on the specific OEM model
Note on A50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Active Power setpoint to HyCon
Note on A74: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Active Power setpoint to HyCon

## OutputChannels
Description: list all the variables to be output during simulations
ChanNum | Location | Model | Type | Position | Name | Legend | BusNum | ID
1 | PPC_model | SMAHYCF20 | VAR | 13 | PREF_BESS | BESS_W_Spt | - | -
2 | PPC_model | SMAHYCF20 | VAR | 14 | QREF_POC | POI_Var_Spt | - | -
3 | PPC_model | SMAHYCF20 | VAR | 15 | PFREF | POI_PF_Spt | - | -
4 | PPC_model | SMAHYCF20 | VAR | 16 | VREF_POC | POI_Vol_Spt | - | -
5 | PPC_model | SMAHYCF20 | VAR | 17 | HZREF_POC | POI_Hz_Spt | - | -
6 | PPC_model | SMAHYCF20 | VAR | 18 | PREF_POC | PwrAtLimSales | - | -
7 | PPC_model | SMAHYCF20 | VAR | 1 | VOLT_RB | VOLT_RB | - | -
8 | PPC_model | SMAHYCF20 | VAR | 2 | P_PCC | P_PCC | - | -
9 | PPC_model | SMAHYCF20 | VAR | 3 | Q_PCC | Q_PCC | - | -
10 | PPC_model | SMAHYCF20 | VAR | 4 | S_PCC | S_PCC | - | -
11 | PPC_model | SMAHYCF20 | VAR | 56 | P_CMD_PV | P_CMD_PV | - | -
12 | PPC_model | SMAHYCF20 | VAR | 57 | Q_CMD_PV | Q_CMD_PV | - | -
13 | PPC_model | SMAHYCF20 | VAR | 58 | P_CMD_BESS | P_CMD_BESS | - | -
14 | PPC_model | SMAHYCF20 | VAR | 59 | Q_CMD_BESS | Q_CMD_BESS | - | -
15 | PPC_model | SMAHYCF20 | VAR | 75 | FRTACTIVE | FRTACTIVE | - | -
16 | PPC_model | SMAHYCF20 | VAR | 76 | FRT_EXITTM | FRT_EXITTM | - | -
17 | INV1_model | SMASC190 | VAR | 102 | INV1_FRT_FLAG | INV1_FRT_FLAG | - | -
18 | INV1_model | SMASC190 | VAR | 163 | INV1_FRT_STATE | INV1_FRT_STATE | - | -
19 | INV1_model | SMASC190 | VAR | 186 | INV1_LVRT | INV1_LVRT | - | -
20 | INV1_model | SMASC190 | VAR | 187 | INV1_HVRT | INV1_HVRT | - | -
21 | INV1_model | SMASC190 | VAR | 9 | INV1_IQ_COMMAND | INV1_IQ_COMMAND | - | -
22 | INV1_model | SMASC190 | VAR | 40 | INV1_IP_COMMAND | INV1_IP_COMMAND | - | -
23 | INV1_model | SMASC190 | VAR | 174 | INV1_P_COMMAND | INV1_P_COMMAND | - | -
24 | INV1_model | SMASC190 | VAR | 175 | INV1_Q_COMMAND | INV1_Q_COMMAND | - | -
25 | INV2_model | SMAGF303 | VAR | 200 | INV2_Frequency | INV2_Frequency | - | -
26 | INV2_model | SMAGF303 | VAR | 82 | INV2_Vd | INV2_Vd | - | -
27 | INV2_model | SMAGF303 | VAR | 83 | INV2_Vq | INV2_Vq | - | -
28 | INV2_model | SMAGF303 | VAR | 86 | INV2_Id | INV2_Id | - | -
29 | INV2_model | SMAGF303 | VAR | 87 | INV2_Iq | INV2_Iq | - | -
30 | INV2_model | SMAGF303 | VAR | 16 | INV2_FRT_FLAG | INV2_FRT_FLAG | - | -
31 | INV2_model | SMAGF303 | VAR | 79 | INV2_ANGLE | INV2_ANGLE | - | -
32 | INV2_model | SMAGF303 | VAR | 17 | VI_X | VI_X | - | -
33 | INV2_model | SMAGF303 | VAR | 18 | VI_R | VI_R | - | -
34 | INV2_model | MachineArray | VAR | 9 | ECOMP | Real component of current in p.u. | 334095 | 1
35 | INV2_model | MachineArray | VAR | 12 | VUEL | Imaginary component of current in p.u. | 334095 | 1
Note on B2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dynamic model - to be consistent with the model specified in ModelDetailsPSSE
Note on D2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: VAR/STATE/CON/ICON
Note on E2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From DYR file. E.g L+10
Note on F2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Provide a name for the variable to be exported
Note on G2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Description of the variable to be exported
Note on H2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: If model is MachineArray (variable comes from a machine array) then need a BusNum and ID of the generator

## LargeDist
Description: For every fault, specify the impedance in Ohms and the X/R ratio. For 3-phase faults, a residual voltage can be set, instead of the fault impedance and X/R. In that case, the fault impedance will be calculated so that the voltage initially dips to the value specified under 'Vresidual'. It is important that Vpoc and SCR as well as X/R are correctly defined for this to work. If both an impedance and 'Vresidual' are defined, only the impedance value is used in the simulation. For Multifault-sequences there are two option: 1) define define the first fault as a regular fault, subsequently define all other faults of the Multifault sequence for any fault belonging to the series, do not set caseID, it will then be interpreted as belonging to the multifaul sequence. 2) select one of the pre-defined multifault sequences under "fault type". The other fault parameters (impedance, fault X_R, residual voltage, and duration will then be ignored). The "Ftime" will be interpreted as the start time of the multifault sequence.
608
38
PSSE-specific settings
CaseNr | Test Type | Ftype | Ftime | Fduration | F_Impedance | Vresidual | Fault X_R | Vpoc | Active Power | Reactive Power | SCR | X_R | SCL_post | X_R_post | setpoint ID | init_help | TimeStep | AccFactor | run in PSCAD? | run in PSS/E? | Comment/Corresponding DMAT case | test group | simulation batch
1 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 51 | 0 | 1 | 0.2 | no | no | 1 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
2 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 2 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
3 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 3 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
4 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 4 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
5 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 5 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
6 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 6 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
7 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 1 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
8 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 2 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
9 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 3 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
10 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 4 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
11 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 5 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
12 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 6 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
13 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 56 | 0 | 1 | 0.2 | no | no | 7 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
14 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 8 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
15 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 9 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
16 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 10 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
17 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 11 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
18 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 12 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
19 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 7 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
20 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 8 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
21 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 9 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
22 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 10 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
23 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 11 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
24 | Fault | 3PHG | 5 | 0.43 | 0 |  | 3 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 12 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
25 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 51 | 0 | 1 | 0.2 | no | no | 13 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
26 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 14 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
27 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 15 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
28 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 16 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
29 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 17 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
30 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 18 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
31 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 13 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
32 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 14 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
33 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 15 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
34 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 16 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
35 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 17 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
36 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 18 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
37 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 56 | 0 | 1 | 0.2 | no | no | 19 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
38 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 20 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
39 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 21 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
40 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 22 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
41 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 23 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
42 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 24 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
43 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 19 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
44 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 20 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
45 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 21 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
46 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 22 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
47 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 23 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
48 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 24 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
49 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 51 | 0 | 1 | 0.2 | no | no | 25 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
50 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 26 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
51 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 27 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
52 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 28 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
53 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 29 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
54 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 30 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
55 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 25 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
56 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 26 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
57 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 27 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
58 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 28 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
59 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 29 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
60 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 30 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
61 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 56 | 0 | 1 | 0.2 | no | no | 31 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
62 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 32 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
63 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 33 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
64 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 34 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
65 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 35 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
66 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 36 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
67 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 31 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
68 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 32 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
69 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 33 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
70 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 34 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
71 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 35 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
72 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 36 | Balanced fault – large disturbance test cases [PSS®E and PSCAD/EMTDC models] | DMAT
73 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 51 | 0 | 1 | 0.2 | yes | no | 37 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
74 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 38 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
75 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 39 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
76 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 40 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
77 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 41 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
78 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 42 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
79 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | no | 37 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
80 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 38 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
81 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 39 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
82 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 40 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
83 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 41 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
84 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 42 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
85 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 56 | 0 | 1 | 0.2 | yes | no | 43 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
86 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 44 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
87 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 45 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
88 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 46 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
89 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 47 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
90 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 48 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
91 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | yes | no | 43 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
92 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 44 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
93 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 45 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
94 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 46 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
95 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 47 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
96 | Fault | 2PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 48 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
97 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 51 | 0 | 1 | 0.2 | yes | no | 49 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
98 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 50 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
99 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 51 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
100 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 52 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
101 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 53 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
102 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 54 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
103 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | no | 49 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
104 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 50 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
105 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 51 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
106 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 52 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
107 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 53 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
108 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 54 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
109 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 56 | 0 | 1 | 0.2 | yes | no | 55 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
110 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 56 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
111 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 57 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
112 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 58 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
113 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 59 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
114 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 60 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
115 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | yes | no | 55 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
116 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 56 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
117 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 57 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
118 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 58 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
119 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 59 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
120 | Fault | 2PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 60 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
121 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 51 | 0 | 1 | 0.2 | yes | no | 61 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl
122 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 62 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
123 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 63 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
124 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 64 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
125 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 65 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
126 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 66 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
127 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | no | 61 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
128 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 62 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
129 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 63 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
130 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 64 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
131 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 65 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
132 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 66 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
133 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 56 | 0 | 1 | 0.2 | yes | no | 67 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
134 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 68 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
135 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 69 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
136 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 70 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
137 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 71 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
138 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 72 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
139 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | yes | no | 67 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
140 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 68 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
141 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 69 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
142 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 70 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
143 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 71 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
144 | Fault | 1PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 72 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
145 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 51 | 0 | 1 | 0.2 | yes | no | 73 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
146 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 74 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
147 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 75 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
148 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 76 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
149 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 77 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
150 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 78 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
151 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | no | 73 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
152 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 74 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
153 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 75 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
154 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 76 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
155 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 77 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
156 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 78 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
157 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 56 | 0 | 1 | 0.2 | yes | no | 79 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
158 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 80 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
159 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 81 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
160 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 82 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
161 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 83 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
162 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 84 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
163 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | yes | no | 79 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
164 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 80 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
165 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 81 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
166 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 82 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
167 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 83 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
168 | Fault | 1PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 84 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
169 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 51 | 0 | 1 | 0.2 | yes | no | 85 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
170 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 86 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
171 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 87 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
172 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 88 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
173 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 89 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
174 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 90 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
175 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | no | 85 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
176 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 86 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
177 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 87 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
178 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 88 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
179 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 89 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
180 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 90 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
181 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 56 | 0 | 1 | 0.2 | yes | no | 91 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
182 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 92 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
183 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 93 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
184 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 94 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
185 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 95 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
186 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 96 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
187 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 16 | 0 | 1 | 0.2 | yes | no | 91 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMATsl5
188 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 92 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
189 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 93 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
190 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 94 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
191 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 95 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
192 | Fault | L-L | 5 | 2 |  | 0 | 3 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 96 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
193 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 51 | 0 | 1 | 0.2 | no | no | 97 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
194 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 98 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
195 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 99 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
196 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 100 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
197 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 101 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
198 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 102 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
199 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 97 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
200 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 98 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
201 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 99 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
202 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 100 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
203 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 101 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
204 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 102 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
205 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 56 | 0 | 1 | 0.2 | no | no | 103 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
206 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 104 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
207 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 105 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
208 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 106 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
209 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 107 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
210 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 108 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
211 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 103 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
212 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 104 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
213 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 105 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
214 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 106 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
215 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 107 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
216 | Fault | 2PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 108 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
217 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 51 | 0 | 1 | 0.2 | no | no | 97 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
218 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 98 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
219 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 99 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
220 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 100 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
221 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 101 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
222 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 102 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
223 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 97 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
224 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 98 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
225 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 99 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
226 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 100 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
227 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 101 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
228 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 102 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
229 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 56 | 0 | 1 | 0.2 | no | no | 103 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
230 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 104 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
231 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 105 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
232 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 106 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
233 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 107 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
234 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 108 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
235 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 103 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
236 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 104 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
237 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 105 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
238 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 106 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
239 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 107 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
240 | Fault | 2PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 108 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
241 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 51 | 0 | 1 | 0.2 | no | no | 97 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
242 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 98 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
243 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 99 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
244 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 100 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
245 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 101 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
246 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 102 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
247 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 97 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
248 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 98 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
249 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 99 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
250 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 100 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
251 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 101 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
252 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 102 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
253 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 56 | 0 | 1 | 0.2 | no | no | 103 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
254 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 104 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
255 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 105 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
256 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 106 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
257 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 107 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
258 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 108 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
259 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 103 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
260 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 104 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
261 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 105 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
262 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 106 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
263 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 107 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
264 | Fault | 2PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 108 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
265 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 51 | 0 | 1 | 0.2 | no | no | 109 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
266 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 110 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
267 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 111 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
268 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 112 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
269 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 113 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
270 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 114 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
271 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 109 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
272 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 110 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
273 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 111 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
274 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 112 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
275 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 113 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
276 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 114 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
277 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 56 | 0 | 1 | 0.2 | no | no | 115 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
278 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 116 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
279 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 117 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
280 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 118 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
281 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 119 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
282 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 120 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
283 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 115 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
284 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 116 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
285 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 117 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
286 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 118 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
287 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 119 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
288 | Fault | 1PHG | 5 | 2 | 1.4142 |  | 1 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 120 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
289 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 51 | 0 | 1 | 0.2 | no | no | 109 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
290 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 110 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
291 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 111 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
292 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 112 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
293 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 113 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
294 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 114 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
295 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 109 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
296 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 110 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
297 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 111 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
298 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 112 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
299 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 113 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
300 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 114 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
301 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 56 | 0 | 1 | 0.2 | no | no | 115 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
302 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 116 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
303 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 117 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
304 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 118 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
305 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 119 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
306 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 120 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
307 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 115 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
308 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 116 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
309 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 117 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
310 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 118 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
311 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 119 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
312 | Fault | 1PHG | 5 | 2 | 2.8284 |  | 1 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 120 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
313 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 51 | 0 | 1 | 0.2 | no | no | 109 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
314 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 53 | 0 | 1 | 0.2 | no | no | 110 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
315 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 52 | 0 | 1 | 0.2 | no | no | 111 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
316 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 31 | 0 | 1 | 0.2 | no | no | 112 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
317 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 43 | 0 | 1 | 0.2 | no | no | 113 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
318 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 42 | 0 | 1 | 0.2 | no | no | 114 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
319 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 11 | 0 | 1 | 0.2 | no | no | 109 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
320 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 13 | 0 | 1 | 0.2 | no | no | 110 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
321 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 12 | 0 | 1 | 0.2 | no | no | 111 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
322 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 1 | 0 | 1 | 0.2 | no | no | 112 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
323 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 3 | 0 | 1 | 0.2 | no | no | 113 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
324 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 2 | 0 | 1 | 0.2 | no | no | 114 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
325 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 56 | 0 | 1 | 0.2 | no | no | 115 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
326 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 58 | 0 | 1 | 0.2 | no | no | 116 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
327 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 57 | 0 | 1 | 0.2 | no | no | 117 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
328 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 36 | 0 | 1 | 0.2 | no | no | 118 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
329 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 48 | 0 | 1 | 0.2 | no | no | 119 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
330 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 47 | 0 | 1 | 0.2 | no | no | 120 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
331 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 16 | 0 | 1 | 0.2 | no | no | 115 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
332 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 18 | 0 | 1 | 0.2 | no | no | 116 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
333 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 17 | 0 | 1 | 0.2 | no | no | 117 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
334 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 6 | 0 | 1 | 0.2 | no | no | 118 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
335 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 8 | 0 | 1 | 0.2 | no | no | 119 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
336 | Fault | 1PHG | 5 | 2 | 7.0711 |  | 1 | [7 empty] | 7 | 0 | 1 | 0.2 | no | no | 120 | Unbalanced fault – large disturbance test cases [PSCAD/EMTDC models] | DMAT
337 | Multifault | 3PHG | 5 | 0.1 |  | 0.2 | 1.13 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | no | 121 | Multiple Fault Ride Through (MFRT) test [PSCAD/EMTDC models] | DMATsl5
|  | 3PHG | 5.25 | 0.1 |  | 0.2 | 1.13 | [9 empty] | 1 |  | yes | no |  |  | DMATsl5
|  | 3PHG | 5.5 | 0.1 |  | 0.2 | 1.13 | [9 empty] | 1 |  | yes | no |  |  | DMATsl5
|  | 2PHG | 8 | 0.1 |  | 0.2 | 1.13 | [9 empty] | 1 |  | yes | no |  |  | DMATsl5
|  | 2PHG | 11 | 0.1 |  | 0.2 | 1.13 | [9 empty] | 1 |  | yes | no |  |  | DMATsl5
|  | 2PHG | 13 | 0.1 |  | 0.2 | 1.13 | [9 empty] | 1 |  | yes | no |  |  | DMATsl5
338 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | yes | no | 122 | Multiple Fault Ride Through (MFRT) test [PSCAD/EMTDC models] | DMATsl5
339 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | no | 123 | Multiple Fault Ride Through (MFRT) test [PSCAD/EMTDC models] | DMAT
340 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | no | 124 | Multiple Fault Ride Through (MFRT) test [PSCAD/EMTDC models] | DMAT
341 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | no | 125 | Multiple Fault Ride Through (MFRT) test [PSCAD/EMTDC models] | DMAT
342 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | yes | 126 | MFRT Test [PSS®E models] | DMATsl5
343 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | yes | 127 | MFRT Test [PSS®E models] | DMATsl5
344 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | no | 128 | MFRT Test [PSS®E models] | DMAT
345 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | no | 129 | MFRT Test [PSS®E models] | DMAT
346 | Multifault_random |  | 5 | [11 empty] | 1 | 0 | 1 | 0.2 | no | no | 130 | MFRT Test [PSS®E models] | DMAT
347 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 90 | 14 | 31 | 0 | 1 | 0.2 | yes | yes | 200 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMATsl5
348 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 90 | 14 | 129 | 0 | 1 | 0.2 | no | no | 201 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
349 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 90 | 14 | 36 | 0 | 1 | 0.2 | no | no | 202 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
350 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 90 | 14 | 31 | 0 | 1 | 0.2 | yes | yes | 203 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMATsl5
351 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 90 | 14 | 129 | 0 | 1 | 0.2 | no | no | 204 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
352 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 90 | 14 | 36 | 0 | 1 | 0.2 | no | no | 205 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
353 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 90 | 3 | 41 | 0 | 1 | 0.2 | yes | yes | 200 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMATsl5
354 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 90 | 3 | 130 | 0 | 1 | 0.2 | no | no | 201 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
355 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [6 empty] | 90 | 3 | 46 | 0 | 1 | 0.2 | no | no | 202 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
356 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 90 | 3 | 41 | 0 | 1 | 0.2 | yes | yes | 203 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMATsl5
357 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 90 | 3 | 130 | 0 | 1 | 0.2 | no | no | 204 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
358 | Fault | 3PHG | 5 | 0.43 |  | 0 | [6 empty] | 90 | 3 | 46 | 0 | 1 | 0.2 | no | no | 205 | POC SCR = 1 FRT Test [PSS®E and PSCAD/EMTDC models] | DMAT
359 | Fault | 3PHG | 5 | 0.43 |  | 0 | [8 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 206 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
360 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | [8 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 207 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
361 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | [8 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 208 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
362 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | [8 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 209 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
363 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | [8 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 210 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
364 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | [8 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 211 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
365 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | [8 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 212 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
366 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | [8 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 213 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
367 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [8 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 214 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
368 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | [8 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 215 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
369 | Fault | 3PHG | 5 | 0.43 |  | 0 | [8 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 216 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
370 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | [8 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 217 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
371 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | [8 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 218 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
372 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | [8 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 219 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
373 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | [8 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 220 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
374 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | [8 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 221 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
375 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | [8 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 222 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
376 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | [8 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 223 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
377 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | [8 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 224 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
378 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | [8 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 225 | FRT assessment for site-specific SCR and X/R [ PSS®E and PSCAD/EMTDC models] | DMATsl6
379 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255
380 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255
381 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255
382 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255
383 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255
384 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255
385 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255
386 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255
387 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255
388 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | 3 | [7 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255
389 | Multifault | 3PHG | 5 | 0.22 |  | 0.4 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Multiple Fault Ride Through (MFRT) test [PSCAD/EMTDC models] | S5255mulf
|  | 2PHG | 5.32 | 0.43 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 1PHG | 5.85 | 0.49 |  | 0.85 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 3PHG | 6.44 | 0.22 |  | 0.4 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 2PHG | 7.66 | 0.12 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 2PHG | 7.88 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 2PHG | 10.1 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 2PHG | 11.82 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 2PHG | 12.54 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 2PHG | 13.86 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 2PHG | 15.13 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 2PHG | 17.35 | 0.12 |  | 0.85 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 1PHG | 19.47 | 0.12 |  | 0.85 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 1PHG | 24.59 | 0.22 |  | 0.85 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
|  | 2PHG | 25.81 | 0.22 |  | 0.7 | 3 | [9 empty] | 1 |  | no | no |  |  | S5255mulf
390 | Fault | 3PHG | 5 | 5 |  | 0 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
391 | Fault | 3PHG | 5 | 5 |  | 0.05 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
392 | Fault | 3PHG | 5 | 5 |  | 0.1 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
393 | Fault | 3PHG | 5 | 5 |  | 0.15 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
394 | Fault | 3PHG | 5 | 5 |  | 0.2 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
395 | Fault | 3PHG | 5 | 5 |  | 0.25 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
396 | Fault | 3PHG | 5 | 5 |  | 0.3 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
397 | Fault | 3PHG | 5 | 5 |  | 0.35 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
398 | Fault | 3PHG | 5 | 5 |  | 0.4 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
399 | Fault | 3PHG | 5 | 5 |  | 0.45 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
400 | Fault | 3PHG | 5 | 5 |  | 0.5 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
401 | Fault | 3PHG | 5 | 5 |  | 0.55 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
402 | Fault | 3PHG | 5 | 5 |  | 0.6 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
403 | Fault | 3PHG | 5 | 5 |  | 0.65 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
404 | Fault | 3PHG | 5 | 5 |  | 0.7 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
405 | Fault | 3PHG | 5 | 5 |  | 0.75 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
406 | Fault | 3PHG | 5 | 5 |  | 0.8 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
407 | Fault | 3PHG | 5 | 5 |  | 0.85 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
408 | Fault | 3PHG | 5 | 5 |  | 0.9 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
409 | Fault | 3PHG | 5 | 5 |  | 0.95 | 3 | [7 empty] | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
410 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | Benchmarking
411 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | Benchmarking
412 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | Benchmarking
413 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | Benchmarking
414 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | Benchmarking
415 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | Benchmarking
416 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | Benchmarking
417 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | Benchmarking
418 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | Benchmarking
419 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | 3 | [7 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | Benchmarking
420 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 311 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg2
421 | Fault | 3PHG | 10 | 0.43 |  | 0.1 | 3 | [7 empty] | 311 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg2
422 | Fault | 3PHG | 10 | 0.43 |  | 0.2 | 3 | [7 empty] | 311 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg2
423 | Fault | 3PHG | 10 | 0.43 |  | 0.3 | 3 | [7 empty] | 311 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg2
424 | Fault | 3PHG | 10 | 0.43 |  | 0.4 | 3 | [7 empty] | 311 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg2
425 | Fault | 3PHG | 10 | 0.43 |  | 0.5 | 3 | [7 empty] | 311 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg2
426 | Fault | 3PHG | 10 | 0.43 |  | 0.6 | 3 | [7 empty] | 311 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg2
427 | Fault | 3PHG | 10 | 0.43 |  | 0.7 | 3 | [7 empty] | 311 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg2
428 | Fault | 3PHG | 10 | 0.43 |  | 0.8 | 3 | [7 empty] | 311 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg2
429 | Fault | 3PHG | 10 | 0.43 |  | 0.9 | 3 | [7 empty] | 311 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg2
430 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg
431 | Fault | 3PHG | 10 | 0.43 |  | 0.1 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg
432 | Fault | 3PHG | 10 | 0.43 |  | 0.2 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg
433 | Fault | 3PHG | 10 | 0.43 |  | 0.3 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg
434 | Fault | 3PHG | 10 | 0.43 |  | 0.4 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg
435 | Fault | 3PHG | 10 | 0.43 |  | 0.5 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg
436 | Fault | 3PHG | 10 | 0.43 |  | 0.6 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg
437 | Fault | 3PHG | 10 | 0.43 |  | 0.7 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg
438 | Fault | 3PHG | 10 | 0.43 |  | 0.8 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg
439 | Fault | 3PHG | 10 | 0.43 |  | 0.9 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | S52515dbg
440 | Fault | 3PHG | 10 | 0.01 |  | 1.019 | 3 | [5 empty] | 108 | 3 | 312 | 0 | 1 | 0.2 | yes | no |  | Low SCR test Table 4 Appendix B SSIAG [PSCAD/EMTDC models] | S52515dbg3
441 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 314 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
442 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 315 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
443 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 316 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
444 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 317 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
445 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 318 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
446 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 319 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
447 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 320 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
448 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 321 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
449 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 322 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
450 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 323 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
451 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 324 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
452 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 325 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
453 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 326 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
454 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 327 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
455 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 328 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
456 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 329 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
457 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 330 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
458 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 331 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
459 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 332 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
460 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 333 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
461 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 334 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
462 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 335 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
463 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 336 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
464 | Fault | 3PHG | 10 | 0.43 |  | 0 | 3 | [7 empty] | 337 | 2 | 1 | 0.2 | yes | yes |  | Low SCR test Table 2 Appendix B SSIAG [ PSS®E and PSCAD/EMTDC models] | lowSCR_finding
465 | Fault | 3PHG | 5 | 5 |  | 0 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
466 | Fault | 3PHG | 5 | 5 |  | 0.05 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
467 | Fault | 3PHG | 5 | 5 |  | 0.1 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
468 | Fault | 3PHG | 5 | 5 |  | 0.15 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
469 | Fault | 3PHG | 5 | 5 |  | 0.2 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
470 | Fault | 3PHG | 5 | 5 |  | 0.25 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
471 | Fault | 3PHG | 5 | 5 |  | 0.3 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
472 | Fault | 3PHG | 5 | 5 |  | 0.35 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
473 | Fault | 3PHG | 5 | 5 |  | 0.4 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
474 | Fault | 3PHG | 5 | 5 |  | 0.45 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
475 | Fault | 3PHG | 5 | 5 |  | 0.5 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
476 | Fault | 3PHG | 5 | 5 |  | 0.55 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
477 | Fault | 3PHG | 5 | 5 |  | 0.6 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
478 | Fault | 3PHG | 5 | 5 |  | 0.65 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
479 | Fault | 3PHG | 5 | 5 |  | 0.7 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
480 | Fault | 3PHG | 5 | 5 |  | 0.75 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
481 | Fault | 3PHG | 5 | 5 |  | 0.8 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
482 | Fault | 3PHG | 5 | 5 |  | 0.85 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
483 | Fault | 3PHG | 5 | 5 |  | 0.9 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
484 | Fault | 3PHG | 5 | 5 |  | 0.95 | 3 | [7 empty] | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
485 | Fault | 3PHG | 5 | 5 |  | 0 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
486 | Fault | 3PHG | 5 | 5 |  | 0.05 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
487 | Fault | 3PHG | 5 | 5 |  | 0.1 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
488 | Fault | 3PHG | 5 | 5 |  | 0.15 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
489 | Fault | 3PHG | 5 | 5 |  | 0.2 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
490 | Fault | 3PHG | 5 | 5 |  | 0.25 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
491 | Fault | 3PHG | 5 | 5 |  | 0.3 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
492 | Fault | 3PHG | 5 | 5 |  | 0.35 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
493 | Fault | 3PHG | 5 | 5 |  | 0.4 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
494 | Fault | 3PHG | 5 | 5 |  | 0.45 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
495 | Fault | 3PHG | 5 | 5 |  | 0.5 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
496 | Fault | 3PHG | 5 | 5 |  | 0.55 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
497 | Fault | 3PHG | 5 | 5 |  | 0.6 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
498 | Fault | 3PHG | 5 | 5 |  | 0.65 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
499 | Fault | 3PHG | 5 | 5 |  | 0.7 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
500 | Fault | 3PHG | 5 | 5 |  | 0.75 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
501 | Fault | 3PHG | 5 | 5 |  | 0.8 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
502 | Fault | 3PHG | 5 | 5 |  | 0.85 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
503 | Fault | 3PHG | 5 | 5 |  | 0.9 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
504 | Fault | 3PHG | 5 | 5 |  | 0.95 | 3 | [7 empty] | 305 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmin
505 | Fault | 3PHG | 5 | 0.43 | 47.539 |  | 3 | [7 empty] | 205 | 0 | 1 | 0.2 | no | yes |  | AEMO Figure 6 - PSSE model Item 19 | S5255_AEMO
506 | Fault | 3PHG | 5 | 0.43 | 47.539 |  | 3 | [7 empty] | 210 | 0 | 1 | 0.2 | no | yes |  | AEMO Figure 6 - PSSE model Item 19 | S5255_AEMO
507 | Fault | 3PHG | 5 | 0.43 | 38.425 |  | 3 | [7 empty] | 204 | 0 | 1 | 0.2 | no | yes |  | AEMO Figure 7 - PSSE model Item 20 | S5255_AEMO
508 | Fault | 3PHG | 5 | 0.43 | 39.325 |  | 3 | [7 empty] | 219 | 0 | 1 | 0.2 | no | yes |  | AEMO Figure 7 - PSSE model Item 20 | S5255_AEMO
509 | Fault | 3PHG | 5 | 0.43 | 46.874 |  | 3 | [7 empty] | 220 | 0 | 1 | 0.2 | no | yes |  | AEMO Figure 8 - PSSE model Item 21 | S5255_AEMO
510 | Fault | 3PHG | 5 | 0.43 | 46.874 |  | 3 | [7 empty] | 236 | 0 | 1 | 0.2 | no | yes |  | AEMO Figure 8 - PSSE model Item 21 | S5255_AEMO
511 | Fault | 3PHG | 5 | 0.43 | 58.07 |  | 3 | [7 empty] | 239 | 0 | 1 | 0.2 | no | yes |  | AEMO Figure 8 - PSSE model Item 21 | S5255_AEMO
512 | Fault | 3PHG | 10 | 0.43 | 409.615 |  | 3 | [7 empty] | 236 | 2 | 1 | 0.2 | yes | yes |  | PSCAD_Model - Item 9, Figure 8 | S5255_TG_flatrun
513 | Fault | 3PHG | 5 | 0.43 | 409.615 |  | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | Transgrid Fig 12 - PSCAD model Item 11 | S5255_TG
514 | Fault | 3PHG | 5 | 0.43 | 285.489 |  | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | Transgrid Fig 12 - PSCAD model Item 11 | S5255_TG
515 | Fault | 3PHG | 5 | 0.43 | 74.475 |  | 3 | [7 empty] | 220 | 2 | 1 | 0.2 | yes | yes |  | Transgrid Fig 13 - PSCAD model Item 12 | S5255_TG
516 | Fault | 3PHG | 5 | 0.43 | 49.65 |  | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | Transgrid Fig 13 - PSCAD model Item 12 | S5255_TG
517 | Fault | 3PHG | 5 | 0.43 | 434.44 |  | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | Transgrid Fig 14 - PSCAD model Item 13 | S5255_TG
518 | Fault | 3PHG | 5 | 0.43 | 248.251 |  | 3 | [7 empty] | 220 | 2 | 1 | 0.2 | yes | yes |  | Transgrid Fig 15 - PSCAD model Item 14 | S5255_TG
519 | Fault | L-L | 5 | 0.43 | 5.589 |  | 947.322 | [7 empty] | 221 | 2 | 1 | 0.2 | yes | no |  | Transgrid Fig 18 - PSCAD model Item 18 | S5255_TG
520 | Fault | 3PHG | 5 | 0.43 | 86.888 |  | 3 | [7 empty] | 219 | 2 | 1 | 0.2 | yes | yes |  | Transgrid Fig 19 - PSCAD model Item 19 | S5255_TG
521 | Fault | 3PHG | 5 | 0.43 | 277.107 |  | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | no |  | AEMO Fig 14 - PSCAD model Item 25 | S5255_AEMO
522 | Fault | 2PHG | 5 | 0.43 | 277.107 |  | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | no |  | AEMO Fig 15 - PSCAD model Item 26 | S5255_AEMO
523 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1dbg
524 | Fault | 3PHG | 5 | 0.43 |  | 0.05 | 3 | [7 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
525 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
526 | Fault | 3PHG | 5 | 0.43 |  | 0.15 | 3 | [7 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
527 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
528 | Fault | 3PHG | 5 | 0.43 |  | 0.25 | 3 | [7 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
529 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
530 | Fault | 3PHG | 5 | 0.43 |  | 0.35 | 3 | [7 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
531 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
532 | Fault | 3PHG | 5 | 0.43 |  | 0.45 | 3 | [7 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
533 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
534 | Fault | 3PHG | 5 | 0.43 |  | 0.55 | 3 | [7 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
535 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
536 | Fault | 3PHG | 5 | 0.43 |  | 0.65 | 3 | [7 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
537 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
538 | Fault | 3PHG | 5 | 0.43 |  | 0.75 | 3 | [7 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
539 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
540 | Fault | 3PHG | 5 | 0.43 |  | 0.85 | 3 | [7 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
541 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | 3 | [7 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
542 | Fault | 3PHG | 5 | 0.43 |  | 0.95 | 3 | [7 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
543 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
544 | Fault | 3PHG | 5 | 0.43 |  | 0.05 | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
545 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
546 | Fault | 3PHG | 5 | 0.43 |  | 0.15 | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
547 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
548 | Fault | 3PHG | 5 | 0.43 |  | 0.25 | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
549 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
550 | Fault | 3PHG | 5 | 0.43 |  | 0.35 | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
551 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
552 | Fault | 3PHG | 5 | 0.43 |  | 0.45 | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
553 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
554 | Fault | 3PHG | 5 | 0.43 |  | 0.55 | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
555 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
556 | Fault | 3PHG | 5 | 0.43 |  | 0.65 | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
557 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
558 | Fault | 3PHG | 5 | 0.43 |  | 0.75 | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
559 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
560 | Fault | 3PHG | 5 | 0.43 |  | 0.85 | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
561 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
562 | Fault | 3PHG | 5 | 0.43 |  | 0.95 | 3 | [7 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
563 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
564 | Fault | 3PHG | 5 | 0.43 |  | 0.05 | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
565 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
566 | Fault | 3PHG | 5 | 0.43 |  | 0.15 | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
567 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
568 | Fault | 3PHG | 5 | 0.43 |  | 0.25 | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
569 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
570 | Fault | 3PHG | 5 | 0.43 |  | 0.35 | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
571 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
572 | Fault | 3PHG | 5 | 0.43 |  | 0.45 | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
573 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
574 | Fault | 3PHG | 5 | 0.43 |  | 0.55 | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
575 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
576 | Fault | 3PHG | 5 | 0.43 |  | 0.65 | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
577 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
578 | Fault | 3PHG | 5 | 0.43 |  | 0.75 | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
579 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
580 | Fault | 3PHG | 5 | 0.43 |  | 0.85 | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
581 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
582 | Fault | 3PHG | 5 | 0.43 |  | 0.95 | 3 | [7 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
583 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
584 | Fault | 3PHG | 5 | 0.43 |  | 0.05 | 3 | [7 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
585 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
586 | Fault | 3PHG | 5 | 0.43 |  | 0.15 | 3 | [7 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
587 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
588 | Fault | 3PHG | 5 | 0.43 |  | 0.25 | 3 | [7 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
589 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
590 | Fault | 3PHG | 5 | 0.43 |  | 0.35 | 3 | [7 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
591 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
592 | Fault | 3PHG | 5 | 0.43 |  | 0.45 | 3 | [7 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
593 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
594 | Fault | 3PHG | 5 | 0.43 |  | 0.55 | 3 | [7 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
595 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
596 | Fault | 3PHG | 5 | 0.43 |  | 0.65 | 3 | [7 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
597 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
598 | Fault | 3PHG | 5 | 0.43 |  | 0.75 | 3 | [7 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
599 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
600 | Fault | 3PHG | 5 | 0.43 |  | 0.85 | 3 | [7 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
601 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | 3 | [7 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
602 | Fault | 3PHG | 5 | 0.43 |  | 0.95 | 3 | [7 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
603 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
604 | Fault | 3PHG | 5 | 0.43 |  | 0.05 | 3 | [7 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
605 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
606 | Fault | 3PHG | 5 | 0.43 |  | 0.15 | 3 | [7 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
607 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
608 | Fault | 3PHG | 5 | 0.43 |  | 0.25 | 3 | [7 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
609 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
610 | Fault | 3PHG | 5 | 0.43 |  | 0.35 | 3 | [7 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
611 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
612 | Fault | 3PHG | 5 | 0.43 |  | 0.45 | 3 | [7 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
613 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
614 | Fault | 3PHG | 5 | 0.43 |  | 0.55 | 3 | [7 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
615 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
616 | Fault | 3PHG | 5 | 0.43 |  | 0.65 | 3 | [7 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
617 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
618 | Fault | 3PHG | 5 | 0.43 |  | 0.75 | 3 | [7 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
619 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
620 | Fault | 3PHG | 5 | 0.43 |  | 0.85 | 3 | [7 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
621 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | 3 | [7 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
622 | Fault | 3PHG | 5 | 0.43 |  | 0.95 | 3 | [7 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
623 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
624 | Fault | 3PHG | 5 | 0.43 |  | 0.05 | 3 | [7 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
625 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
626 | Fault | 3PHG | 5 | 0.43 |  | 0.15 | 3 | [7 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
627 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
628 | Fault | 3PHG | 5 | 0.43 |  | 0.25 | 3 | [7 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
629 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
630 | Fault | 3PHG | 5 | 0.43 |  | 0.35 | 3 | [7 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
631 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
632 | Fault | 3PHG | 5 | 0.43 |  | 0.45 | 3 | [7 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
633 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
634 | Fault | 3PHG | 5 | 0.43 |  | 0.55 | 3 | [7 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
635 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
636 | Fault | 3PHG | 5 | 0.43 |  | 0.65 | 3 | [7 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
637 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
638 | Fault | 3PHG | 5 | 0.43 |  | 0.75 | 3 | [7 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
639 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
640 | Fault | 3PHG | 5 | 0.43 |  | 0.85 | 3 | [7 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
641 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | 3 | [7 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
642 | Fault | 3PHG | 5 | 0.43 |  | 0.95 | 3 | [7 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
643 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
644 | Fault | 3PHG | 5 | 0.43 |  | 0.05 | 3 | [7 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
645 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
646 | Fault | 3PHG | 5 | 0.43 |  | 0.15 | 3 | [7 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
647 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
648 | Fault | 3PHG | 5 | 0.43 |  | 0.25 | 3 | [7 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
649 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
650 | Fault | 3PHG | 5 | 0.43 |  | 0.35 | 3 | [7 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
651 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
652 | Fault | 3PHG | 5 | 0.43 |  | 0.45 | 3 | [7 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
653 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
654 | Fault | 3PHG | 5 | 0.43 |  | 0.55 | 3 | [7 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
655 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
656 | Fault | 3PHG | 5 | 0.43 |  | 0.65 | 3 | [7 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
657 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
658 | Fault | 3PHG | 5 | 0.43 |  | 0.75 | 3 | [7 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
659 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
660 | Fault | 3PHG | 5 | 0.43 |  | 0.85 | 3 | [7 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
661 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | 3 | [7 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
662 | Fault | 3PHG | 5 | 0.43 |  | 0.95 | 3 | [7 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
663 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
664 | Fault | 3PHG | 5 | 0.43 |  | 0.05 | 3 | [7 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
665 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
666 | Fault | 3PHG | 5 | 0.43 |  | 0.15 | 3 | [7 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
667 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
668 | Fault | 3PHG | 5 | 0.43 |  | 0.25 | 3 | [7 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
669 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
670 | Fault | 3PHG | 5 | 0.43 |  | 0.35 | 3 | [7 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
671 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
672 | Fault | 3PHG | 5 | 0.43 |  | 0.45 | 3 | [7 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
673 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
674 | Fault | 3PHG | 5 | 0.43 |  | 0.55 | 3 | [7 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
675 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
676 | Fault | 3PHG | 5 | 0.43 |  | 0.65 | 3 | [7 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
677 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
678 | Fault | 3PHG | 5 | 0.43 |  | 0.75 | 3 | [7 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
679 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
680 | Fault | 3PHG | 5 | 0.43 |  | 0.85 | 3 | [7 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
681 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | 3 | [7 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
682 | Fault | 3PHG | 5 | 0.43 |  | 0.95 | 3 | [7 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
683 | Fault | 3PHG | 5 | 0.43 |  | 0 | 3 | [7 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
684 | Fault | 3PHG | 5 | 0.43 |  | 0.05 | 3 | [7 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
685 | Fault | 3PHG | 5 | 0.43 |  | 0.1 | 3 | [7 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
686 | Fault | 3PHG | 5 | 0.43 |  | 0.15 | 3 | [7 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
687 | Fault | 3PHG | 5 | 0.43 |  | 0.2 | 3 | [7 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
688 | Fault | 3PHG | 5 | 0.43 |  | 0.25 | 3 | [7 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
689 | Fault | 3PHG | 5 | 0.43 |  | 0.3 | 3 | [7 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
690 | Fault | 3PHG | 5 | 0.43 |  | 0.35 | 3 | [7 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
691 | Fault | 3PHG | 5 | 0.43 |  | 0.4 | 3 | [7 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
692 | Fault | 3PHG | 5 | 0.43 |  | 0.45 | 3 | [7 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
693 | Fault | 3PHG | 5 | 0.43 |  | 0.5 | 3 | [7 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
694 | Fault | 3PHG | 5 | 0.43 |  | 0.55 | 3 | [7 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
695 | Fault | 3PHG | 5 | 0.43 |  | 0.6 | 3 | [7 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
696 | Fault | 3PHG | 5 | 0.43 |  | 0.65 | 3 | [7 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
697 | Fault | 3PHG | 5 | 0.43 |  | 0.7 | 3 | [7 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
698 | Fault | 3PHG | 5 | 0.43 |  | 0.75 | 3 | [7 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
699 | Fault | 3PHG | 5 | 0.43 |  | 0.8 | 3 | [7 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
700 | Fault | 3PHG | 5 | 0.43 |  | 0.85 | 3 | [7 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
701 | Fault | 3PHG | 5 | 0.43 |  | 0.9 | 3 | [7 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
702 | Fault | 3PHG | 5 | 0.43 |  | 0.95 | 3 | [7 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
Note on C6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Multifault, include a few sequences that are hard-coded. In case a multifault sequence is chosen, The Fault X_R, Impedance, residual voltage, duration and application time are ignored.
Note on Q6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Ini_help = 0: normal ini Ini_help = 1: fix SCL to inf before 2sec when low SCR Ini_help = 2: fix Vinf to 1.0pu before 2sec when low SCR
Note on A7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MAT
Note on A31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MAT
Note on A55: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MAT
Note on Y465: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be checked again: we want to change the SCR only, not after the fault is applied Reply: Assuming that the fault happens, so the SCR change, but voltage level does not change much
Note on W537: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Need to update the Vinf = 1.1pu so Q will be equal to Qmin

## ORT
PSSE-specific settings
CaseNr | Test Type | time | Disturbance Frequency | Disturbance Magnitude | Vbase | PhaseOsc Magnitude | ActivePower | ReactivePower | Grid SCR | Grid X_R | setpoint ID | TimeStep | AccFactor | run in PSCAD? | run in PSS/E? | Comment/Corresponding DMAT case | test group | simulation batch
1 | ORT | 5 | 0.1 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
2 | ORT | 5 | 0.2 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
3 | ORT | 5 | 0.3 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
4 | ORT | 5 | 0.4 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
5 | ORT | 5 | 0.5 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
6 | ORT | 5 | 0.6 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
7 | ORT | 5 | 0.7 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
8 | ORT | 5 | 0.8 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
9 | ORT | 5 | 0.9 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 190 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
10 | ORT | 5 | 1 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
11 | ORT | 5 | 2 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
12 | ORT | 5 | 3 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
13 | ORT | 5 | 4 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
14 | ORT | 5 | 5 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
15 | ORT | 5 | 6 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
16 | ORT | 5 | 7 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
17 | ORT | 5 | 8 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
18 | ORT | 5 | 9 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
19 | ORT | 5 | 10 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
20 | ORT | 5 | 11 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
21 | ORT | 5 | 12 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
22 | ORT | 5 | 13 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
23 | ORT | 5 | 14 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
24 | ORT | 5 | 15 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
25 | ORT | 5 | 16 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
26 | ORT | 5 | 17 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
27 | ORT | 5 | 18 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
28 | ORT | 5 | 19 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
29 | ORT | 5 | 20 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
30 | ORT | 5 | 21 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
31 | ORT | 5 | 22 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
32 | ORT | 5 | 23 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
33 | ORT | 5 | 24 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
34 | ORT | 5 | 25 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | yes | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMATsl
35 | ORT | 5 | 26 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
36 | ORT | 5 | 27 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
37 | ORT | 5 | 28 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
38 | ORT | 5 | 29 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
39 | ORT | 5 | 30 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
40 | ORT | 5 | 31 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
41 | ORT | 5 | 32 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
42 | ORT | 5 | 33 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
43 | ORT | 5 | 34 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
44 | ORT | 5 | 35 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
45 | ORT | 5 | 36 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
46 | ORT | 5 | 37 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
47 | ORT | 5 | 38 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
48 | ORT | 5 | 39 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
49 | ORT | 5 | 40 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
50 | ORT | 5 | 41 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
51 | ORT | 5 | 42 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
52 | ORT | 5 | 43 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
53 | ORT | 5 | 44 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
54 | ORT | 5 | 45 | 0.005 |  | 0 |  |  |  |  | 11 | 1 | 0.2 | no | no | 191 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
55 | ORT | 5 | 0.1 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
56 | ORT | 5 | 0.2 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
57 | ORT | 5 | 0.3 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
58 | ORT | 5 | 0.4 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
59 | ORT | 5 | 0.5 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
60 | ORT | 5 | 0.6 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
61 | ORT | 5 | 0.7 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
62 | ORT | 5 | 0.8 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
63 | ORT | 5 | 0.9 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
64 | ORT | 5 | 1 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
65 | ORT | 5 | 2 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
66 | ORT | 5 | 3 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
67 | ORT | 5 | 4 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
68 | ORT | 5 | 5 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
69 | ORT | 5 | 6 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
70 | ORT | 5 | 7 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
71 | ORT | 5 | 8 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
72 | ORT | 5 | 9 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
73 | ORT | 5 | 10 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
74 | ORT | 5 | 11 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
75 | ORT | 5 | 12 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
76 | ORT | 5 | 13 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
77 | ORT | 5 | 14 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
78 | ORT | 5 | 15 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
79 | ORT | 5 | 16 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
80 | ORT | 5 | 17 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
81 | ORT | 5 | 18 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
82 | ORT | 5 | 19 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
83 | ORT | 5 | 20 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
84 | ORT | 5 | 21 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
85 | ORT | 5 | 22 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
86 | ORT | 5 | 23 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
87 | ORT | 5 | 24 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
88 | ORT | 5 | 25 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
89 | ORT | 5 | 26 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
90 | ORT | 5 | 27 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
91 | ORT | 5 | 28 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
92 | ORT | 5 | 29 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
93 | ORT | 5 | 30 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
94 | ORT | 5 | 31 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
95 | ORT | 5 | 32 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
96 | ORT | 5 | 33 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
97 | ORT | 5 | 34 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
98 | ORT | 5 | 35 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
99 | ORT | 5 | 36 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
100 | ORT | 5 | 37 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
101 | ORT | 5 | 38 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
102 | ORT | 5 | 39 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
103 | ORT | 5 | 40 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
104 | ORT | 5 | 41 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
105 | ORT | 5 | 42 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
106 | ORT | 5 | 43 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
107 | ORT | 5 | 44 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
108 | ORT | 5 | 45 | 0.005 |  | 2 |  |  |  |  | 11 | 1 | 0.2 | no | no | 192 | Grid Oscillation rejection test [PSCAD/EMTDC models] | DMAT
Note on F2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: if not specified, just modulate in proportion to Vth voltage dictated by setpoint

## SmallDist
When defining the SmallDist tests, make sure the initial values of the profiles do not contradict the Initialisation parameters in the Setpoints tab, as they will overwrite the parameters form the "Setpoints" sheet, where applicable. E.G.: When running S5.2.5.4 on an inifinite grid, and the selected initial setpoint defined in the "PSCAD setpoint ID" inisilises to 1.04pu at the POC, then the test profile selected under "Test profile" and defined in the "Profiles" sheet, should also start with 1.04pu to ensure smooth intialisation. If the profile starts at a different voltage, it might for example lead to different power flows at the POC and an incoherent transformer tap. (In the future a routine could be added that scales or offsets the profile to match the initial valuye of the profile, and notifies the user). Grid SCR and Grid X/R refer to the point where the grid source is attached, which may be differnet from the POC. For example in the case of Mulwala the grid source is connected at 132 kV level, (which is where the plant controls the voltage) but the POC is at 22 kV level. | [10 empty] | PSSE-specific settings
CaseNr | Test Type | Test profile | Etime | ActivePower | ReactivePower | Secondary SCL time | Secondary SCL | Secondary X_R | setpoint ID | init_help | TimeStep | AccFactor | run in PSCAD? | run in PSS/E? | Comment/Corresponding DMAT case | test group | simulation batch
1 | V_profile | FLAT_RUN_300 | [6 empty] | 81 | 0 | 1 | 0.2 | yes | no | 0.1 | Pre-requisite tests – single machine infinite bus (SMIB) flat run [PSCAD/EMTDC models] | DMATsllong
2 | V_profile | FLAT_RUN_300 | [6 empty] | 81 | 0 | 1 | 0.2 | yes | no | 0.2 | Pre-requisite tests – single machine infinite bus (SMIB) flat run [PSCAD/EMTDC models] | DMATsllong
3 | V_profile | FLAT_RUN_300 | [6 empty] | 86 | 0 | 1 | 0.2 | yes | no | 0.3 | Pre-requisite tests – single machine infinite bus (SMIB) flat run [PSCAD/EMTDC models] | DMATsllong
4 | V_profile | FLAT_RUN_5 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | no | 0.4 | Pre-requisite tests – single machine infinite bus (SMIB) flat run [PSCAD/EMTDC models] | DMATsl1
5 | V_profile | FLAT_RUN_5 | [6 empty] | 1 | 0 | 1 | 0.2 | yes | no | 0.5 | Pre-requisite tests – single machine infinite bus (SMIB) flat run [PSCAD/EMTDC models] | DMATsl1
6 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 51 | 0 | 1 | 0.2 | no | no | 149 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
7 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 61 | 0 | 1 | 0.2 | no | no | 149 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
8 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 56 | 0 | 1 | 0.2 | no | no | 150 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
9 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 150 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
10 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 151 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
11 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 41 | 0 | 1 | 0.2 | no | no | 151 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
12 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 36 | 0 | 1 | 0.2 | no | no | 152 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
13 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 46 | 0 | 1 | 0.2 | no | no | 152 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
14 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 153 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsl1
15 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 153 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsl1
16 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 16 | 0 | 1 | 0.2 | no | no | 154 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
17 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 6 | 0 | 1 | 0.2 | no | no | 154 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
18 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 51 | 0 | 1 | 0.2 | no | no | 155 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
19 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 61 | 0 | 1 | 0.2 | no | no | 155 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
20 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 56 | 0 | 1 | 0.2 | no | no | 156 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
21 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 156 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
22 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 157 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
23 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 41 | 0 | 1 | 0.2 | no | no | 157 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
24 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 36 | 0 | 1 | 0.2 | no | no | 158 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
25 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 46 | 0 | 1 | 0.2 | no | no | 158 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
26 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 159 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsl1
27 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 1 | 0 | 1 | 0.2 | no | no | 159 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
28 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 16 | 0 | 1 | 0.2 | yes | yes | 160 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsl1
29 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 6 | 0 | 1 | 0.2 | no | no | 160 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
30 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 162 | 0 | 1 | 0.2 | no | no | 161 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
31 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 166 | 0 | 1 | 0.2 | no | no | 161 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
32 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 164 | 0 | 1 | 0.2 | no | no | 162 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
33 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 168 | 0 | 1 | 0.2 | no | no | 162 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
34 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 161 | 0 | 1 | 0.2 | no | no | 163 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
35 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 165 | 0 | 1 | 0.2 | no | no | 163 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
36 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 163 | 0 | 1 | 0.2 | no | no | 164 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
37 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 167 | 0 | 1 | 0.2 | no | no | 164 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
38 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 141 | 0 | 1 | 0.2 | yes | yes | 165 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsl1
39 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 131 | 0 | 1 | 0.2 | yes | yes | 165 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsl1
40 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 146 | 0 | 1 | 0.2 | no | no | 166 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
41 | Q_stp_profile | MAT_QREF_STEP_Fig4.1 | [6 empty] | 136 | 0 | 1 | 0.2 | no | no | 166 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
42 | P_stp_profile | MAT_P_STEP_Fig5 | [6 empty] | 51 | 0 | 1 | 0.2 | no | no | 167 | Active Power Controller Reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
43 | P_stp_profile | MAT_P_STEP_Fig5 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 168 | Active Power Controller Reference step change [PSS®E and PSCAD/EMTDC models] | DMAT
44 | P_stp_profile | MAT_P_STEP_Fig5 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 169 | Active Power Controller Reference step change [PSS®E and PSCAD/EMTDC models] | DMATsl1
45 | P_stp_profile | MAT_P_STEP_Fig5 | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 169 | Active Power Controller Reference step change [PSS®E and PSCAD/EMTDC models] | DMATsl1
46 | F_profile | F_PROFILE_Fig6_1 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 170 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
47 | F_profile | F_PROFILE_Fig6_2 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 170 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
48 | F_profile | F_PROFILE_Fig6_3 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 170 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
49 | F_profile | F_PROFILE_Fig6_4 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 170 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
50 | F_profile | F_PROFILE_Fig6_1 | [6 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 171 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
51 | F_profile | F_PROFILE_Fig6_2 | [6 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 171 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
52 | F_profile | F_PROFILE_Fig6_3 | [6 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 171 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
53 | F_profile | F_PROFILE_Fig6_4 | [6 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 171 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
54 | F_profile | F_PROFILE_Fig6_1 | [6 empty] | 123 | 0 | 1 | 0.2 | yes | yes | 172 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
55 | F_profile | F_PROFILE_Fig6_2 | [6 empty] | 123 | 0 | 1 | 0.2 | yes | yes | 172 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
56 | F_profile | F_PROFILE_Fig6_3 | [6 empty] | 123 | 0 | 1 | 0.2 | yes | yes | 172 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
57 | F_profile | F_PROFILE_Fig6_4 | [6 empty] | 123 | 0 | 1 | 0.2 | yes | yes | 172 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
58 | F_profile | F_PROFILE_Fig6_1 | [6 empty] | 127 | 0 | 1 | 0.2 | yes | yes | 173 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
59 | F_profile | F_PROFILE_Fig6_2 | [6 empty] | 127 | 0 | 1 | 0.2 | yes | yes | 173 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
60 | F_profile | F_PROFILE_Fig6_3 | [6 empty] | 127 | 0 | 1 | 0.2 | yes | yes | 173 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
61 | F_profile | F_PROFILE_Fig6_4 | [6 empty] | 127 | 0 | 1 | 0.2 | yes | yes | 173 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
62 | F_profile | F_PROFILE_Fig7_1 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 174 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
63 | F_profile | F_PROFILE_Fig7_2 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 174 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
64 | F_profile | F_PROFILE_Fig7_1 | [6 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 175 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
65 | F_profile | F_PROFILE_Fig7_2 | [6 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 175 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
66 | F_profile | F_PROFILE_Fig7_1 | [6 empty] | 123 | 0 | 1 | 0.2 | yes | yes | 176 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
67 | F_profile | F_PROFILE_Fig7_2 | [6 empty] | 123 | 0 | 1 | 0.2 | yes | yes | 176 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
68 | F_profile | F_PROFILE_Fig7_1 | [6 empty] | 127 | 0 | 1 | 0.2 | yes | yes | 177 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2
69 | F_profile | F_PROFILE_Fig7_2 | [6 empty] | 127 | 0 | 1 | 0.2 | yes | yes | 177 | Grid frequency – controller test [PSS®E and PSCAD/EMTDC models] | DMATsl2 | Need to initialise with High P, then reduce to low level before applying Frequency Disturbance
70 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 51 | 0 | 1 | 0.2 | no | no | 178 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
71 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 61 | 0 | 1 | 0.2 | no | no | 178 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
72 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 179 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
73 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 41 | 0 | 1 | 0.2 | no | no | 179 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
74 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 180 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
75 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 180 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
76 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 181 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
77 | V_profile | MAT_V_STEP_Fig8 | [6 empty] | 122 | 0 | 1 | 0.2 | yes | yes | 181 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
78 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 51 | 0 | 1 | 0.2 | no | no | 182 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
79 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 61 | 0 | 1 | 0.2 | no | no | 182 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
80 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 183 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
81 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 41 | 0 | 1 | 0.2 | no | no | 183 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
82 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 184 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
83 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 184 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
84 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 121 | 0 | 1 | 0.2 | yes | yes | 185 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
85 | V_profile | MAT_V_STEP_Fig9 | [6 empty] | 122 | 0 | 1 | 0.2 | yes | yes | 185 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
86 | V_profile | MAT_V_STEP_Fig10.1 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 51 | 0 | 1 | 0.2 | no | no | 186 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
87 | V_profile | MAT_V_STEP_Fig10.1 | [6 empty] | 61 | 0 | 1 | 0.2 | no | no | 186 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
88 | V_profile | MAT_V_STEP_Fig10.1 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 187 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
89 | V_profile | MAT_V_STEP_Fig10.1 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 41 | 0 | 1 | 0.2 | no | no | 187 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
90 | V_profile | MAT_V_STEP_Fig10.1 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 11 | 0 | 1 | 0.2 | yes | yes | 188 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
91 | V_profile | MAT_V_STEP_Fig10.1 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 1 | 0 | 1 | 0.2 | yes | yes | 188 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3dbg91
92 | V_profile | MAT_V_STEP_Fig10.1 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 121 | 0 | 1 | 0.2 | yes | yes | 189 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
93 | V_profile | MAT_V_STEP_Fig10.1 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 122 | 0 | 1 | 0.2 | yes | yes | 189 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
94 | V_profile | MAT_V_STEP_Fig10.2 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 51 | 0 | 1 | 0.2 | no | no | 186 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
95 | V_profile | MAT_V_STEP_Fig10.2 | [6 empty] | 61 | 0 | 1 | 0.2 | no | no | 186 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
96 | V_profile | MAT_V_STEP_Fig10.2 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 187 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
97 | V_profile | MAT_V_STEP_Fig10.2 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 41 | 0 | 1 | 0.2 | no | no | 187 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
98 | V_profile | MAT_V_STEP_Fig10.2 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 11 | 0 | 1 | 0.2 | yes | yes | 188 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3dbg98
99 | V_profile | MAT_V_STEP_Fig10.2 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 1 | 0 | 1 | 0.2 | yes | yes | 188 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
100 | V_profile | MAT_V_STEP_Fig10.2 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 121 | 0 | 1 | 0.2 | yes | yes | 189 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
101 | V_profile | MAT_V_STEP_Fig10.2 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 122 | 0 | 1 | 0.2 | yes | yes | 189 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
102 | V_profile | MAT_V_STEP_Fig10.3 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 51 | 0 | 1 | 0.2 | no | no | 186 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
103 | V_profile | MAT_V_STEP_Fig10.3 | [6 empty] | 61 | 0 | 1 | 0.2 | no | no | 186 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
104 | V_profile | MAT_V_STEP_Fig10.3 | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 187 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
105 | V_profile | MAT_V_STEP_Fig10.3 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 41 | 0 | 1 | 0.2 | no | no | 187 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
106 | V_profile | MAT_V_STEP_Fig10.3 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 11 | 0 | 1 | 0.2 | yes | yes | 188 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
107 | V_profile | MAT_V_STEP_Fig10.3 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 1 | 0 | 1 | 0.2 | yes | yes | 188 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
108 | V_profile | MAT_V_STEP_Fig10.3 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 121 | 0 | 1 | 0.2 | yes | yes | 189 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3dbg108
109 | V_profile | MAT_V_STEP_Fig10.3 | V_profile | MAT_V_STEP_Fig8 |  |  |  |  | 122 | 0 | 1 | 0.2 | yes | yes | 189 | Grid voltage change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl3
110 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 51 | 0 | 1 | 0.2 | no | no | 193 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
111 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 61 | 0 | 1 | 0.2 | no | no | 193 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
112 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 56 | 0 | 1 | 0.2 | no | no | 194 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
113 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 194 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
114 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 195 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
115 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 41 | 0 | 1 | 0.2 | no | no | 195 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
116 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 36 | 0 | 1 | 0.2 | no | no | 196 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
117 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 46 | 0 | 1 | 0.2 | no | no | 196 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
118 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 197 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl4
119 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 197 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMATsl4
120 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 16 | 0 | 1 | 0.2 | no | no | 198 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
121 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 6 | 0 | 1 | 0.2 | no | no | 198 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
122 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 51 | 0 | 1 | 0.2 | no | no | 193 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
123 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 61 | 0 | 1 | 0.2 | no | no | 193 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
124 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 56 | 0 | 1 | 0.2 | no | no | 194 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
125 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 66 | 0 | 1 | 0.2 | no | no | 194 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
126 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 31 | 0 | 1 | 0.2 | no | no | 195 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
127 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 41 | 0 | 1 | 0.2 | no | no | 195 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
128 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 36 | 0 | 1 | 0.2 | no | no | 196 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
129 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 46 | 0 | 1 | 0.2 | no | no | 196 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
130 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 11 | 0 | 1 | 0.2 | no | no | 197 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
131 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 1 | 0 | 1 | 0.2 | no | no | 197 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
132 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 16 | 0 | 1 | 0.2 | no | no | 198 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
133 | ANG_profile | MAT_ANG_STEP+/-60deg | [6 empty] | 6 | 0 | 1 | 0.2 | no | no | 198 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMAT
134 | P_stp_profile | MAT_P_STEP_Fig12 | [6 empty] | 106 | 0 | 1 | 0.2 | yes | yes | 199 | POC SCR = 1 Active Power reference change test [PSS®E and PSCAD/EMTDC models] | DMATsl4
135 | P_stp_profile | MAT_P_STEP_Fig12 | [6 empty] | 116 | 0 | 1 | 0.2 | yes | yes | 199 | POC SCR = 1 Active Power reference change test [PSS®E and PSCAD/EMTDC models] | DMATsl4
136 | Auxiliary_profile | AVAIL_P_-20% | [6 empty] | 11 | 0 | 1 | 0.2 | no | no | 226 | Input power source step change test | DMAT | Need to check profile again
137 | Auxiliary_profile | AVAIL_P_-20% | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes | 226 | Input power source step change test | DMATsl4
138 | Auxiliary_profile | AVAIL_P_+20% | [6 empty] | 11 | 0 | 1 | 0.2 | no | no | 227 | Input power source step change test | DMAT
139 | Auxiliary_profile | AVAIL_P_+20% | [6 empty] | 1 | 0 | 1 | 0.2 | no | no | 227 | Input power source step change test | DMAT
140 | Auxiliary_profile | AVAIL_P_+20% | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes | 228 | Input power source step change test | DMATsl4 | Need to check profile again
141 | Auxiliary_profile | AVAIL_P_+20% | [6 empty] | 1 | 0 | 1 | 0.2 | no | no | 228 | Input power source step change test | DMAT
142 | Auxiliary_profile | AVAIL_P_-20% | [6 empty] | 11 | 0 | 1 | 0.2 | no | no | 229 | Input power source step change test | DMAT
143 | Auxiliary_profile | AVAIL_P_-20% | [6 empty] | 1 | 0 | 1 | 0.2 | no | no | 229 | Input power source step change test | DMAT
144 | F_profile | S5253_UF | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5253long
145 | F_profile | S5253_OF | [6 empty] | 1 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5253long
146 | F_profile | S5253_UF | [6 empty] | 6 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253long
147 | F_profile | S5253_OF | [6 empty] | 6 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253long
148 | F_profile | S5253_UF | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5253long
149 | F_profile | S5253_OF | [6 empty] | 11 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5253long
150 | F_profile | S5253_UF | [6 empty] | 16 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253long
151 | F_profile | S5253_OF | [6 empty] | 16 | 0 | 1 | 0.2 | no | no |  | V control mode | S5253long
152 | F_profile | S5253_UF | [6 empty] | 131 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S5253long
153 | F_profile | S5253_OF | [6 empty] | 131 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S5253long
154 | F_profile | S5253_UF | [6 empty] | 136 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253long
155 | F_profile | S5253_OF | [6 empty] | 136 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253long
156 | F_profile | S5253_UF | [6 empty] | 141 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S5253long
157 | F_profile | S5253_OF | [6 empty] | 141 | 0 | 1 | 0.2 | yes | yes |  | Q control mode | S5253long
158 | F_profile | S5253_UF | [6 empty] | 146 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253long
159 | F_profile | S5253_OF | [6 empty] | 146 | 0 | 1 | 0.2 | no | no |  | Q control mode | S5253long
160 | F_profile | S5253_UF | [6 empty] | 171 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S5253long
161 | F_profile | S5253_OF | [6 empty] | 171 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S5253long
162 | F_profile | S5253_UF | [6 empty] | 176 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253long
163 | F_profile | S5253_OF | [6 empty] | 176 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253long
164 | F_profile | S5253_UF | [6 empty] | 181 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S5253long
165 | F_profile | S5253_OF | [6 empty] | 181 | 0 | 1 | 0.2 | yes | yes |  | PF control mode | S5253long
166 | F_profile | S5253_UF | [6 empty] | 186 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253long
167 | F_profile | S5253_OF | [6 empty] | 186 | 0 | 1 | 0.2 | no | no |  | PF control mode | S5253long
168 | F_profile | S5253_UF_short | [6 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
169 | F_profile | S5253_OF_short | [6 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
170 | F_profile | S5253_UF_short | [6 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
171 | F_profile | S5253_OF_short | [6 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
172 | F_profile | S5253_UF_short | [6 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
173 | F_profile | S5253_OF_short | [6 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
174 | F_profile | S5253_UF_short | [6 empty] | 206 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
175 | F_profile | S5253_OF_short | [6 empty] | 206 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
176 | F_profile | S5253_UF_short | [6 empty] | 209 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
177 | F_profile | S5253_OF_short | [6 empty] | 209 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
178 | F_profile | S5253_UF_short | [6 empty] | 210 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
179 | F_profile | S5253_OF_short | [6 empty] | 210 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
180 | F_profile | S5253_UF_short | [6 empty] | 211 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
181 | F_profile | S5253_OF_short | [6 empty] | 211 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
182 | F_profile | S5253_UF_short | [6 empty] | 214 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
183 | F_profile | S5253_OF_short | [6 empty] | 214 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
184 | F_profile | S5253_UF_short | [6 empty] | 215 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
185 | F_profile | S5253_OF_short | [6 empty] | 215 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
186 | F_profile | S5253_UF_short | [6 empty] | 216 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
187 | F_profile | S5253_OF_short | [6 empty] | 216 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
188 | F_profile | S5253_UF_short | [6 empty] | 219 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
189 | F_profile | S5253_OF_short | [6 empty] | 219 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
190 | F_profile | S5253_UF_short | [6 empty] | 220 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
191 | F_profile | S5253_OF_short | [6 empty] | 220 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
192 | F_profile | S5253_UF_short | [6 empty] | 221 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
193 | F_profile | S5253_OF_short | [6 empty] | 221 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
194 | F_profile | S5253_UF_short | [6 empty] | 224 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
195 | F_profile | S5253_OF_short | [6 empty] | 224 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
196 | F_profile | S5253_UF_short | [6 empty] | 225 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
197 | F_profile | S5253_OF_short | [6 empty] | 225 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
198 | F_profile | S5253_UF_short | [6 empty] | 226 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
199 | F_profile | S5253_OF_short | [6 empty] | 226 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
200 | F_profile | S5253_UF_short | [6 empty] | 229 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
201 | F_profile | S5253_OF_short | [6 empty] | 229 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
202 | F_profile | S5253_UF_short | [6 empty] | 230 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
203 | F_profile | S5253_OF_short | [6 empty] | 230 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
204 | F_profile | S5253_UF_short | [6 empty] | 231 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
205 | F_profile | S5253_OF_short | [6 empty] | 231 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
206 | F_profile | S5253_UF_short | [6 empty] | 234 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
207 | F_profile | S5253_OF_short | [6 empty] | 234 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
208 | F_profile | S5253_UF_short | [6 empty] | 235 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
209 | F_profile | S5253_OF_short | [6 empty] | 235 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
210 | F_profile | S5253_UF_short | [6 empty] | 236 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
211 | F_profile | S5253_OF_short | [6 empty] | 236 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
212 | F_profile | S5253_UF_short | [6 empty] | 239 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
213 | F_profile | S5253_OF_short | [6 empty] | 239 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
214 | F_profile | S5253_UF_short | [6 empty] | 240 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
215 | F_profile | S5253_OF_short | [6 empty] | 240 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
216 | F_profile | S5253_UF_short | [6 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
217 | F_profile | S5253_OF_short | [6 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
218 | F_profile | S5253_UF_short | [6 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
219 | F_profile | S5253_OF_short | [6 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
220 | F_profile | S5253_UF_short | [6 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
221 | F_profile | S5253_OF_short | [6 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
222 | F_profile | S5253_UF_short | [6 empty] | 246 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
223 | F_profile | S5253_OF_short | [6 empty] | 246 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
224 | F_profile | S5253_UF_short | [6 empty] | 249 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
225 | F_profile | S5253_OF_short | [6 empty] | 249 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
226 | F_profile | S5253_UF_short | [6 empty] | 250 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
227 | F_profile | S5253_OF_short | [6 empty] | 250 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
228 | F_profile | S5253_UF_short | [6 empty] | 251 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
229 | F_profile | S5253_OF_short | [6 empty] | 251 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
230 | F_profile | S5253_UF_short | [6 empty] | 254 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
231 | F_profile | S5253_OF_short | [6 empty] | 254 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
232 | F_profile | S5253_UF_short | [6 empty] | 255 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
233 | F_profile | S5253_OF_short | [6 empty] | 255 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
234 | F_profile | S5253_UF_short | [6 empty] | 256 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
235 | F_profile | S5253_OF_short | [6 empty] | 256 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
236 | F_profile | S5253_UF_short | [6 empty] | 259 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
237 | F_profile | S5253_OF_short | [6 empty] | 259 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
238 | F_profile | S5253_UF_short | [6 empty] | 260 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
239 | F_profile | S5253_OF_short | [6 empty] | 260 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
240 | F_profile | S5253_UF_short | [6 empty] | 261 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
241 | F_profile | S5253_OF_short | [6 empty] | 261 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
242 | F_profile | S5253_UF_short | [6 empty] | 264 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
243 | F_profile | S5253_OF_short | [6 empty] | 264 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
244 | F_profile | S5253_UF_short | [6 empty] | 265 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
245 | F_profile | S5253_OF_short | [6 empty] | 265 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
246 | F_profile | S5253_UF_short | [6 empty] | 266 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
247 | F_profile | S5253_OF_short | [6 empty] | 266 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
248 | F_profile | S5253_UF_short | [6 empty] | 269 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
249 | F_profile | S5253_OF_short | [6 empty] | 269 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
250 | F_profile | S5253_UF_short | [6 empty] | 270 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
251 | F_profile | S5253_OF_short | [6 empty] | 270 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
252 | F_profile | S5253_UF_short | [6 empty] | 271 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
253 | F_profile | S5253_OF_short | [6 empty] | 271 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
254 | F_profile | S5253_UF_short | [6 empty] | 274 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
255 | F_profile | S5253_OF_short | [6 empty] | 274 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
256 | F_profile | S5253_UF_short | [6 empty] | 275 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
257 | F_profile | S5253_OF_short | [6 empty] | 275 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
258 | F_profile | S5253_UF_short | [6 empty] | 276 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
259 | F_profile | S5253_OF_short | [6 empty] | 276 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
260 | F_profile | S5253_UF_short | [6 empty] | 279 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
261 | F_profile | S5253_OF_short | [6 empty] | 279 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
262 | F_profile | S5253_UF_short | [6 empty] | 280 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
263 | F_profile | S5253_OF_short | [6 empty] | 280 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5253
264 | F_profile | S5253_UF_short | [6 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
265 | F_profile | S5253_OF_short | [6 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
266 | F_profile | S5253_UF_short | [6 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
267 | F_profile | S5253_OF_short | [6 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
268 | F_profile | S5253_UF_short | [6 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
269 | F_profile | S5253_OF_short | [6 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
270 | F_profile | S5253_UF_short | [6 empty] | 286 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
271 | F_profile | S5253_OF_short | [6 empty] | 286 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
272 | F_profile | S5253_UF_short | [6 empty] | 289 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
273 | F_profile | S5253_OF_short | [6 empty] | 289 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
274 | F_profile | S5253_UF_short | [6 empty] | 290 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
275 | F_profile | S5253_OF_short | [6 empty] | 290 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
276 | F_profile | S5253_UF_short | [6 empty] | 291 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
277 | F_profile | S5253_OF_short | [6 empty] | 291 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
278 | F_profile | S5253_UF_short | [6 empty] | 294 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
279 | F_profile | S5253_OF_short | [6 empty] | 294 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
280 | F_profile | S5253_UF_short | [6 empty] | 295 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
281 | F_profile | S5253_OF_short | [6 empty] | 295 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
282 | F_profile | S5253_UF_short | [6 empty] | 296 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
283 | F_profile | S5253_OF_short | [6 empty] | 296 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
284 | F_profile | S5253_UF_short | [6 empty] | 299 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
285 | F_profile | S5253_OF_short | [6 empty] | 299 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
286 | F_profile | S5253_UF_short | [6 empty] | 300 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
287 | F_profile | S5253_OF_short | [6 empty] | 300 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
288 | F_profile | S5253_UF_short | [6 empty] | 301 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
289 | F_profile | S5253_OF_short | [6 empty] | 301 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
290 | F_profile | S5253_UF_short | [6 empty] | 304 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
291 | F_profile | S5253_OF_short | [6 empty] | 304 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
292 | F_profile | S5253_UF_short | [6 empty] | 305 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
293 | F_profile | S5253_OF_short | [6 empty] | 305 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
294 | F_profile | S5253_UF_short | [6 empty] | 306 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
295 | F_profile | S5253_OF_short | [6 empty] | 306 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
296 | F_profile | S5253_UF_short | [6 empty] | 309 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
297 | F_profile | S5253_OF_short | [6 empty] | 309 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
298 | F_profile | S5253_UF_short | [6 empty] | 310 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
299 | F_profile | S5253_OF_short | [6 empty] | 310 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
300 | F_profile | S5253_UF_short | [6 empty] | 311 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
301 | F_profile | S5253_OF_short | [6 empty] | 311 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
302 | F_profile | S5253_UF_short | [6 empty] | 314 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
303 | F_profile | S5253_OF_short | [6 empty] | 314 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
304 | F_profile | S5253_UF_short | [6 empty] | 315 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
305 | F_profile | S5253_OF_short | [6 empty] | 315 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
306 | F_profile | S5253_UF_short | [6 empty] | 316 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
307 | F_profile | S5253_OF_short | [6 empty] | 316 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
308 | F_profile | S5253_UF_short | [6 empty] | 319 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
309 | F_profile | S5253_OF_short | [6 empty] | 319 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
310 | F_profile | S5253_UF_short | [6 empty] | 320 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
311 | F_profile | S5253_OF_short | [6 empty] | 320 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5253
312 | V_profile | S5254_LVRT | [6 empty] | 441 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
313 | V_profile | S5254_HVRT | [6 empty] | 441 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
314 | V_profile | S5254_LVRT_Qmax | [6 empty] | 444 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
315 | V_profile | S5254_HVRT_Qmax | [6 empty] | 444 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
316 | V_profile | S5254_LVRT_Qmin | [6 empty] | 445 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
317 | V_profile | S5254_HVRT_Qmin | [6 empty] | 445 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
318 | V_profile | S5254_LVRT | [6 empty] | 446 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
319 | V_profile | S5254_HVRT | [6 empty] | 446 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
320 | V_profile | S5254_LVRT_Qmax | [6 empty] | 449 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
321 | V_profile | S5254_HVRT_Qmax | [6 empty] | 449 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
322 | V_profile | S5254_LVRT_Qmin | [6 empty] | 450 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
323 | V_profile | S5254_HVRT_Qmin | [6 empty] | 450 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
324 | V_profile | S5254_LVRT | [6 empty] | 451 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
325 | V_profile | S5254_HVRT | [6 empty] | 451 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
326 | V_profile | S5254_LVRT_Qmax | [6 empty] | 454 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
327 | V_profile | S5254_HVRT_Qmax | [6 empty] | 454 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
328 | V_profile | S5254_LVRT_Qmin | [6 empty] | 455 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
329 | V_profile | S5254_HVRT_Qmin | [6 empty] | 455 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
330 | V_profile | S5254_LVRT | [6 empty] | 456 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
331 | V_profile | S5254_HVRT | [6 empty] | 456 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
332 | V_profile | S5254_LVRT_Qmax | [6 empty] | 459 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
333 | V_profile | S5254_HVRT_Qmax | [6 empty] | 459 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
334 | V_profile | S5254_LVRT_Qmin | [6 empty] | 460 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
335 | V_profile | S5254_HVRT_Qmin | [6 empty] | 460 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
336 | V_profile | S5254_LVRT | [6 empty] | 461 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
337 | V_profile | S5254_HVRT | [6 empty] | 461 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
338 | V_profile | S5254_LVRT_Qmax | [6 empty] | 464 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
339 | V_profile | S5254_HVRT_Qmax | [6 empty] | 464 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
340 | V_profile | S5254_LVRT_Qmin | [6 empty] | 465 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
341 | V_profile | S5254_HVRT_Qmin | [6 empty] | 465 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
342 | V_profile | S5254_LVRT | [6 empty] | 466 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
343 | V_profile | S5254_HVRT | [6 empty] | 466 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
344 | V_profile | S5254_LVRT_Qmax | [6 empty] | 469 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
345 | V_profile | S5254_HVRT_Qmax | [6 empty] | 469 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
346 | V_profile | S5254_LVRT_Qmin | [6 empty] | 470 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
347 | V_profile | S5254_HVRT_Qmin | [6 empty] | 470 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
348 | V_profile | S5254_LVRT | [6 empty] | 471 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
349 | V_profile | S5254_HVRT | [6 empty] | 471 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
350 | V_profile | S5254_LVRT_Qmax | [6 empty] | 474 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
351 | V_profile | S5254_HVRT_Qmax | [6 empty] | 474 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
352 | V_profile | S5254_LVRT_Qmin | [6 empty] | 475 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
353 | V_profile | S5254_HVRT_Qmin | [6 empty] | 475 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
354 | V_profile | S5254_LVRT | [6 empty] | 476 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
355 | V_profile | S5254_HVRT | [6 empty] | 476 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
356 | V_profile | S5254_LVRT_Qmax | [6 empty] | 479 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
357 | V_profile | S5254_HVRT_Qmax | [6 empty] | 479 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
358 | V_profile | S5254_LVRT_Qmin | [6 empty] | 480 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
359 | V_profile | S5254_HVRT_Qmin | [6 empty] | 480 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5254
360 | V_profile | S5254_LVRT | [6 empty] | 481 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
361 | V_profile | S5254_HVRT | [6 empty] | 481 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
362 | V_profile | S5254_LVRT_Qmax | [6 empty] | 484 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
363 | V_profile | S5254_HVRT_Qmax | [6 empty] | 484 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
364 | V_profile | S5254_LVRT_Qmin | [6 empty] | 485 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
365 | V_profile | S5254_HVRT_Qmin | [6 empty] | 485 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
366 | V_profile | S5254_LVRT | [6 empty] | 486 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
367 | V_profile | S5254_HVRT | [6 empty] | 486 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
368 | V_profile | S5254_LVRT_Qmax | [6 empty] | 489 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
369 | V_profile | S5254_HVRT_Qmax | [6 empty] | 489 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
370 | V_profile | S5254_LVRT_Qmin | [6 empty] | 490 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
371 | V_profile | S5254_HVRT_Qmin | [6 empty] | 490 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
372 | V_profile | S5254_LVRT | [6 empty] | 491 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
373 | V_profile | S5254_HVRT | [6 empty] | 491 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
374 | V_profile | S5254_LVRT_Qmax | [6 empty] | 494 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
375 | V_profile | S5254_HVRT_Qmax | [6 empty] | 494 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
376 | V_profile | S5254_LVRT_Qmin | [6 empty] | 495 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
377 | V_profile | S5254_HVRT_Qmin | [6 empty] | 495 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
378 | V_profile | S5254_LVRT | [6 empty] | 496 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
379 | V_profile | S5254_HVRT | [6 empty] | 496 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
380 | V_profile | S5254_LVRT_Qmax | [6 empty] | 499 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
381 | V_profile | S5254_HVRT_Qmax | [6 empty] | 499 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
382 | V_profile | S5254_LVRT_Qmin | [6 empty] | 500 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
383 | V_profile | S5254_HVRT_Qmin | [6 empty] | 500 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
384 | V_profile | S5254_LVRT | [6 empty] | 501 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
385 | V_profile | S5254_HVRT | [6 empty] | 501 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
386 | V_profile | S5254_LVRT_Qmax | [6 empty] | 504 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
387 | V_profile | S5254_HVRT_Qmax | [6 empty] | 504 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
388 | V_profile | S5254_LVRT_Qmin | [6 empty] | 505 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
389 | V_profile | S5254_HVRT_Qmin | [6 empty] | 505 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
390 | V_profile | S5254_LVRT | [6 empty] | 506 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
391 | V_profile | S5254_HVRT | [6 empty] | 506 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
392 | V_profile | S5254_LVRT_Qmax | [6 empty] | 509 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
393 | V_profile | S5254_HVRT_Qmax | [6 empty] | 509 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
394 | V_profile | S5254_LVRT_Qmin | [6 empty] | 510 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
395 | V_profile | S5254_HVRT_Qmin | [6 empty] | 510 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
396 | V_profile | S5254_LVRT | [6 empty] | 511 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
397 | V_profile | S5254_HVRT | [6 empty] | 511 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
398 | V_profile | S5254_LVRT_Qmax | [6 empty] | 514 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
399 | V_profile | S5254_HVRT_Qmax | [6 empty] | 514 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
400 | V_profile | S5254_LVRT_Qmin | [6 empty] | 515 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
401 | V_profile | S5254_HVRT_Qmin | [6 empty] | 515 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
402 | V_profile | S5254_LVRT | [6 empty] | 516 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
403 | V_profile | S5254_HVRT | [6 empty] | 516 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
404 | V_profile | S5254_LVRT_Qmax | [6 empty] | 519 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
405 | V_profile | S5254_HVRT_Qmax | [6 empty] | 519 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
406 | V_profile | S5254_LVRT_Qmin | [6 empty] | 520 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
407 | V_profile | S5254_HVRT_Qmin | [6 empty] | 520 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254
408 | V_profile | S5254_LVRT | [6 empty] | 521 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
409 | V_profile | S5254_HVRT | [6 empty] | 521 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
410 | V_profile | S5254_LVRT_Qmax | [6 empty] | 524 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
411 | V_profile | S5254_HVRT_Qmax | [6 empty] | 524 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
412 | V_profile | S5254_LVRT_Qmin | [6 empty] | 525 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
413 | V_profile | S5254_HVRT_Qmin | [6 empty] | 525 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
414 | V_profile | S5254_LVRT | [6 empty] | 526 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
415 | V_profile | S5254_HVRT | [6 empty] | 526 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
416 | V_profile | S5254_LVRT_Qmax | [6 empty] | 529 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
417 | V_profile | S5254_HVRT_Qmax | [6 empty] | 529 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
418 | V_profile | S5254_LVRT_Qmin | [6 empty] | 530 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
419 | V_profile | S5254_HVRT_Qmin | [6 empty] | 530 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
420 | V_profile | S5254_LVRT | [6 empty] | 531 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
421 | V_profile | S5254_HVRT | [6 empty] | 531 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
422 | V_profile | S5254_LVRT_Qmax | [6 empty] | 534 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
423 | V_profile | S5254_HVRT_Qmax | [6 empty] | 534 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
424 | V_profile | S5254_LVRT_Qmin | [6 empty] | 535 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
425 | V_profile | S5254_HVRT_Qmin | [6 empty] | 535 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
426 | V_profile | S5254_LVRT | [6 empty] | 536 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
427 | V_profile | S5254_HVRT | [6 empty] | 536 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
428 | V_profile | S5254_LVRT_Qmax | [6 empty] | 539 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
429 | V_profile | S5254_HVRT_Qmax | [6 empty] | 539 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
430 | V_profile | S5254_LVRT_Qmin | [6 empty] | 540 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
431 | V_profile | S5254_HVRT_Qmin | [6 empty] | 540 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
432 | V_profile | S5254_LVRT | [6 empty] | 541 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
433 | V_profile | S5254_HVRT | [6 empty] | 541 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
434 | V_profile | S5254_LVRT_Qmax | [6 empty] | 544 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
435 | V_profile | S5254_HVRT_Qmax | [6 empty] | 544 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
436 | V_profile | S5254_LVRT_Qmin | [6 empty] | 545 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
437 | V_profile | S5254_HVRT_Qmin | [6 empty] | 545 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
438 | V_profile | S5254_LVRT | [6 empty] | 546 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
439 | V_profile | S5254_HVRT | [6 empty] | 546 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
440 | V_profile | S5254_LVRT_Qmax | [6 empty] | 549 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
441 | V_profile | S5254_HVRT_Qmax | [6 empty] | 549 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
442 | V_profile | S5254_LVRT_Qmin | [6 empty] | 550 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
443 | V_profile | S5254_HVRT_Qmin | [6 empty] | 550 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
444 | V_profile | S5254_LVRT | [6 empty] | 551 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
445 | V_profile | S5254_HVRT | [6 empty] | 551 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
446 | V_profile | S5254_LVRT_Qmax | [6 empty] | 554 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
447 | V_profile | S5254_HVRT_Qmax | [6 empty] | 554 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
448 | V_profile | S5254_LVRT_Qmin | [6 empty] | 555 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
449 | V_profile | S5254_HVRT_Qmin | [6 empty] | 555 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
450 | V_profile | S5254_LVRT | [6 empty] | 556 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
451 | V_profile | S5254_HVRT | [6 empty] | 556 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
452 | V_profile | S5254_LVRT_Qmax | [6 empty] | 559 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
453 | V_profile | S5254_HVRT_Qmax | [6 empty] | 559 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
454 | V_profile | S5254_LVRT_Qmin | [6 empty] | 560 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
455 | V_profile | S5254_HVRT_Qmin | [6 empty] | 560 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5254
456 | V_profile | S5254_110_CUO | [6 empty] | 24 | 2 | 1 | 0.2 | no | no |  | V control mode | S5254long
457 | V_profile | S5254_090_CUO | [6 empty] | 25 | 2 | 1 | 0.2 | no | no |  | V control mode | S5254long
458 | V_profile | S5254_110_CUO | [6 empty] | 29 | 2 | 1 | 0.2 | no | no |  | V control mode | S5254long
459 | V_profile | S5254_090_CUO | [6 empty] | 30 | 2 | 1 | 0.2 | no | no |  | V control mode | S5254long
460 | V_profile | S5254_110_CUO | [6 empty] | 154 | 2 | 1 | 0.2 | no | no |  | Q control mode | S5254long
461 | V_profile | S5254_090_CUO | [6 empty] | 155 | 2 | 1 | 0.2 | no | no |  | Q control mode | S5254long
462 | V_profile | S5254_110_CUO | [6 empty] | 159 | 2 | 1 | 0.2 | no | no |  | Q control mode | S5254long
463 | V_profile | S5254_090_CUO | [6 empty] | 160 | 2 | 1 | 0.2 | no | no |  | Q control mode | S5254long
464 | V_profile | S5254_110_CUO | [6 empty] | 194 | 2 | 1 | 0.2 | no | no |  | PF control mode | S5254long
465 | V_profile | S5254_090_CUO | [6 empty] | 195 | 2 | 1 | 0.2 | no | no |  | PF control mode | S5254long
466 | V_profile | S5254_110_CUO | [6 empty] | 199 | 2 | 1 | 0.2 | no | no |  | PF control mode | S5254long
467 | V_profile | S5254_090_CUO_short | [6 empty] | 481 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
468 | V_profile | S5254_110_CUO_short | [6 empty] | 481 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
469 | V_profile | S5254_090_CUO_short | [6 empty] | 484 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
470 | V_profile | S5254_110_CUO_short | [6 empty] | 484 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
471 | V_profile | S5254_090_CUO_short | [6 empty] | 485 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
472 | V_profile | S5254_110_CUO_short | [6 empty] | 485 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
473 | V_profile | S5254_090_CUO_short | [6 empty] | 486 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
474 | V_profile | S5254_110_CUO_short | [6 empty] | 486 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
475 | V_profile | S5254_090_CUO_short | [6 empty] | 489 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
476 | V_profile | S5254_110_CUO_short | [6 empty] | 489 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
477 | V_profile | S5254_090_CUO_short | [6 empty] | 490 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
478 | V_profile | S5254_110_CUO_short | [6 empty] | 490 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
479 | V_profile | S5254_090_CUO_short | [6 empty] | 491 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
480 | V_profile | S5254_110_CUO_short | [6 empty] | 491 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
481 | V_profile | S5254_090_CUO_short | [6 empty] | 494 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
482 | V_profile | S5254_110_CUO_short | [6 empty] | 494 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
483 | V_profile | S5254_090_CUO_short | [6 empty] | 495 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
484 | V_profile | S5254_110_CUO_short | [6 empty] | 495 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
485 | V_profile | S5254_090_CUO_short | [6 empty] | 496 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
486 | V_profile | S5254_110_CUO_short | [6 empty] | 496 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
487 | V_profile | S5254_090_CUO_short | [6 empty] | 499 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
488 | V_profile | S5254_110_CUO_short | [6 empty] | 499 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
489 | V_profile | S5254_090_CUO_short | [6 empty] | 500 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
490 | V_profile | S5254_110_CUO_short | [6 empty] | 500 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
491 | V_profile | S5254_090_CUO_short | [6 empty] | 501 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
492 | V_profile | S5254_110_CUO_short | [6 empty] | 501 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
493 | V_profile | S5254_090_CUO_short | [6 empty] | 504 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
494 | V_profile | S5254_110_CUO_short | [6 empty] | 504 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
495 | V_profile | S5254_090_CUO_short | [6 empty] | 505 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
496 | V_profile | S5254_110_CUO_short | [6 empty] | 505 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
497 | V_profile | S5254_090_CUO_short | [6 empty] | 506 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
498 | V_profile | S5254_110_CUO_short | [6 empty] | 506 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
499 | V_profile | S5254_090_CUO_short | [6 empty] | 509 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
500 | V_profile | S5254_110_CUO_short | [6 empty] | 509 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
501 | V_profile | S5254_090_CUO_short | [6 empty] | 510 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
502 | V_profile | S5254_110_CUO_short | [6 empty] | 510 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
503 | V_profile | S5254_090_CUO_short | [6 empty] | 511 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
504 | V_profile | S5254_110_CUO_short | [6 empty] | 511 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
505 | V_profile | S5254_090_CUO_short | [6 empty] | 514 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
506 | V_profile | S5254_110_CUO_short | [6 empty] | 514 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
507 | V_profile | S5254_090_CUO_short | [6 empty] | 515 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
508 | V_profile | S5254_110_CUO_short | [6 empty] | 515 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
509 | V_profile | S5254_090_CUO_short | [6 empty] | 516 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
510 | V_profile | S5254_110_CUO_short | [6 empty] | 516 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
511 | V_profile | S5254_090_CUO_short | [6 empty] | 519 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
512 | V_profile | S5254_110_CUO_short | [6 empty] | 519 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
513 | V_profile | S5254_090_CUO_short | [6 empty] | 520 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
514 | V_profile | S5254_110_CUO_short | [6 empty] | 520 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5254 | S5254CUO
515 | F_profile | S5257_OF_ShedLoad | [6 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
516 | F_profile | S5257_OF_ShedLoad | [6 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
517 | F_profile | S5257_OF_ShedLoad | [6 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
518 | F_profile | S5257_OF_ShedLoad | [6 empty] | 206 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
519 | F_profile | S5257_OF_ShedLoad | [6 empty] | 209 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
520 | F_profile | S5257_OF_ShedLoad | [6 empty] | 210 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
521 | V_profile | S5257_OF_ShedLoad | [6 empty] | 211 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
522 | V_profile | S5257_OF_ShedLoad | [6 empty] | 214 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
523 | V_profile | S5257_OF_ShedLoad | [6 empty] | 215 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
524 | V_profile | S5257_OF_ShedLoad | [6 empty] | 216 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
525 | V_profile | S5257_OF_ShedLoad | [6 empty] | 219 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
526 | V_profile | S5257_OF_ShedLoad | [6 empty] | 220 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
527 | F_profile | S5257_OF_ShedLoad | [6 empty] | 221 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
528 | F_profile | S5257_OF_ShedLoad | [6 empty] | 224 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
529 | F_profile | S5257_OF_ShedLoad | [6 empty] | 225 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
530 | F_profile | S5257_OF_ShedLoad | [6 empty] | 226 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
531 | F_profile | S5257_OF_ShedLoad | [6 empty] | 229 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
532 | F_profile | S5257_OF_ShedLoad | [6 empty] | 230 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
533 | V_profile | S5257_OF_ShedLoad | [6 empty] | 231 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
534 | V_profile | S5257_OF_ShedLoad | [6 empty] | 234 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
535 | V_profile | S5257_OF_ShedLoad | [6 empty] | 235 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
536 | V_profile | S5257_OF_ShedLoad | [6 empty] | 236 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
537 | V_profile | S5257_OF_ShedLoad | [6 empty] | 239 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
538 | V_profile | S5257_OF_ShedLoad | [6 empty] | 240 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5257
539 | F_profile | S5257_OF_ShedLoad | [6 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
540 | F_profile | S5257_OF_ShedLoad | [6 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
541 | F_profile | S5257_OF_ShedLoad | [6 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
542 | F_profile | S5257_OF_ShedLoad | [6 empty] | 246 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
543 | F_profile | S5257_OF_ShedLoad | [6 empty] | 249 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
544 | F_profile | S5257_OF_ShedLoad | [6 empty] | 250 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
545 | V_profile | S5257_OF_ShedLoad | [6 empty] | 251 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
546 | V_profile | S5257_OF_ShedLoad | [6 empty] | 254 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
547 | V_profile | S5257_OF_ShedLoad | [6 empty] | 255 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
548 | V_profile | S5257_OF_ShedLoad | [6 empty] | 256 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
549 | V_profile | S5257_OF_ShedLoad | [6 empty] | 259 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
550 | V_profile | S5257_OF_ShedLoad | [6 empty] | 260 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
551 | F_profile | S5257_OF_ShedLoad | [6 empty] | 261 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
552 | F_profile | S5257_OF_ShedLoad | [6 empty] | 264 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
553 | F_profile | S5257_OF_ShedLoad | [6 empty] | 265 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
554 | F_profile | S5257_OF_ShedLoad | [6 empty] | 266 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
555 | F_profile | S5257_OF_ShedLoad | [6 empty] | 269 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
556 | F_profile | S5257_OF_ShedLoad | [6 empty] | 270 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
557 | V_profile | S5257_OF_ShedLoad | [6 empty] | 271 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
558 | V_profile | S5257_OF_ShedLoad | [6 empty] | 274 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
559 | V_profile | S5257_OF_ShedLoad | [6 empty] | 275 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
560 | V_profile | S5257_OF_ShedLoad | [6 empty] | 276 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
561 | V_profile | S5257_OF_ShedLoad | [6 empty] | 279 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
562 | V_profile | S5257_OF_ShedLoad | [6 empty] | 280 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5257
563 | F_profile | S5257_OF_ShedLoad | [6 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
564 | F_profile | S5257_OF_ShedLoad | [6 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
565 | F_profile | S5257_OF_ShedLoad | [6 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
566 | F_profile | S5257_OF_ShedLoad | [6 empty] | 286 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
567 | F_profile | S5257_OF_ShedLoad | [6 empty] | 289 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
568 | F_profile | S5257_OF_ShedLoad | [6 empty] | 290 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
569 | V_profile | S5257_OF_ShedLoad | [6 empty] | 291 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
570 | V_profile | S5257_OF_ShedLoad | [6 empty] | 294 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
571 | V_profile | S5257_OF_ShedLoad | [6 empty] | 295 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
572 | V_profile | S5257_OF_ShedLoad | [6 empty] | 296 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
573 | V_profile | S5257_OF_ShedLoad | [6 empty] | 299 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
574 | V_profile | S5257_OF_ShedLoad | [6 empty] | 300 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
575 | F_profile | S5257_OF_ShedLoad | [6 empty] | 301 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
576 | F_profile | S5257_OF_ShedLoad | [6 empty] | 304 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
577 | F_profile | S5257_OF_ShedLoad | [6 empty] | 305 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
578 | F_profile | S5257_OF_ShedLoad | [6 empty] | 306 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
579 | F_profile | S5257_OF_ShedLoad | [6 empty] | 309 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
580 | F_profile | S5257_OF_ShedLoad | [6 empty] | 310 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
581 | V_profile | S5257_OF_ShedLoad | [6 empty] | 311 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
582 | V_profile | S5257_OF_ShedLoad | [6 empty] | 314 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
583 | V_profile | S5257_OF_ShedLoad | [6 empty] | 315 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
584 | V_profile | S5257_OF_ShedLoad | [6 empty] | 316 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
585 | V_profile | S5257_OF_ShedLoad | [6 empty] | 319 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
586 | V_profile | S5257_OF_ShedLoad | [6 empty] | 320 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5257
587 | F_profile | S5258_OF_TRIP | [6 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
588 | F_profile | S5258_UF_TRIP | [6 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
589 | V_profile | S5258_OV_TRIP | [6 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
590 | V_profile | S5258_UV_TRIP | [6 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
591 | F_profile | S5258_OF_TRIP | [6 empty] | 206 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
592 | F_profile | S5258_UF_TRIP | [6 empty] | 206 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
593 | F_profile | S5258_OV_TRIP | [6 empty] | 206 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
594 | F_profile | S5258_UV_TRIP | [6 empty] | 206 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
595 | F_profile | S5258_OF_TRIP | [6 empty] | 211 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
596 | F_profile | S5258_UF_TRIP | [6 empty] | 211 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
597 | V_profile | S5258_OV_TRIP | [6 empty] | 211 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
598 | V_profile | S5258_UV_TRIP | [6 empty] | 211 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
599 | F_profile | S5258_OF_TRIP | [6 empty] | 216 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
600 | F_profile | S5258_UF_TRIP | [6 empty] | 216 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
601 | V_profile | S5258_OV_TRIP | [6 empty] | 216 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
602 | V_profile | S5258_UV_TRIP | [6 empty] | 216 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
603 | F_profile | S5258_OF_TRIP | [6 empty] | 221 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
604 | F_profile | S5258_UF_TRIP | [6 empty] | 221 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
605 | F_profile | S5258_OV_TRIP | [6 empty] | 221 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
606 | F_profile | S5258_UV_TRIP | [6 empty] | 221 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
607 | F_profile | S5258_OF_TRIP | [6 empty] | 226 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
608 | F_profile | S5258_UF_TRIP | [6 empty] | 226 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
609 | V_profile | S5258_OV_TRIP | [6 empty] | 226 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
610 | V_profile | S5258_UV_TRIP | [6 empty] | 226 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
611 | V_profile | S5258_OF_TRIP | [6 empty] | 231 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
612 | V_profile | S5258_UF_TRIP | [6 empty] | 231 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
613 | V_profile | S5258_OV_TRIP | [6 empty] | 231 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
614 | V_profile | S5258_UV_TRIP | [6 empty] | 231 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
615 | V_profile | S5258_OF_TRIP | [6 empty] | 236 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
616 | V_profile | S5258_UF_TRIP | [6 empty] | 236 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
617 | V_profile | S5258_OV_TRIP | [6 empty] | 236 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
618 | V_profile | S5258_UV_TRIP | [6 empty] | 236 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5258
619 | V_profile | S5258_OF_TRIP | [6 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5258
620 | V_profile | S5258_UF_TRIP | [6 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5258
621 | V_profile | S5258_OV_TRIP | [6 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5258
622 | V_profile | S5258_UV_TRIP | [6 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5258
623 | F_profile | S52511_F_db | [6 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
624 | F_profile | S52511_+/-1Hz | [6 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
625 | F_profile | S52511_F_db | [6 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
626 | F_profile | S52511_+/-1Hz | [6 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
627 | F_profile | S52511_F_db | [6 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
628 | F_profile | S52511_+/-1Hz | [6 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
629 | F_profile | S52511_F_db | [6 empty] | 206 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
630 | F_profile | S52511_+/-1Hz | [6 empty] | 206 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
631 | F_profile | S52511_F_db | [6 empty] | 209 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
632 | F_profile | S52511_+/-1Hz | [6 empty] | 209 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
633 | F_profile | S52511_F_db | [6 empty] | 210 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
634 | F_profile | S52511_+/-1Hz | [6 empty] | 210 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
635 | F_profile | S52511_F_db | [6 empty] | 211 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
636 | F_profile | S52511_+/-1Hz | [6 empty] | 211 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
637 | F_profile | S52511_F_db | [6 empty] | 214 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
638 | F_profile | S52511_+/-1Hz | [6 empty] | 214 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
639 | F_profile | S52511_F_db | [6 empty] | 215 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
640 | F_profile | S52511_+/-1Hz | [6 empty] | 215 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
641 | F_profile | S52511_F_db | [6 empty] | 216 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
642 | F_profile | S52511_+/-1Hz | [6 empty] | 216 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
643 | F_profile | S52511_F_db | [6 empty] | 219 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
644 | F_profile | S52511_+/-1Hz | [6 empty] | 219 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
645 | F_profile | S52511_F_db | [6 empty] | 220 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
646 | F_profile | S52511_+/-1Hz | [6 empty] | 220 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
647 | F_profile | S52511_F_db | [6 empty] | 221 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
648 | F_profile | S52511_+/-1Hz | [6 empty] | 221 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
649 | F_profile | S52511_F_db | [6 empty] | 224 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
650 | F_profile | S52511_+/-1Hz | [6 empty] | 224 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
651 | F_profile | S52511_F_db | [6 empty] | 225 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
652 | F_profile | S52511_+/-1Hz | [6 empty] | 225 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
653 | F_profile | S52511_F_db | [6 empty] | 226 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
654 | F_profile | S52511_+/-1Hz | [6 empty] | 226 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
655 | F_profile | S52511_F_db | [6 empty] | 229 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
656 | F_profile | S52511_+/-1Hz | [6 empty] | 229 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
657 | F_profile | S52511_F_db | [6 empty] | 230 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
658 | F_profile | S52511_+/-1Hz | [6 empty] | 230 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
659 | F_profile | S52511_F_db | [6 empty] | 231 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
660 | F_profile | S52511_+/-1Hz | [6 empty] | 231 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
661 | F_profile | S52511_F_db | [6 empty] | 234 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
662 | F_profile | S52511_+/-1Hz | [6 empty] | 234 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
663 | F_profile | S52511_F_db | [6 empty] | 235 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
664 | F_profile | S52511_+/-1Hz | [6 empty] | 235 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
665 | F_profile | S52511_F_db | [6 empty] | 236 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
666 | F_profile | S52511_+/-1Hz | [6 empty] | 236 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
667 | F_profile | S52511_F_db | [6 empty] | 239 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
668 | F_profile | S52511_+/-1Hz | [6 empty] | 239 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
669 | F_profile | S52511_F_db | [6 empty] | 240 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
670 | F_profile | S52511_+/-1Hz | [6 empty] | 240 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52511
671 | F_profile | S52511_F_db | [6 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
672 | F_profile | S52511_+/-1Hz | [6 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
673 | F_profile | S52511_F_db | [6 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
674 | F_profile | S52511_+/-1Hz | [6 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
675 | F_profile | S52511_F_db | [6 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
676 | F_profile | S52511_+/-1Hz | [6 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
677 | F_profile | S52511_F_db | [6 empty] | 246 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
678 | F_profile | S52511_+/-1Hz | [6 empty] | 246 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
679 | F_profile | S52511_F_db | [6 empty] | 249 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
680 | F_profile | S52511_+/-1Hz | [6 empty] | 249 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
681 | F_profile | S52511_F_db | [6 empty] | 250 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
682 | F_profile | S52511_+/-1Hz | [6 empty] | 250 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
683 | F_profile | S52511_F_db | [6 empty] | 251 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
684 | F_profile | S52511_+/-1Hz | [6 empty] | 251 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
685 | F_profile | S52511_F_db | [6 empty] | 254 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
686 | F_profile | S52511_+/-1Hz | [6 empty] | 254 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
687 | F_profile | S52511_F_db | [6 empty] | 255 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
688 | F_profile | S52511_+/-1Hz | [6 empty] | 255 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
689 | F_profile | S52511_F_db | [6 empty] | 256 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
690 | F_profile | S52511_+/-1Hz | [6 empty] | 256 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
691 | F_profile | S52511_F_db | [6 empty] | 259 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
692 | F_profile | S52511_+/-1Hz | [6 empty] | 259 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
693 | F_profile | S52511_F_db | [6 empty] | 260 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
694 | F_profile | S52511_+/-1Hz | [6 empty] | 260 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
695 | F_profile | S52511_F_db | [6 empty] | 261 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
696 | F_profile | S52511_+/-1Hz | [6 empty] | 261 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
697 | F_profile | S52511_F_db | [6 empty] | 264 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
698 | F_profile | S52511_+/-1Hz | [6 empty] | 264 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
699 | F_profile | S52511_F_db | [6 empty] | 265 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
700 | F_profile | S52511_+/-1Hz | [6 empty] | 265 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
701 | F_profile | S52511_F_db | [6 empty] | 266 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
702 | F_profile | S52511_+/-1Hz | [6 empty] | 266 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
703 | F_profile | S52511_F_db | [6 empty] | 269 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
704 | F_profile | S52511_+/-1Hz | [6 empty] | 269 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
705 | F_profile | S52511_F_db | [6 empty] | 270 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
706 | F_profile | S52511_+/-1Hz | [6 empty] | 270 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
707 | F_profile | S52511_F_db | [6 empty] | 271 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
708 | F_profile | S52511_+/-1Hz | [6 empty] | 271 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
709 | F_profile | S52511_F_db | [6 empty] | 274 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
710 | F_profile | S52511_+/-1Hz | [6 empty] | 274 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
711 | F_profile | S52511_F_db | [6 empty] | 275 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
712 | F_profile | S52511_+/-1Hz | [6 empty] | 275 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
713 | F_profile | S52511_F_db | [6 empty] | 276 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
714 | F_profile | S52511_+/-1Hz | [6 empty] | 276 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
715 | F_profile | S52511_F_db | [6 empty] | 279 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
716 | F_profile | S52511_+/-1Hz | [6 empty] | 279 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
717 | F_profile | S52511_F_db | [6 empty] | 280 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
718 | F_profile | S52511_+/-1Hz | [6 empty] | 280 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52511
719 | F_profile | S52511_F_db | [6 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
720 | F_profile | S52511_+/-1Hz | [6 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
721 | F_profile | S52511_F_db | [6 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
722 | F_profile | S52511_+/-1Hz | [6 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
723 | F_profile | S52511_F_db | [6 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
724 | F_profile | S52511_+/-1Hz | [6 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
725 | F_profile | S52511_F_db | [6 empty] | 286 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
726 | F_profile | S52511_+/-1Hz | [6 empty] | 286 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
727 | F_profile | S52511_F_db | [6 empty] | 289 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
728 | F_profile | S52511_+/-1Hz | [6 empty] | 289 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
729 | F_profile | S52511_F_db | [6 empty] | 290 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
730 | F_profile | S52511_+/-1Hz | [6 empty] | 290 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
731 | F_profile | S52511_F_db | [6 empty] | 291 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
732 | F_profile | S52511_+/-1Hz | [6 empty] | 291 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
733 | F_profile | S52511_F_db | [6 empty] | 294 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
734 | F_profile | S52511_+/-1Hz | [6 empty] | 294 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
735 | F_profile | S52511_F_db | [6 empty] | 295 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
736 | F_profile | S52511_+/-1Hz | [6 empty] | 295 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
737 | F_profile | S52511_F_db | [6 empty] | 296 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
738 | F_profile | S52511_+/-1Hz | [6 empty] | 296 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
739 | F_profile | S52511_F_db | [6 empty] | 299 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
740 | F_profile | S52511_+/-1Hz | [6 empty] | 299 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
741 | F_profile | S52511_F_db | [6 empty] | 300 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
742 | F_profile | S52511_+/-1Hz | [6 empty] | 300 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
743 | F_profile | S52511_F_db | [6 empty] | 301 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
744 | F_profile | S52511_+/-1Hz | [6 empty] | 301 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
745 | F_profile | S52511_F_db | [6 empty] | 304 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
746 | F_profile | S52511_+/-1Hz | [6 empty] | 304 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
747 | F_profile | S52511_F_db | [6 empty] | 305 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
748 | F_profile | S52511_+/-1Hz | [6 empty] | 305 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
749 | F_profile | S52511_F_db | [6 empty] | 306 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
750 | F_profile | S52511_+/-1Hz | [6 empty] | 306 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
751 | F_profile | S52511_F_db | [6 empty] | 309 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
752 | F_profile | S52511_+/-1Hz | [6 empty] | 309 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
753 | F_profile | S52511_F_db | [6 empty] | 310 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
754 | F_profile | S52511_+/-1Hz | [6 empty] | 310 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
755 | F_profile | S52511_F_db | [6 empty] | 311 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
756 | F_profile | S52511_+/-1Hz | [6 empty] | 311 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
757 | F_profile | S52511_F_db | [6 empty] | 314 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
758 | F_profile | S52511_+/-1Hz | [6 empty] | 314 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
759 | F_profile | S52511_F_db | [6 empty] | 315 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
760 | F_profile | S52511_+/-1Hz | [6 empty] | 315 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
761 | F_profile | S52511_F_db | [6 empty] | 316 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
762 | F_profile | S52511_+/-1Hz | [6 empty] | 316 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
763 | F_profile | S52511_F_db | [6 empty] | 319 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
764 | F_profile | S52511_+/-1Hz | [6 empty] | 319 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
765 | F_profile | S52511_F_db | [6 empty] | 320 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
766 | F_profile | S52511_+/-1Hz | [6 empty] | 320 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52511
767 | V_stp_profile | S52513_V0+/-5% | 5 | [5 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
768 | V_stp_profile | S52513_Vmax-2.5%/+5% | 12.5 | [5 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
769 | V_stp_profile | S52513_Vmin+2.5%/-5% | 12.5 | [5 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
770 | V_stp_profile | S52513_V0+/-5% | 5 | [5 empty] | 206 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
771 | V_stp_profile | S52513_Vmax-2.5%/+5% | 12.5 | [5 empty] | 209 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
772 | V_stp_profile | S52513_Vmin+2.5%/-5% | 12.5 | [5 empty] | 210 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
773 | V_stp_profile | S52513_V0+/-5% | 5 | [5 empty] | 211 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
774 | V_stp_profile | S52513_Vmax-2.5%/+5% | 12.5 | [5 empty] | 214 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
775 | V_stp_profile | S52513_Vmin+2.5%/-5% | 12.5 | [5 empty] | 215 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
776 | V_stp_profile | S52513_V0+/-5% | 5 | [5 empty] | 216 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
777 | V_stp_profile | S52513_Vmax-2.5%/+5% | 12.5 | [5 empty] | 219 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
778 | V_stp_profile | S52513_Vmin+2.5%/-5% | 12.5 | [5 empty] | 220 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
779 | V_stp_profile | S52513_V0+/-5% | 5 | [5 empty] | 221 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
780 | V_stp_profile | S52513_Vmax-2.5%/+5% | 12.5 | [5 empty] | 224 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
781 | V_stp_profile | S52513_Vmin+2.5%/-5% | 12.5 | [5 empty] | 225 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
782 | V_stp_profile | S52513_V0+/-5% | 5 | [5 empty] | 226 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
783 | V_stp_profile | S52513_Vmax-2.5%/+5% | 12.5 | [5 empty] | 229 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
784 | V_stp_profile | S52513_Vmin+2.5%/-5% | 12.5 | [5 empty] | 230 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
785 | V_stp_profile | S52513_V0+/-5% | 5 | [5 empty] | 231 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
786 | V_stp_profile | S52513_Vmax-2.5%/+5% | 12.5 | [5 empty] | 234 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
787 | V_stp_profile | S52513_Vmin+2.5%/-5% | 12.5 | [5 empty] | 235 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
788 | V_stp_profile | S52513_V0+/-5% | 5 | [5 empty] | 236 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
789 | V_stp_profile | S52513_Vmax-2.5%/+5% | 12.5 | [5 empty] | 239 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
790 | V_stp_profile | S52513_Vmin+2.5%/-5% | 12.5 | [5 empty] | 240 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
791 | Q_stp_profile | S52513_Q0+/-15 | 5 | [5 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
792 | Q_stp_profile | S52513_Qmax-10/+20 | 12.5 | [5 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
793 | Q_stp_profile | S52513_Qmin+10/-20 | 12.5 | [5 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
794 | Q_stp_profile | S52513_Q0+/-15 | 5 | [5 empty] | 246 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
795 | Q_stp_profile | S52513_Qmax-10/+20 | 12.5 | [5 empty] | 249 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
796 | Q_stp_profile | S52513_Qmin+10/-20 | 12.5 | [5 empty] | 250 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
797 | Q_stp_profile | S52513_Q0+/-15 | 5 | [5 empty] | 251 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
798 | Q_stp_profile | S52513_Qmax-10/+20 | 12.5 | [5 empty] | 254 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
799 | Q_stp_profile | S52513_Qmin+10/-20 | 12.5 | [5 empty] | 255 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
800 | Q_stp_profile | S52513_Q0+/-15 | 5 | [5 empty] | 256 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
801 | Q_stp_profile | S52513_Qmax-10/+20 | 12.5 | [5 empty] | 259 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
802 | Q_stp_profile | S52513_Qmin+10/-20 | 12.5 | [5 empty] | 260 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
803 | Q_stp_profile | S52513_Q0+/-15 | 5 | [5 empty] | 261 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
804 | Q_stp_profile | S52513_Qmax-10/+20 | 12.5 | [5 empty] | 264 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
805 | Q_stp_profile | S52513_Qmin+10/-20 | 12.5 | [5 empty] | 265 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
806 | Q_stp_profile | S52513_Q0+/-15 | 5 | [5 empty] | 266 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
807 | Q_stp_profile | S52513_Qmax-10/+20 | 12.5 | [5 empty] | 269 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
808 | Q_stp_profile | S52513_Qmin+10/-20 | 12.5 | [5 empty] | 270 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
809 | Q_stp_profile | S52513_Q0+/-15 | 5 | [5 empty] | 271 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
810 | Q_stp_profile | S52513_Qmax-10/+20 | 12.5 | [5 empty] | 274 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
811 | Q_stp_profile | S52513_Qmin+10/-20 | 12.5 | [5 empty] | 275 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
812 | Q_stp_profile | S52513_Q0+/-15 | 5 | [5 empty] | 276 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
813 | Q_stp_profile | S52513_Qmax-10/+20 | 12.5 | [5 empty] | 279 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
814 | Q_stp_profile | S52513_Qmin+10/-20 | 12.5 | [5 empty] | 280 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
815 | PF_stp_profile | S52513_PF0+/-0.02 | 5 | [5 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
816 | PF_stp_profile | S52513_PFMax-0.01/+0.03 | 12.5 | [5 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
817 | PF_stp_profile | S52513_PFMin+0.01/-0.03 | 12.5 | [5 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
818 | PF_stp_profile | S52513_PF0+/-0.02 | 5 | [5 empty] | 286 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
819 | PF_stp_profile | S52513_PFMax-0.01/+0.03 | 12.5 | [5 empty] | 289 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
820 | PF_stp_profile | S52513_PFMin+0.01/-0.03 | 12.5 | [5 empty] | 290 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
821 | PF_stp_profile | S52513_PF0+/-0.02 | 5 | [5 empty] | 291 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
822 | PF_stp_profile | S52513_PFMax-0.01/+0.03 | 12.5 | [5 empty] | 294 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
823 | PF_stp_profile | S52513_PFMin+0.01/-0.03 | 12.5 | [5 empty] | 295 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
824 | PF_stp_profile | S52513_PF0+/-0.02 | 5 | [5 empty] | 296 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
825 | PF_stp_profile | S52513_PFMax-0.01/+0.03 | 12.5 | [5 empty] | 299 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
826 | PF_stp_profile | S52513_PFMin+0.01/-0.03 | 12.5 | [5 empty] | 300 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
827 | PF_stp_profile | S52513_PF0+/-0.02 | 5 | [5 empty] | 301 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
828 | PF_stp_profile | S52513_PFMax-0.01/+0.03 | 12.5 | [5 empty] | 304 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
829 | PF_stp_profile | S52513_PFMin+0.01/-0.03 | 12.5 | [5 empty] | 305 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
830 | PF_stp_profile | S52513_PF0+/-0.02 | 5 | [5 empty] | 306 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
831 | PF_stp_profile | S52513_PFMax-0.01/+0.03 | 12.5 | [5 empty] | 309 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
832 | PF_stp_profile | S52513_PFMin+0.01/-0.03 | 12.5 | [5 empty] | 310 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
833 | PF_stp_profile | S52513_PF0+/-0.02 | 5 | [5 empty] | 311 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
834 | PF_stp_profile | S52513_PFMax-0.01/+0.03 | 12.5 | [5 empty] | 314 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
835 | PF_stp_profile | S52513_PFMin+0.01/-0.03 | 12.5 | [5 empty] | 315 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
836 | PF_stp_profile | S52513_PF0+/-0.02 | 5 | [5 empty] | 316 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
837 | PF_stp_profile | S52513_PFMax-0.01/+0.03 | 12.5 | [5 empty] | 319 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
838 | PF_stp_profile | S52513_PFMin+0.01/-0.03 | 12.5 | [5 empty] | 320 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
839 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
840 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
841 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
842 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 206 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
843 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 209 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
844 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 210 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
845 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 211 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
846 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 214 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
847 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 215 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
848 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 216 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
849 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 219 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
850 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 220 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
851 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 221 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
852 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 224 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
853 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 225 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
854 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 226 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
855 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 229 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
856 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 230 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
857 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 231 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
858 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 234 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
859 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 235 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
860 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 236 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
861 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 239 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
862 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 240 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52513
863 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
864 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
865 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
866 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 246 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
867 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 249 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
868 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 250 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
869 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 251 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
870 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 254 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
871 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 255 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
872 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 256 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
873 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 259 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
874 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 260 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
875 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 261 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
876 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 264 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
877 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 265 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
878 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 266 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
879 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 269 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
880 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 270 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
881 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 271 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
882 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 274 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
883 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 275 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
884 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 276 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
885 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 279 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
886 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 280 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S52513
887 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
888 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
889 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
890 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 286 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
891 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 289 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
892 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 290 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
893 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 291 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
894 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 294 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
895 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 295 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
896 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 296 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
897 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 299 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
898 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 300 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
899 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 301 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
900 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 304 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
901 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 305 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
902 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 306 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
903 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 309 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
904 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 310 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
905 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 311 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
906 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 314 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
907 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 315 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
908 | V_profile | S52513_V_STEP_+/-5% | 5 | [5 empty] | 316 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
909 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 319 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
910 | V_profile | S52513_V_STEP_+/-5% | 12.5 | [5 empty] | 320 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S52513
911 | P_stp_profile | S52514_-/+50% | [6 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
912 | P_stp_profile | S52514_-/+50% | [6 empty] | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
913 | P_stp_profile | S52514_-/+50% | [6 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
914 | P_stp_profile | S52514_-/+50% | [6 empty] | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
915 | P_stp_profile | S52514_-/+50% | [6 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
916 | P_stp_profile | S52514_-/+50% | [6 empty] | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
917 | P_stp_profile | S52514_-/+50% | [6 empty] | 206 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
918 | P_stp_profile | S52514_-/+50% | [6 empty] | 206 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
919 | P_stp_profile | S52514_-/+50% | [6 empty] | 209 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
920 | P_stp_profile | S52514_-/+50% | [6 empty] | 209 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
921 | P_stp_profile | S52514_-/+50% | [6 empty] | 210 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
922 | P_stp_profile | S52514_-/+50% | [6 empty] | 210 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
923 | P_stp_profile | S52514_-/+50% | [6 empty] | 211 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
924 | P_stp_profile | S52514_-/+50% | [6 empty] | 211 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
925 | P_stp_profile | S52514_-/+50% | [6 empty] | 214 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
926 | P_stp_profile | S52514_-/+50% | [6 empty] | 214 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
927 | P_stp_profile | S52514_-/+50% | [6 empty] | 215 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
928 | P_stp_profile | S52514_-/+50% | [6 empty] | 215 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
929 | P_stp_profile | S52514_-/+50% | [6 empty] | 216 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
930 | P_stp_profile | S52514_-/+50% | [6 empty] | 216 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
931 | P_stp_profile | S52514_-/+50% | [6 empty] | 219 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
932 | P_stp_profile | S52514_-/+50% | [6 empty] | 219 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
933 | P_stp_profile | S52514_-/+50% | [6 empty] | 220 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
934 | P_stp_profile | S52514_-/+50% | [6 empty] | 220 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
935 | P_stp_profile | S52514_-/+50% | [6 empty] | 221 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
936 | P_stp_profile | S52514_-/+50% | [6 empty] | 221 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
937 | P_stp_profile | S52514_-/+50% | [6 empty] | 224 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
938 | P_stp_profile | S52514_-/+50% | [6 empty] | 224 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
939 | P_stp_profile | S52514_-/+50% | [6 empty] | 225 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
940 | P_stp_profile | S52514_-/+50% | [6 empty] | 225 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
941 | P_stp_profile | S52514_-/+50% | [6 empty] | 226 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
942 | P_stp_profile | S52514_-/+50% | [6 empty] | 226 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
943 | P_stp_profile | S52514_-/+50% | [6 empty] | 229 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
944 | P_stp_profile | S52514_-/+50% | [6 empty] | 229 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
945 | P_stp_profile | S52514_-/+50% | [6 empty] | 230 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
946 | P_stp_profile | S52514_-/+50% | [6 empty] | 230 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
947 | P_stp_profile | S52514_-/+50% | [6 empty] | 231 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
948 | P_stp_profile | S52514_-/+50% | [6 empty] | 231 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
949 | P_stp_profile | S52514_-/+50% | [6 empty] | 234 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
950 | P_stp_profile | S52514_-/+50% | [6 empty] | 234 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
951 | P_stp_profile | S52514_-/+50% | [6 empty] | 235 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
952 | P_stp_profile | S52514_-/+50% | [6 empty] | 235 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
953 | P_stp_profile | S52514_-/+50% | [6 empty] | 236 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
954 | P_stp_profile | S52514_-/+50% | [6 empty] | 236 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
955 | P_stp_profile | S52514_-/+50% | [6 empty] | 239 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
956 | P_stp_profile | S52514_-/+50% | [6 empty] | 239 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
957 | P_stp_profile | S52514_-/+50% | [6 empty] | 240 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
958 | P_stp_profile | S52514_-/+50% | [6 empty] | 240 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52514
959 | V_profile | LowSCR_V0-/+5% | [6 empty] | 311 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | S52515
960 | V_profile | LowSCR_V0-5% | [6 empty] | 311 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | S52515
961 | V_profile | LowSCR_V0-10% | [6 empty] | 311 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | S52515
962 | ANG_profile | MAT_ANG_STEP+/-20deg | [6 empty] | 11 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52516
963 | ANG_profile | MAT_ANG_STEP+/-20deg | [6 empty] | 1 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S52516
964 | V_stp_profile | S52513_V0+/-5% | [6 empty] | 1 | 2 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
965 | V_stp_profile | S52513_V0+/-5% | [6 empty] | 11 | 2 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
966 | Q_stp_profile | S52513_Q0+/-15 | [6 empty] | 131 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | Benchmarking
967 | Q_stp_profile | S52513_Q0+/-15 | [6 empty] | 141 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | Benchmarking
968 | PF_stp_profile | S52513_PF0+/-0.02 | [6 empty] | 171 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | Benchmarking
969 | PF_stp_profile | S52513_PF0+/-0.02 | [6 empty] | 181 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | Benchmarking
970 | V_profile | V_STEP_+/-5% | [6 empty] | 1 | 2 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
971 | V_profile | V_STEP_+/-5% | [6 empty] | 11 | 2 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
972 | P_stp_profile | S52514_-/+50% | [6 empty] | 1 | 2 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
973 | P_stp_profile | S52514_-/+50% | [6 empty] | 11 | 2 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
974 | F_profile | S52511_+/-1Hz | [6 empty] | 1 | 2 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
975 | F_profile | S52511_+/-1Hz | [6 empty] | 11 | 2 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
976 | ANG_profile | MAT_ANG_STEP | [6 empty] | 1 | 2 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
977 | ANG_profile | MAT_ANG_STEP | [6 empty] | 11 | 2 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
978 | Auxiliary_profile | AVAIL_P_-20% | [6 empty] | 1 | 2 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
979 | Auxiliary_profile | AVAIL_P_-20% | [6 empty] | 11 | 2 | 1 | 0.2 | yes | yes |  | V control mode | Benchmarking
980 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 211 | 2 | 1 | 0.2 | yes | yes | 153 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsldbgBESSonly
981 | V_stp_profile | MAT_VREF_STEP_Fig2 | [6 empty] | 201 | 2 | 1 | 0.2 | yes | yes | 153 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsldbgBESSonly
982 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 211 | 2 | 1 | 0.2 | yes | yes | 159 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsldbgBESSonly
983 | V_profile | MAT_V_STEP_Fig3 | [6 empty] | 201 | 2 | 1 | 0.2 | yes | yes | 160 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsldbgBESSonly
984 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 241 | 2 | 1 | 0.2 | yes | yes | 165 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsldbgBESSonly
985 | Q_stp_profile | MAT_QREF_STEP_Fig4 | [6 empty] | 231 | 2 | 1 | 0.2 | yes | yes | 165 | Voltage reference step change [PSS®E and PSCAD/EMTDC models] | DMATsldbgBESSonly
986 | P_stp_profile | MAT_P_STEP_Fig5 | [6 empty] | 211 | 2 | 1 | 0.2 | yes | yes | 169 | Active Power Controller Reference step change [PSS®E and PSCAD/EMTDC models] | DMATsldbgBESSonly
987 | P_stp_profile | MAT_P_STEP_Fig5 | [6 empty] | 201 | 2 | 1 | 0.2 | yes | yes | 169 | Active Power Controller Reference step change [PSS®E and PSCAD/EMTDC models] | DMATsldbgBESSonly
988 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 211 | 2 | 1 | 0.2 | yes | yes | 197 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMATsldbgBESSonly
989 | ANG_profile | MAT_ANG_STEP+/-40deg | [6 empty] | 201 | 2 | 1 | 0.2 | yes | yes | 197 | Grid voltage phase angle change – response test [PSS®E and PSCAD/EMTDC models] | DMATsldbgBESSonly
990 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 311 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCR
991 | V_stp_profile | LowSCR_V0-5% | [6 empty] | 311 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCR
992 | V_stp_profile | LowSCR_V0-10% | [6 empty] | 311 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCR
993 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 325 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
994 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 326 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
995 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 327 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
996 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 328 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
997 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 329 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
998 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 330 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
999 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 331 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
1000 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 332 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
1001 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 333 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
1002 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 334 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
1003 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 335 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
1004 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 336 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
1005 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 337 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
1006 | V_stp_profile | LowSCR_V0-/+5% | [6 empty] | 324 | 2 | 1 | 0.2 | yes | no |  | Low SCR test Table 3 Appendix B SSIAG [PSCAD/EMTDC models] | lowSCRdbg
1007 | P_stp_profile | S52514_AEMO | [6 empty] | 338 | 0 | 1 | 0.2 | no | yes |  | V control mode - PSSE_Model - Item 23 | S52514_AEMO
1008 | P_stp_profile | S52514_AEMO | [6 empty] | 339 | 0 | 1 | 0.2 | no | no |  | V control mode | S52514_AEMO
1009 | P_stp_profile | S52514_AEMO | [6 empty] | 340 | 0 | 1 | 0.2 | no | no |  | V control mode | S52514_AEMO
1010 | F_profile | S52511_AEMO | [6 empty] | 341 | 0 | 1 | 0.2 | no | no |  | V control mode | S52511_AEMO
1011 | F_profile | S52511_AEMO | [6 empty] | 342 | 0 | 1 | 0.2 | no | no |  | V control mode | S52511_AEMO
1012 | F_profile | S52511_AEMO | [6 empty] | 340 | 0 | 1 | 0.2 | no | no |  | V control mode | S52511_AEMO
1013 | P_stp_profile | S52514_AEMO_2 | [6 empty] | 343 | 0 | 1 | 0.2 | no | no |  | V control mode | S52514_AEMO2
1014 | V_profile | S5254_090_AEMO | [6 empty] | 346 | 0 | 1 | 0.2 | no | yes |  | AEMO Figure 2 - PSSE model Item 16, 17 | S5254_AEMO
1015 | V_profile | S5254_080_AEMO | [6 empty] | 347 | 0 | 1 | 0.2 | no | yes |  | AEMO Figure 4 - PSSE model Item 18 | S5254_AEMO
1016 | V_profile | S5254_080_AEMO | [6 empty] | 348 | 0 | 1 | 0.2 | no | yes |  | AEMO Figure 4 - PSSE model Item 18 | S5254_AEMO
1017 | V_profile | S5254_LVRT_Qmax | [6 empty] | 355 | 0 | 1 | 0.2 | no | yes |  | V control mode Item 30 PSSE Model | S5254_Transgrid
1018 | V_profile | S5254_HVRT_Qmax | [6 empty] | 355 | 0 | 1 | 0.2 | no | yes |  | V control mode Item 30 PSSE Model | S5254_Transgrid
1019 | V_profile | S5254_LVRT_Qmin | [6 empty] | 356 | 0 | 1 | 0.2 | no | yes |  | V control mode Item 30 PSSE Model | S5254_Transgrid
1020 | V_profile | S5254_HVRT_Qmin | [6 empty] | 356 | 0 | 1 | 0.2 | no | yes |  | V control mode Item 30 PSSE Model | S5254_Transgrid
1021 | V_profile | S5254_LVRT_Qmax | [6 empty] | 357 | 0 | 1 | 0.2 | no | yes |  | V control mode Item 30 PSSE Model | S5254_Transgrid
1022 | V_profile | S5254_HVRT_Qmax | [6 empty] | 357 | 0 | 1 | 0.2 | no | yes |  | V control mode Item 30 PSSE Model | S5254_Transgrid
1023 | V_profile | S5254_LVRT_Qmin | [6 empty] | 358 | 0 | 1 | 0.2 | no | yes |  | V control mode Item 30 PSSE Model | S5254_Transgrid
1024 | V_profile | S5254_HVRT_Qmin | [6 empty] | 358 | 0 | 1 | 0.2 | no | yes |  | V control mode Item 30 PSSE Model | S5254_Transgrid
1025 | V_profile | S5254_LVRT_Qmax | [6 empty] | 359 | 0 | 1 | 0.2 | no | yes |  | V control mode Item 30 PSSE Model | S5254_Transgrid
1026 | V_profile | S5254_HVRT_Qmax | [6 empty] | 359 | 0 | 1 | 0.2 | no | yes |  | V control mode Item 30 PSSE Model | S5254_Transgrid
1027 | V_profile | S5254_LVRT_Qmin | [6 empty] | 360 | 0 | 1 | 0.2 | no | yes |  | V control mode Item 30 PSSE Model | S5254_Transgrid
1028 | V_profile | S5254_HVRT_Qmin | [6 empty] | 360 | 0 | 1 | 0.2 | no | yes |  | V control mode Item 30 PSSE Model | S5254_Transgrid
1029 | V_profile | FLAT_RUN_12 | [6 empty] | 371 | 2 | 1 | 0.2 | yes | no | 0.4 | PSCAD_Model - Item 9, Figure 8 | Flatrun_TG
Note on D2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Event time: use to calculate the rise and settling time in S52513 -> should be aligned with the setpoint or disturbance profile.
Note on A3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: review
Note on A48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: to be revisited - available P vs. setpoint --> how to adjust in model?
Note on J56: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: here the available energy from solar needs to be limited --> not sure if model can do it. And if so, how.
Note on J78: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not fully correct, MAT asks for P=0.5, which is not available in the setpoints at the moment
Note on J86: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not fully correct, MAT asks for P=0.5, which is not available in the setpoints at the moment
Note on J94: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not fully correct, MAT asks for P=0.5, which is not available in the setpoints at the moment
Note on J102: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not fully correct, MAT asks for P=0.5, which is not available in the setpoints at the moment
Note on J110: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not fully correct, MAT asks for P=0.5, which is not available in the setpoints at the moment
Note on N458: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Exclude V control mode
Note on Q1031: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Need to update the Vinf = 1.1pu so Q will be equal to Qmin. Also change the GridSource mode to SourceNormal

## TOV
Overvoltage tests. Overvoltage condition is created by connecting a suitably-sized capacitor at the Connection point. The calculation is designed to take into account the power flows at POC
PSSE-specific settings
CaseNr | Test Type | time | Fduration | Capacity(F) | Vresidual | SCL_post | X_R_post | setpoint ID | init_help | TimeStep | AccFactor | run in PSCAD? | run in PSS/E? | Comment/Corresponding DMAT case | test group | simulation batch
1 | TOV | 5 | 0.9 |  | 1.15 |  |  | 51 | 0 | 1 | 0.2 | no | no | 131 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
2 | TOV | 5 | 0.9 |  | 1.15 |  |  | 53 | 0 | 1 | 0.2 | no | no | 132 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
3 | TOV | 5 | 0.9 |  | 1.15 |  |  | 52 | 0 | 1 | 0.2 | no | no | 133 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
4 | TOV | 5 | 0.9 |  | 1.15 |  |  | 31 | 0 | 1 | 0.2 | no | no | 134 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
5 | TOV | 5 | 0.9 |  | 1.15 |  |  | 43 | 0 | 1 | 0.2 | no | no | 135 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
6 | TOV | 5 | 0.9 |  | 1.15 |  |  | 42 | 0 | 1 | 0.2 | no | no | 136 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
7 | TOV | 5 | 0.9 |  | 1.15 |  |  | 11 | 0 | 1 | 0.2 | yes | yes | 137 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMATsl
8 | TOV | 5 | 0.9 |  | 1.15 |  |  | 13 | 0 | 1 | 0.2 | no | no | 138 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
9 | TOV | 5 | 0.9 |  | 1.15 |  |  | 12 | 0 | 1 | 0.2 | no | no | 139 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
10 | TOV | 5 | 0.9 |  | 1.15 |  |  | 1 | 0 | 1 | 0.2 | yes | yes | 137 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMATsl
11 | TOV | 5 | 0.9 |  | 1.15 |  |  | 3 | 0 | 1 | 0.2 | no | no | 138 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
12 | TOV | 5 | 0.9 |  | 1.15 |  |  | 2 | 0 | 1 | 0.2 | no | no | 139 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
13 | TOV | 5 | 0.1 |  | 1.2 |  |  | 51 | 0 | 1 | 0.2 | no | no | 140 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
14 | TOV | 5 | 0.1 |  | 1.2 |  |  | 53 | 0 | 1 | 0.2 | no | no | 141 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
15 | TOV | 5 | 0.1 |  | 1.2 |  |  | 52 | 0 | 1 | 0.2 | no | no | 142 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
16 | TOV | 5 | 0.1 |  | 1.2 |  |  | 31 | 0 | 1 | 0.2 | no | no | 143 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
17 | TOV | 5 | 0.1 |  | 1.2 |  |  | 43 | 0 | 1 | 0.2 | no | no | 144 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
18 | TOV | 5 | 0.1 |  | 1.2 |  |  | 42 | 0 | 1 | 0.2 | no | no | 145 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
19 | TOV | 5 | 0.1 |  | 1.2 |  |  | 11 | 0 | 1 | 0.2 | yes | yes | 146 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMATsl
20 | TOV | 5 | 0.1 |  | 1.2 |  |  | 13 | 0 | 1 | 0.2 | no | no | 147 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
21 | TOV | 5 | 0.1 |  | 1.2 |  |  | 12 | 0 | 1 | 0.2 | no | no | 148 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
22 | TOV | 5 | 0.1 |  | 1.2 |  |  | 1 | 0 | 1 | 0.2 | yes | yes | 146 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMATsl
23 | TOV | 5 | 0.1 |  | 1.2 |  |  | 3 | 0 | 1 | 0.2 | no | no | 147 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
24 | TOV | 5 | 0.1 |  | 1.2 |  |  | 2 | 0 | 1 | 0.2 | no | no | 148 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | DMAT
25 | TOV | 5 | 20 |  | 1.2 |  |  | 1 | 0 | 1 | 0.2 | no | no | 137 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | Benchmarking-5.3.9
26 | TOV | 5 | 2 |  | 1.25 |  |  | 1 | 0 | 1 | 0.2 | no | no | 136 | Temporary Over-Voltage (TOV) Test [PSS®E and PSCAD/EMTDC models] | Benchmarking-5.3.9
27 | TOV | 5 | 0.34 |  | 1.1 |  |  | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255dbg
28 | TOV | 5 | 0.34 |  | 1.2 |  |  | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255dbg
29 | TOV | 5 | 0.34 |  | 1.3 |  |  | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255dbg
30 | TOV | 5 | 0.34 |  | 1.4 |  |  | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255dbg
31 | TOV | 5 | 0.34 |  | 1.5 |  |  | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255dbg
32 | TOV | 5 | 0.34 |  | 1.6 |  |  | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255dbg
33 | TOV | 5 | 0.34 |  | 1.7 |  |  | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255dbg
34 | TOV | 5 | 0.34 |  | 1.8 |  |  | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255dbg
35 | TOV | 5 | 0.34 |  | 1.9 |  |  | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255dbg
36 | TOV | 5 | 0.34 |  | 2 |  |  | 11 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255dbg
37 | TOV | 5 | 5 |  | 1.1 |  |  | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
38 | TOV | 5 | 5 |  | 1.15 |  |  | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
39 | TOV | 5 | 5 |  | 1.2 |  |  | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
40 | TOV | 5 | 5 |  | 1.25 |  |  | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
41 | TOV | 5 | 5 |  | 1.3 |  |  | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
42 | TOV | 5 | 5 |  | 1.35 |  |  | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
43 | TOV | 5 | 5 |  | 1.4 |  |  | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
44 | TOV | 5 | 5 |  | 1.45 |  |  | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
45 | TOV | 5 | 5 |  | 1.5 |  |  | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
46 | TOV | 5 | 5 |  | 1.55 |  |  | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
47 | TOV | 5 | 5 |  | 1.6 |  |  | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
48 | TOV | 5 | 5 |  | 1.65 |  |  | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
49 | TOV | 5 | 5 |  | 1.7 |  |  | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
50 | TOV | 5 | 5 |  | 1.75 |  |  | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
51 | TOV | 5 | 5 |  | 1.8 |  |  | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
52 | TOV | 5 | 5 |  | 1.85 |  |  | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
53 | TOV | 5 | 5 |  | 1.9 |  |  | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
54 | TOV | 5 | 5 |  | 1.95 |  |  | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
55 | TOV | 5 | 5 |  | 2 |  |  | 301 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255Iq
56 | TOV | 5 | 5 |  | 1.1 |  |  | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
57 | TOV | 5 | 5 |  | 1.15 |  |  | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
58 | TOV | 5 | 5 |  | 1.2 |  |  | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
59 | TOV | 5 | 5 |  | 1.25 |  |  | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
60 | TOV | 5 | 5 |  | 1.3 |  |  | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
61 | TOV | 5 | 5 |  | 1.35 |  |  | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
62 | TOV | 5 | 5 |  | 1.4 |  |  | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
63 | TOV | 5 | 5 |  | 1.45 |  |  | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
64 | TOV | 5 | 5 |  | 1.5 |  |  | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
65 | TOV | 5 | 5 |  | 1.55 |  |  | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
66 | TOV | 5 | 5 |  | 1.6 |  |  | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
67 | TOV | 5 | 5 |  | 1.65 |  |  | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
68 | TOV | 5 | 5 |  | 1.7 |  |  | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
69 | TOV | 5 | 5 |  | 1.75 |  |  | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
70 | TOV | 5 | 5 |  | 1.8 |  |  | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
71 | TOV | 5 | 5 |  | 1.85 |  |  | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
72 | TOV | 5 | 5 |  | 1.9 |  |  | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
73 | TOV | 5 | 5 |  | 1.95 |  |  | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
74 | TOV | 5 | 5 |  | 2 |  |  | 304 | 0 | 1 | 0.2 | yes | yes |  | Iq rise/settling time and P recovery assessment | S5255IqQmax
75 | TOV | 5 | 5 |  | 1.1 |  |  | 305 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255IqQmin
76 | TOV | 5 | 5 |  | 1.15 |  |  | 305 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255IqQmin
77 | TOV | 5 | 5 |  | 1.2 |  |  | 305 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255IqQmin
78 | TOV | 5 | 5 |  | 1.25 |  |  | 305 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255IqQmin
79 | TOV | 5 | 5 |  | 1.3 |  |  | 305 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255IqQmin
80 | TOV | 5 | 5 |  | 1.35 |  |  | 305 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255IqQmin
81 | TOV | 5 | 5 |  | 1.4 |  |  | 305 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255IqQmin
82 | TOV | 5 | 5 |  | 1.45 |  |  | 305 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255IqQmin
83 | TOV | 5 | 5 |  | 1.5 |  |  | 305 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255IqQmin
84 | TOV | 5 | 5 |  | 1.55 |  |  | 305 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255IqQmin
85 | TOV | 5 | 5 |  | 1.6 |  |  | 305 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255IqQmin
86 | TOV | 5 | 5 |  | 1.65 |  |  | 305 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255IqQmin
87 | TOV | 5 | 5 |  | 1.7 |  |  | 305 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255IqQmin
88 | TOV | 5 | 5 |  | 1.75 |  |  | 305 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255IqQmin
89 | TOV | 5 | 5 |  | 1.8 |  |  | 305 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255IqQmin
90 | TOV | 5 | 5 |  | 1.85 |  |  | 305 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255IqQmin
91 | TOV | 5 | 5 |  | 1.9 |  |  | 305 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255IqQmin
92 | TOV | 5 | 5 |  | 1.95 |  |  | 305 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255IqQmin
93 | TOV | 5 | 5 |  | 2 |  |  | 305 | 0 | 1 | 0.2 | yes | yes |  | V control mode | S5255IqQmin
94 | TOV | 5 | 0.34 |  | 1.05 |  |  | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
95 | TOV | 5 | 0.34 |  | 1.1 |  |  | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
96 | TOV | 5 | 0.34 |  | 1.15 |  |  | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
97 | TOV | 5 | 0.34 |  | 1.2 |  |  | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
98 | TOV | 5 | 0.34 |  | 1.25 |  |  | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
99 | TOV | 5 | 0.34 |  | 1.3 |  |  | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
100 | TOV | 5 | 0.34 |  | 1.35 |  |  | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
101 | TOV | 5 | 0.34 |  | 1.4 |  |  | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
102 | TOV | 5 | 0.34 |  | 1.45 |  |  | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
103 | TOV | 5 | 0.34 |  | 1.5 |  |  | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
104 | TOV | 5 | 0.34 |  | 1.55 |  |  | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
105 | TOV | 5 | 0.34 |  | 1.6 |  |  | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
106 | TOV | 5 | 0.34 |  | 1.65 |  |  | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
107 | TOV | 5 | 0.34 |  | 1.7 |  |  | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
108 | TOV | 5 | 0.34 |  | 1.75 |  |  | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
109 | TOV | 5 | 0.34 |  | 1.8 |  |  | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
110 | TOV | 5 | 0.34 |  | 1.85 |  |  | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
111 | TOV | 5 | 0.34 |  | 1.9 |  |  | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
112 | TOV | 5 | 0.34 |  | 1.95 |  |  | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
113 | TOV | 5 | 0.34 |  | 2 |  |  | 201 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
114 | TOV | 5 | 0.34 |  | 1.05 |  |  | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
115 | TOV | 5 | 0.34 |  | 1.1 |  |  | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
116 | TOV | 5 | 0.34 |  | 1.15 |  |  | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
117 | TOV | 5 | 0.34 |  | 1.2 |  |  | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
118 | TOV | 5 | 0.34 |  | 1.25 |  |  | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
119 | TOV | 5 | 0.34 |  | 1.3 |  |  | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
120 | TOV | 5 | 0.34 |  | 1.35 |  |  | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
121 | TOV | 5 | 0.34 |  | 1.4 |  |  | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
122 | TOV | 5 | 0.34 |  | 1.45 |  |  | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
123 | TOV | 5 | 0.34 |  | 1.5 |  |  | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
124 | TOV | 5 | 0.34 |  | 1.55 |  |  | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
125 | TOV | 5 | 0.34 |  | 1.6 |  |  | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
126 | TOV | 5 | 0.34 |  | 1.65 |  |  | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
127 | TOV | 5 | 0.34 |  | 1.7 |  |  | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
128 | TOV | 5 | 0.34 |  | 1.75 |  |  | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
129 | TOV | 5 | 0.34 |  | 1.8 |  |  | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
130 | TOV | 5 | 0.34 |  | 1.85 |  |  | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
131 | TOV | 5 | 0.34 |  | 1.9 |  |  | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
132 | TOV | 5 | 0.34 |  | 1.95 |  |  | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
133 | TOV | 5 | 0.34 |  | 2 |  |  | 204 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
134 | TOV | 5 | 0.34 |  | 1.05 |  |  | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
135 | TOV | 5 | 0.34 |  | 1.1 |  |  | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
136 | TOV | 5 | 0.34 |  | 1.15 |  |  | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
137 | TOV | 5 | 0.34 |  | 1.2 |  |  | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
138 | TOV | 5 | 0.34 |  | 1.25 |  |  | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
139 | TOV | 5 | 0.34 |  | 1.3 |  |  | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
140 | TOV | 5 | 0.34 |  | 1.35 |  |  | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
141 | TOV | 5 | 0.34 |  | 1.4 |  |  | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
142 | TOV | 5 | 0.34 |  | 1.45 |  |  | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
143 | TOV | 5 | 0.34 |  | 1.5 |  |  | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
144 | TOV | 5 | 0.34 |  | 1.55 |  |  | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
145 | TOV | 5 | 0.34 |  | 1.6 |  |  | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
146 | TOV | 5 | 0.34 |  | 1.65 |  |  | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
147 | TOV | 5 | 0.34 |  | 1.7 |  |  | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
148 | TOV | 5 | 0.34 |  | 1.75 |  |  | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
149 | TOV | 5 | 0.34 |  | 1.8 |  |  | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
150 | TOV | 5 | 0.34 |  | 1.85 |  |  | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
151 | TOV | 5 | 0.34 |  | 1.9 |  |  | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
152 | TOV | 5 | 0.34 |  | 1.95 |  |  | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
153 | TOV | 5 | 0.34 |  | 2 |  |  | 205 | 2 | 1 | 0.2 | yes | yes |  | V control mode | S5255Iq1
154 | TOV | 5 | 0.34 |  | 1.05 |  |  | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
155 | TOV | 5 | 0.34 |  | 1.1 |  |  | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
156 | TOV | 5 | 0.34 |  | 1.15 |  |  | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
157 | TOV | 5 | 0.34 |  | 1.2 |  |  | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
158 | TOV | 5 | 0.34 |  | 1.25 |  |  | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
159 | TOV | 5 | 0.34 |  | 1.3 |  |  | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
160 | TOV | 5 | 0.34 |  | 1.35 |  |  | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
161 | TOV | 5 | 0.34 |  | 1.4 |  |  | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
162 | TOV | 5 | 0.34 |  | 1.45 |  |  | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
163 | TOV | 5 | 0.34 |  | 1.5 |  |  | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
164 | TOV | 5 | 0.34 |  | 1.55 |  |  | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
165 | TOV | 5 | 0.34 |  | 1.6 |  |  | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
166 | TOV | 5 | 0.34 |  | 1.65 |  |  | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
167 | TOV | 5 | 0.34 |  | 1.7 |  |  | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
168 | TOV | 5 | 0.34 |  | 1.75 |  |  | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
169 | TOV | 5 | 0.34 |  | 1.8 |  |  | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
170 | TOV | 5 | 0.34 |  | 1.85 |  |  | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
171 | TOV | 5 | 0.34 |  | 1.9 |  |  | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
172 | TOV | 5 | 0.34 |  | 1.95 |  |  | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
173 | TOV | 5 | 0.34 |  | 2 |  |  | 241 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
174 | TOV | 5 | 0.34 |  | 1.05 |  |  | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
175 | TOV | 5 | 0.34 |  | 1.1 |  |  | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
176 | TOV | 5 | 0.34 |  | 1.15 |  |  | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
177 | TOV | 5 | 0.34 |  | 1.2 |  |  | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
178 | TOV | 5 | 0.34 |  | 1.25 |  |  | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
179 | TOV | 5 | 0.34 |  | 1.3 |  |  | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
180 | TOV | 5 | 0.34 |  | 1.35 |  |  | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
181 | TOV | 5 | 0.34 |  | 1.4 |  |  | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
182 | TOV | 5 | 0.34 |  | 1.45 |  |  | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
183 | TOV | 5 | 0.34 |  | 1.5 |  |  | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
184 | TOV | 5 | 0.34 |  | 1.55 |  |  | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
185 | TOV | 5 | 0.34 |  | 1.6 |  |  | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
186 | TOV | 5 | 0.34 |  | 1.65 |  |  | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
187 | TOV | 5 | 0.34 |  | 1.7 |  |  | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
188 | TOV | 5 | 0.34 |  | 1.75 |  |  | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
189 | TOV | 5 | 0.34 |  | 1.8 |  |  | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
190 | TOV | 5 | 0.34 |  | 1.85 |  |  | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
191 | TOV | 5 | 0.34 |  | 1.9 |  |  | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
192 | TOV | 5 | 0.34 |  | 1.95 |  |  | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
193 | TOV | 5 | 0.34 |  | 2 |  |  | 244 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
194 | TOV | 5 | 0.34 |  | 1.05 |  |  | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
195 | TOV | 5 | 0.34 |  | 1.1 |  |  | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
196 | TOV | 5 | 0.34 |  | 1.15 |  |  | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
197 | TOV | 5 | 0.34 |  | 1.2 |  |  | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
198 | TOV | 5 | 0.34 |  | 1.25 |  |  | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
199 | TOV | 5 | 0.34 |  | 1.3 |  |  | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
200 | TOV | 5 | 0.34 |  | 1.35 |  |  | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
201 | TOV | 5 | 0.34 |  | 1.4 |  |  | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
202 | TOV | 5 | 0.34 |  | 1.45 |  |  | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
203 | TOV | 5 | 0.34 |  | 1.5 |  |  | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
204 | TOV | 5 | 0.34 |  | 1.55 |  |  | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
205 | TOV | 5 | 0.34 |  | 1.6 |  |  | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
206 | TOV | 5 | 0.34 |  | 1.65 |  |  | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
207 | TOV | 5 | 0.34 |  | 1.7 |  |  | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
208 | TOV | 5 | 0.34 |  | 1.75 |  |  | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
209 | TOV | 5 | 0.34 |  | 1.8 |  |  | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
210 | TOV | 5 | 0.34 |  | 1.85 |  |  | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
211 | TOV | 5 | 0.34 |  | 1.9 |  |  | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
212 | TOV | 5 | 0.34 |  | 1.95 |  |  | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
213 | TOV | 5 | 0.34 |  | 2 |  |  | 245 | 2 | 1 | 0.2 | yes | yes |  | Q control mode | S5255Iq2
214 | TOV | 5 | 0.34 |  | 1.05 |  |  | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
215 | TOV | 5 | 0.34 |  | 1.1 |  |  | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
216 | TOV | 5 | 0.34 |  | 1.15 |  |  | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
217 | TOV | 5 | 0.34 |  | 1.2 |  |  | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
218 | TOV | 5 | 0.34 |  | 1.25 |  |  | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
219 | TOV | 5 | 0.34 |  | 1.3 |  |  | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
220 | TOV | 5 | 0.34 |  | 1.35 |  |  | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
221 | TOV | 5 | 0.34 |  | 1.4 |  |  | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
222 | TOV | 5 | 0.34 |  | 1.45 |  |  | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
223 | TOV | 5 | 0.34 |  | 1.5 |  |  | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
224 | TOV | 5 | 0.34 |  | 1.55 |  |  | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
225 | TOV | 5 | 0.34 |  | 1.6 |  |  | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
226 | TOV | 5 | 0.34 |  | 1.65 |  |  | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
227 | TOV | 5 | 0.34 |  | 1.7 |  |  | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
228 | TOV | 5 | 0.34 |  | 1.75 |  |  | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
229 | TOV | 5 | 0.34 |  | 1.8 |  |  | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
230 | TOV | 5 | 0.34 |  | 1.85 |  |  | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
231 | TOV | 5 | 0.34 |  | 1.9 |  |  | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
232 | TOV | 5 | 0.34 |  | 1.95 |  |  | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
233 | TOV | 5 | 0.34 |  | 2 |  |  | 281 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
234 | TOV | 5 | 0.34 |  | 1.05 |  |  | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
235 | TOV | 5 | 0.34 |  | 1.1 |  |  | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
236 | TOV | 5 | 0.34 |  | 1.15 |  |  | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
237 | TOV | 5 | 0.34 |  | 1.2 |  |  | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
238 | TOV | 5 | 0.34 |  | 1.25 |  |  | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
239 | TOV | 5 | 0.34 |  | 1.3 |  |  | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
240 | TOV | 5 | 0.34 |  | 1.35 |  |  | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
241 | TOV | 5 | 0.34 |  | 1.4 |  |  | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
242 | TOV | 5 | 0.34 |  | 1.45 |  |  | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
243 | TOV | 5 | 0.34 |  | 1.5 |  |  | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
244 | TOV | 5 | 0.34 |  | 1.55 |  |  | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
245 | TOV | 5 | 0.34 |  | 1.6 |  |  | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
246 | TOV | 5 | 0.34 |  | 1.65 |  |  | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
247 | TOV | 5 | 0.34 |  | 1.7 |  |  | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
248 | TOV | 5 | 0.34 |  | 1.75 |  |  | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
249 | TOV | 5 | 0.34 |  | 1.8 |  |  | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
250 | TOV | 5 | 0.34 |  | 1.85 |  |  | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
251 | TOV | 5 | 0.34 |  | 1.9 |  |  | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
252 | TOV | 5 | 0.34 |  | 1.95 |  |  | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
253 | TOV | 5 | 0.34 |  | 2 |  |  | 284 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
254 | TOV | 5 | 0.34 |  | 1.05 |  |  | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
255 | TOV | 5 | 0.34 |  | 1.1 |  |  | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
256 | TOV | 5 | 0.34 |  | 1.15 |  |  | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
257 | TOV | 5 | 0.34 |  | 1.2 |  |  | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
258 | TOV | 5 | 0.34 |  | 1.25 |  |  | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
259 | TOV | 5 | 0.34 |  | 1.3 |  |  | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
260 | TOV | 5 | 0.34 |  | 1.35 |  |  | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
261 | TOV | 5 | 0.34 |  | 1.4 |  |  | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
262 | TOV | 5 | 0.34 |  | 1.45 |  |  | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
263 | TOV | 5 | 0.34 |  | 1.5 |  |  | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
264 | TOV | 5 | 0.34 |  | 1.55 |  |  | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
265 | TOV | 5 | 0.34 |  | 1.6 |  |  | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
266 | TOV | 5 | 0.34 |  | 1.65 |  |  | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
267 | TOV | 5 | 0.34 |  | 1.7 |  |  | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
268 | TOV | 5 | 0.34 |  | 1.75 |  |  | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
269 | TOV | 5 | 0.34 |  | 1.8 |  |  | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
270 | TOV | 5 | 0.34 |  | 1.85 |  |  | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
271 | TOV | 5 | 0.34 |  | 1.9 |  |  | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
272 | TOV | 5 | 0.34 |  | 1.95 |  |  | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
273 | TOV | 5 | 0.34 |  | 2 |  |  | 285 | 2 | 1 | 0.2 | yes | yes |  | PF control mode | S5255Iq3
Note on J6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Ini_help = 0: normal ini Ini_help = 1: fix SCL to inf before 2sec when low SCR Ini_help = 2: fix Vinf to 1.0pu before 2sec when low SCR
Note on A7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MAT

## Setpoints
Description: This sheet is used to initialise the model at different setpoints. The "name" of the PSCAD setting to be adjusted is for readability only and is not used. The module that contains the component is separated by a colon in case is is a submodule of "Main" The value of each parameter needs to be defined for each of the setpoint IDs | [5 empty] | Setpoints | [119 empty] | various Pavail, Pini, max-min SCR/X_R | [9 empty] | Different DYR - Q setpoint | [29 empty] | various Pavail, Pini, max-min SCR/X_R | [9 empty] | Different DYR - PF setpoint | [29 empty] | Transgrid Proposed setpoints - Vcontrol min SCR | [39 empty] | Transgrid Proposed setpoints - Qcontrol min SCR | [39 empty] | Transgrid Proposed setpoints - PFcontrol min SCR | [39 empty] | Transgrid Proposed setpoints - Vcontrol max SCR | [39 empty] | Transgrid Proposed setpoints - Qcontrol max SCR | [39 empty] | Transgrid Proposed setpoints - PFcontrol max SCR | [39 empty] | Transgrid Proposed setpoints - Vcontrol INF SCR | [39 empty] | Transgrid Proposed setpoints - Qcontrol INF SCR | [39 empty] | Transgrid Proposed setpoints - PFcontrol INF SCR
[5 empty] | ParameterName | AemoMinSCR - Pmax |  |  |  |  | AemoMinSCR - Pmin |  |  |  |  | AemoMaxSCR - Pmax |  |  |  |  | AemoMaxSCR - Pmin |  |  |  |  | INF SCR - Pmax |  |  |  |  | INF SCR - Pmin |  |  |  |  | SCR=3, X/R=14 | [9 empty] | SCR=3, X/R=3 | [9 empty] | SCR=10, X/R=14 | [9 empty] | SCR=10, X/R=3 | [9 empty] | SCR=3, X/R=6 | [9 empty] | SCR=5, X/R=6 | [9 empty] | SCR=10, X/R=6 | [9 empty] | SCR=1, X/R=14 | [9 empty] | SCR=1, X/R=3 | [9 empty] | Pavai=1, Pini=0.5 |  | P0.5 - 0.5 |  | P0.5 - 0.05 |  | P0.05 -0.05 |  | 3-14 | 3-3 | AemoMinSCR - Pmax |  |  |  |  | AemoMinSCR - Pmin |  |  |  |  | AemoMaxSCR - Pmax |  |  |  |  | AemoMaxSCR - Pmin |  |  |  |  | INF SCR - Pmax |  |  |  |  | INF SCR - Pmin |  |  |  |  | X/R = 14 |  |  |  | X/R = 3 |  |  |  | Place holder |  | AemoMinSCR - Pmax |  |  |  |  | AemoMinSCR - Pmin |  |  |  |  | AemoMaxSCR - Pmax |  |  |  |  | AemoMaxSCR - Pmin |  |  |  |  | INF SCR - Pmax |  |  |  |  | INF SCR - Pmin |  |  |  |  | PV only max export |  |  |  |  | PV and BESS combined max export |  |  |  |  | BESS only export |  |  |  |  | Charging while exporting too (PV maxed out) |  |  |  |  | 0MW dispatch from both |  |  |  |  | Net zero dispatch while PV charge BESS |  |  |  |  | BESS Charging from grid and PV |  |  |  |  | BESS charging from Grid only |  |  |  |  | PV only max export |  |  |  |  | PV and BESS combined max export |  |  |  |  | BESS only export |  |  |  |  | Charging while exporting too |  |  |  |  | 0MW dispatch from both |  |  |  |  | Net zero dispatch while PV charge BESS |  |  |  |  | BESS Charging from grid and PV |  |  |  |  | BESS charging from Grid only |  |  |  |  | PV only max export |  |  |  |  | PV and BESS combined max export |  |  |  |  | BESS only export |  |  |  |  | Charging while exporting too |  |  |  |  | 0MW dispatch from both |  |  |  |  | Net zero dispatch while PV charge BESS |  |  |  |  | BESS Charging from grid and PV |  |  |  |  | BESS charging from Grid only |  |  |  |  | PV only max export |  |  |  |  | PV and BESS combined max export |  |  |  |  | BESS only export |  |  |  |  | Charging while exporting too |  |  |  |  | 0MW dispatch from both |  |  |  |  | Net zero dispatch while PV charge BESS |  |  |  |  | BESS Charging from grid and PV |  |  |  |  | BESS charging from Grid only |  |  |  |  | PV only max export |  |  |  |  | PV and BESS combined max export |  |  |  |  | BESS only export |  |  |  |  | Charging while exporting too |  |  |  |  | 0MW dispatch from both |  |  |  |  | Net zero dispatch while PV charge BESS |  |  |  |  | BESS Charging from grid and PV |  |  |  |  | BESS charging from Grid only |  |  |  |  | PV only max export |  |  |  |  | PV and BESS combined max export |  |  |  |  | BESS only export |  |  |  |  | Charging while exporting too |  |  |  |  | 0MW dispatch from both |  |  |  |  | Net zero dispatch while PV charge BESS |  |  |  |  | BESS Charging from grid and PV |  |  |  |  | BESS charging from Grid only |  |  |  |  | PV only max export |  |  |  |  | PV and BESS combined max export |  |  |  |  | BESS only export |  |  |  |  | Charging while exporting too |  |  |  |  | 0MW dispatch from both |  |  |  |  | Net zero dispatch while PV charge BESS |  |  |  |  | BESS Charging from grid and PV |  |  |  |  | BESS charging from Grid only |  |  |  |  | PV only max export |  |  |  |  | PV and BESS combined max export |  |  |  |  | BESS only export |  |  |  |  | Charging while exporting too |  |  |  |  | 0MW dispatch from both |  |  |  |  | Net zero dispatch while PV charge BESS |  |  |  |  | BESS Charging from grid and PV |  |  |  |  | BESS charging from Grid only |  |  |  |  | PV only max export |  |  |  |  | PV and BESS combined max export |  |  |  |  | BESS only export |  |  |  |  | Charging while exporting too |  |  |  |  | 0MW dispatch from both |  |  |  |  | Net zero dispatch while PV charge BESS |  |  |  |  | BESS Charging from grid and PV |  |  |  |  | BESS charging from Grid only
GENERAL |  |  |  |  | Setpoint ID | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212 | 213 | 214 | 215 | 216 | 217 | 218 | 219 | 220 | 221 | 222 | 223 | 224 | 225 | 226 | 227 | 228 | 229 | 230 | 231 | 232 | 233 | 234 | 235 | 236 | 237 | 238 | 239 | 240 | 241 | 242 | 243 | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273 | 274 | 275 | 276 | 277 | 278 | 279 | 280 | 281 | 282 | 283 | 284 | 285 | 286 | 287 | 288 | 289 | 290 | 291 | 292 | 293 | 294 | 295 | 296 | 297 | 298 | 299 | 300 | 301 | 302 | 303 | 304 | 305 | 306 | 307 | 308 | 309 | 310 | 311 | 312 | 313 | 314 | 315 | 316 | 317 | 318 | 319 | 320 | 321 | 322 | 323 | 324 | 325 | 326 | 327 | 328 | 329 | 330 | 331 | 332 | 333 | 334 | 335 | 336 | 337 | 338 | 339 | 340 | 341 | 342 | 343 | 344 | 345 | 346 | 347 | 348 | 349 | 350 | 351 | 352 | 353 | 354 | 355 | 356 | 357 | 358 | 359 | 360 | 361 | 362 | 363 | 364 | 365 | 366 | 367 | 368 | 369 | 370 | 371 | 372 | 373 | 374 | 375 | 376 | 377 | 378 | 379 | 380 | 381 | 382 | 383 | 384 | 385 | 386 | 387 | 388 | 389 | 390 | 391 | 392 | 393 | 394 | 395 | 396 | 397 | 398 | 399 | 400 | 401 | 402 | 403 | 404 | 405 | 406 | 407 | 408 | 409 | 410 | 411 | 412 | 413 | 414 | 415 | 416 | 417 | 418 | 419 | 420 | 421 | 422 | 423 | 424 | 425 | 426 | 427 | 428 | 429 | 430 | 431 | 432 | 433 | 434 | 435 | 436 | 437 | 438 | 439 | 440 | 441 | 442 | 443 | 444 | 445 | 446 | 447 | 448 | 449 | 450 | 451 | 452 | 453 | 454 | 455 | 456 | 457 | 458 | 459 | 460 | 461 | 462 | 463 | 464 | 465 | 466 | 467 | 468 | 469 | 470 | 471 | 472 | 473 | 474 | 475 | 476 | 477 | 478 | 479 | 480 | 481 | 482 | 483 | 484 | 485 | 486 | 487 | 488 | 489 | 490 | 491 | 492 | 493 | 494 | 495 | 496 | 497 | 498 | 499 | 500 | 501 | 502 | 503 | 504 | 505 | 506 | 507 | 508 | 509 | 510 | 511 | 512 | 513 | 514 | 515 | 516 | 517 | 518 | 519 | 520 | 521 | 522 | 523 | 524 | 525 | 526 | 527 | 528 | 529 | 530 | 531 | 532 | 533 | 534 | 535 | 536 | 537 | 538 | 539 | 540 | 541 | 542 | 543 | 544 | 545 | 546 | 547 | 548 | 549 | 550 | 551 | 552 | 553 | 554 | 555 | 556 | 557 | 558 | 559 | 560
| Q0 | Qmax | Qmin |  | GridMVA | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 595 | 595 | 595 | 595 | 595 | 595 | 595 | 595 | 595 | 595 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 483 | 1109 | 483 | 1109 | 483 | 1109 | 483 | 1109 | 357 | 357 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 357 | 1190 | 357 | 1190 | 357 | 1190 | 357 | 1190 | 1189881 | 1189881 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999
system normal voltage | 1.03 | 1.01 | 1.063 |  | SCR | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4.0588 | 12.3222 | 4.0588 | 12.3222 | 4.0588 | 12.3222 | 4.0588 | 12.3222 | 3 | 3 | 5.3667 | 5.3667 | 5.3667 | 5.3667 | 5.3667 | 5.3667 | 5.3667 | 5.3667 | 5.3667 | 5.3667 | 12.3222 | 12.3222 | 12.3222 | 12.3222 | 12.3222 | 12.3222 | 12.3222 | 12.3222 | 12.3222 | 12.3222 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 3 | 10 | 3 | 10 | 3 | 10 | 3 | 10 | 9999 | 9999 | 5.3667 | 5.3667 | 5.3667 | 5.3667 | 5.3667 | 5.3667 | 5.3667 | 5.3667 | 5.3667 | 5.3667 | 12.3222 | 12.3222 | 12.3222 | 12.3222 | 12.3222 | 12.3222 | 12.3222 | 12.3222 | 12.3222 | 12.3222 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 1111.1 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 4.0588 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 9.3193 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 7.0513 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277 | 840.3277
droop | 12.7% | 12.7% | 12.7% |  | X_R | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3 | 3.77 | 3 | 3.77 | 3 | 3.77 | 14 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 14 | 14 | 14 | 14 | 3 | 3 | 3 | 3 | 3 | 14 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
droop base | 90 | 90 | 90 |  | Pini | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.5 | 0.5 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 0.05 | 0.05 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034
[5 empty] | P1ini | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.25 | 0.25 | 0.25 | 0.25 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0 | 0 | 0 | 0 | 0 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | 0 | 0 | 0 | 0 | 0 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 0 | 0 | 0 | 0 | 0 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | 0 | 0 | 0 | 0 | 0 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 0 | 0 | 0 | 0 | 0 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | 0 | 0 | 0 | 0 | 0 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 0 | 0 | 0 | 0 | 0 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | 0 | 0 | 0 | 0 | 0 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 0 | 0 | 0 | 0 | 0 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | 0 | 0 | 0 | 0 | 0 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 0 | 0 | 0 | 0 | 0 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | 0 | 0 | 0 | 0 | 0 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 0 | 0 | 0 | 0 | 0 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | 0 | 0 | 0 | 0 | 0 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 0 | 0 | 0 | 0 | 0 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | 0 | 0 | 0 | 0 | 0 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 0 | 0 | 0 | 0 | 0 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | 0 | 0 | 0 | 0 | 0 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034
[5 empty] | Qini | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395
[5 empty] | Q1ini | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0 | 0.15 | -0.15 | 0.1975 | -0.1975 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338 | 0.54338
[5 empty] | Pavai | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[5 empty] | V_POC | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02
[5 empty] | P | 119 | 119 | 119 | 119 | 119 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 119 | 119 | 119 | 119 | 119 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 119 | 119 | 119 | 119 | 119 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 119 | 119 | 119 | 119 | 119 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 119 | 119 | 119 | 119 | 119 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 119 | 119 | 119 | 119 | 119 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 119 | 119 | 119 | 119 | 119 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 119 | 119 | 119 | 119 | 119 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 119 | 119 | 119 | 119 | 119 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 119 | 119 | 119 | 119 | 119 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 119 | 119 | 119 | 119 | 119 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 119 | 119 | 119 | 119 | 119 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 59.5 | 59.5 | 59.5 | 59.5 | 5.95 | 5.95 | 5.95 | 5.95 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 119 | 119 | 119 | 119 | 119 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 119 | 119 | 119 | 119 | 119 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 119 | 119 | 5.95 | 5.95 | 119 | 119 | 5.95 | 5.95 | 5.95 | 5.95 | 119 | 119 | 119 | 119 | 119 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 119 | 119 | 119 | 119 | 119 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 119 | 119 | 119 | 119 | 119 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -50 | -50 | -50 | -50 | -50 | -100 | -100 | -100 | -100 | -100 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -50 | -50 | -50 | -50 | -50 | -100 | -100 | -100 | -100 | -100 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -50 | -50 | -50 | -50 | -50 | -100 | -100 | -100 | -100 | -100 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -50 | -50 | -50 | -50 | -50 | -100 | -100 | -100 | -100 | -100 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -50 | -50 | -50 | -50 | -50 | -100 | -100 | -100 | -100 | -100 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -50 | -50 | -50 | -50 | -50 | -100 | -100 | -100 | -100 | -100 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -50 | -50 | -50 | -50 | -50 | -100 | -100 | -100 | -100 | -100 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -50 | -50 | -50 | -50 | -50 | -100 | -100 | -100 | -100 | -100 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -50 | -50 | -50 | -50 | -50 | -100 | -100 | -100 | -100 | -100
[5 empty] | Q | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005 | 0 | 35.7 | -35.7 | 47.005 | -47.005
PSSE-specific |  |  |  |  | P_PV1 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 2.9754 | 2.9754 | 2.9754 | 2.9754 | 2.9754 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 29.7504 | 29.7504 | 29.7504 | 29.7504 | 2.9754 | 2.9754 | 2.9754 | 2.9754 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 2.9754 | 2.9754 | 2.9754 | 2.9754 | 2.9754 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 119 | 119 | 119 | 119 | 119 | 60 | 60 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 119 | 119 | 119 | 119 | 119 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 119 | 119 | 119 | 119 | 119 | 60 | 60 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 119 | 119 | 119 | 119 | 119 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 119 | 119 | 119 | 119 | 119 | 60 | 60 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 119 | 119 | 119 | 119 | 119 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 119 | 119 | 119 | 119 | 119 | 60 | 60 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 119 | 119 | 119 | 119 | 119 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 119 | 119 | 119 | 119 | 119 | 60 | 60 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 119 | 119 | 119 | 119 | 119 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 119 | 119 | 119 | 119 | 119 | 60 | 60 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 119 | 119 | 119 | 119 | 119 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 119 | 119 | 119 | 119 | 119 | 60 | 60 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 119 | 119 | 119 | 119 | 119 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 119 | 119 | 119 | 119 | 119 | 60 | 60 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 119 | 119 | 119 | 119 | 119 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 119 | 119 | 119 | 119 | 119 | 60 | 60 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 119 | 119 | 119 | 119 | 119 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 | 50 | 0 | 0 | 0 | 0 | 0
[5 empty] | Q_PV1 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -6.0604 | -6.0604 | -6.0604 | -6.0604 | -7.5876 | -7.5876 | -7.5876 | -7.5876 | -6.0604 | -6.0604 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -6.0604 | -6.0604 | -6.0604 | -6.0604 | -7.5876 | -7.5876 | -7.5876 | -7.5876 | -6.0604 | -6.0604 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025
Pmax | Q0 | Q0.3 | Q-0.3 | Qmax | LOC_PV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1 | MV1
Ploss 33kV - POC (pu) | 0.0025556 | 0.002556 | 0.002556 | 0.002556 | BUS_PV1 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094 | 334094
Qloss 33kV - POC (pu) | -0.022222 | -0.0088777 | -0.016667 | 0.0088777 | P_PV2 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 2.9754 | 2.9754 | 2.9754 | 2.9754 | 2.9754 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 29.7504 | 29.7504 | 29.7504 | 29.7504 | 2.9754 | 2.9754 | 2.9754 | 2.9754 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 2.9754 | 2.9754 | 2.9754 | 2.9754 | 2.9754 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 59.6521 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 3.1271 | 0 | 0 | 0 | 0 | 0 | 59 | 59 | 59 | 59 | 59 | 100 | 100 | 100 | 100 | 100 | -59 | -59 | -59 | -59 | -59 | 0 | 0 | 0 | 0 | 0 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | 0 | 0 | 0 | 0 | 0 | 59 | 59 | 59 | 59 | 59 | 100 | 100 | 100 | 100 | 100 | -59 | -59 | -59 | -59 | -59 | 0 | 0 | 0 | 0 | 0 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | 0 | 0 | 0 | 0 | 0 | 59 | 59 | 59 | 59 | 59 | 100 | 100 | 100 | 100 | 100 | -59 | -59 | -59 | -59 | -59 | 0 | 0 | 0 | 0 | 0 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | 0 | 0 | 0 | 0 | 0 | 59 | 59 | 59 | 59 | 59 | 100 | 100 | 100 | 100 | 100 | -59 | -59 | -59 | -59 | -59 | 0 | 0 | 0 | 0 | 0 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | 0 | 0 | 0 | 0 | 0 | 59 | 59 | 59 | 59 | 59 | 100 | 100 | 100 | 100 | 100 | -59 | -59 | -59 | -59 | -59 | 0 | 0 | 0 | 0 | 0 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | 0 | 0 | 0 | 0 | 0 | 59 | 59 | 59 | 59 | 59 | 100 | 100 | 100 | 100 | 100 | -59 | -59 | -59 | -59 | -59 | 0 | 0 | 0 | 0 | 0 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | 0 | 0 | 0 | 0 | 0 | 59 | 59 | 59 | 59 | 59 | 100 | 100 | 100 | 100 | 100 | -59 | -59 | -59 | -59 | -59 | 0 | 0 | 0 | 0 | 0 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | 0 | 0 | 0 | 0 | 0 | 59 | 59 | 59 | 59 | 59 | 100 | 100 | 100 | 100 | 100 | -59 | -59 | -59 | -59 | -59 | 0 | 0 | 0 | 0 | 0 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | 0 | 0 | 0 | 0 | 0 | 59 | 59 | 59 | 59 | 59 | 100 | 100 | 100 | 100 | 100 | -59 | -59 | -59 | -59 | -59 | 0 | 0 | 0 | 0 | 0 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100
[5 empty] | Q_PV2 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -6.0604 | -6.0604 | -6.0604 | -6.0604 | -7.5876 | -7.5876 | -7.5876 | -7.5876 | -6.0604 | -6.0604 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -6.0604 | -6.0604 | -6.0604 | -6.0604 | -7.5876 | -7.5876 | -7.5876 | -7.5876 | -6.0604 | -6.0604 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | -1.3222 | 17.3218 | -18.8417 | 24.0307 | -24.4942 | -7.5876 | 11.2541 | -24.4459 | 16.9066 | -30.0984 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025 | 0 | 17.85 | -17.85 | 23.5025 | -23.5025
Pmin = 0.05 | Q0 | Q0.3 | Q-0.3 |  | LOC_PV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2 | MV2
Ploss 33kV - POC (pu) | 6.3896e-06 | 6.3896e-06 | 6.3896e-06 |  | BUS_PV2 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095 | 334095
Qloss 33kV - POC (pu) | -0.12752 | -0.11086 | -0.11086 |  | offline_machines
disconnect_buses
P = 0.5 | Q0 | Q0.3 | Q-0.3 |  | TR1_from | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091 | 334091
Ploss 33kV - POC (pu) | 6.3896e-06 | 6.3896e-06 | 6.3896e-06 |  | TR1_to | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090 | 334090
Qloss 33kV - POC (pu) | -0.10186 | -0.11086 | -0.11086 |  | TR1_tap | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.025 | 1.0625 | 0.9875 | 1.075 | 0.9875 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025 | 1.0375 | 1.05 | 1.0375 | 1.0625 | 1.025
[5 empty] | dyr | AemoMinSCR - Pmax 131: SUMSF_SMIB_V1_Qctrl.dyr; AemoMinSCR - Pmax 132: SUMSF_SMIB_V1_Qctrl.dyr; AemoMinSCR - Pmax 133: SUMSF_SMIB_V1_Qctrl.dyr; AemoMinSCR - Pmax 134: SUMSF_SMIB_V1_Qctrl.dyr; AemoMinSCR - Pmax 135: SUMSF_SMIB_V1_Qctrl.dyr; AemoMinSCR - Pmin 136: SUMSF_SMIB_V1_Qctrl.dyr; AemoMinSCR - Pmin 137: SUMSF_SMIB_V1_Qctrl.dyr; AemoMinSCR - Pmin 138: SUMSF_SMIB_V1_Qctrl.dyr; AemoMinSCR - Pmin 139: SUMSF_SMIB_V1_Qctrl.dyr; AemoMinSCR - Pmin 140: SUMSF_SMIB_V1_Qctrl.dyr; AemoMaxSCR - Pmax 141: SUMSF_SMIB_V1_Qctrl.dyr; AemoMaxSCR - Pmax 142: SUMSF_SMIB_V1_Qctrl.dyr; AemoMaxSCR - Pmax 143: SUMSF_SMIB_V1_Qctrl.dyr; AemoMaxSCR - Pmax 144: SUMSF_SMIB_V1_Qctrl.dyr; AemoMaxSCR - Pmax 145: SUMSF_SMIB_V1_Qctrl.dyr; AemoMaxSCR - Pmin 146: SUMSF_SMIB_V1_Qctrl.dyr; AemoMaxSCR - Pmin 147: SUMSF_SMIB_V1_Qctrl.dyr; AemoMaxSCR - Pmin 148: SUMSF_SMIB_V1_Qctrl.dyr; AemoMaxSCR - Pmin 149: SUMSF_SMIB_V1_Qctrl.dyr; AemoMaxSCR - Pmin 150: SUMSF_SMIB_V1_Qctrl.dyr; INF SCR - Pmax 151: SUMSF_SMIB_V1_Qctrl.dyr; INF SCR - Pmax 152: SUMSF_SMIB_V1_Qctrl.dyr; INF SCR - Pmax 153: SUMSF_SMIB_V1_Qctrl.dyr; INF SCR - Pmax 154: SUMSF_SMIB_V1_Qctrl.dyr; INF SCR - Pmax 155: SUMSF_SMIB_V1_Qctrl.dyr; INF SCR - Pmin 156: SUMSF_SMIB_V1_Qctrl.dyr; INF SCR - Pmin 157: SUMSF_SMIB_V1_Qctrl.dyr; INF SCR - Pmin 158: SUMSF_SMIB_V1_Qctrl.dyr; INF SCR - Pmin 159: SUMSF_SMIB_V1_Qctrl.dyr; INF SCR - Pmin 160: SUMSF_SMIB_V1_Qctrl.dyr; X/R = 14 161: SUMSF_SMIB_V1_Qctrl.dyr; X/R = 14 162: SUMSF_SMIB_V1_Qctrl.dyr; X/R = 14 163: SUMSF_SMIB_V1_Qctrl.dyr; X/R = 14 164: SUMSF_SMIB_V1_Qctrl.dyr; X/R = 3 165: SUMSF_SMIB_V1_Qctrl.dyr; X/R = 3 166: SUMSF_SMIB_V1_Qctrl.dyr; X/R = 3 167: SUMSF_SMIB_V1_Qctrl.dyr; X/R = 3 168: SUMSF_SMIB_V1_Qctrl.dyr; Place holder 169: SUMSF_SMIB_V1_Qctrl.dyr; Place holder 170: SUMSF_SMIB_V1_Qctrl.dyr; AemoMinSCR - Pmax 171: SUMSF_SMIB_V1_PFctrl.dyr; AemoMinSCR - Pmax 172: SUMSF_SMIB_V1_PFctrl.dyr; AemoMinSCR - Pmax 173: SUMSF_SMIB_V1_PFctrl.dyr; AemoMinSCR - Pmax 174: SUMSF_SMIB_V1_PFctrl.dyr; AemoMinSCR - Pmax 175: SUMSF_SMIB_V1_PFctrl.dyr; AemoMinSCR - Pmin 176: SUMSF_SMIB_V1_PFctrl.dyr; AemoMinSCR - Pmin 177: SUMSF_SMIB_V1_PFctrl.dyr; AemoMinSCR - Pmin 178: SUMSF_SMIB_V1_PFctrl.dyr; AemoMinSCR - Pmin 179: SUMSF_SMIB_V1_PFctrl.dyr; AemoMinSCR - Pmin 180: SUMSF_SMIB_V1_PFctrl.dyr; AemoMaxSCR - Pmax 181: SUMSF_SMIB_V1_PFctrl.dyr; AemoMaxSCR - Pmax 182: SUMSF_SMIB_V1_PFctrl.dyr; AemoMaxSCR - Pmax 183: SUMSF_SMIB_V1_PFctrl.dyr; AemoMaxSCR - Pmax 184: SUMSF_SMIB_V1_PFctrl.dyr; AemoMaxSCR - Pmax 185: SUMSF_SMIB_V1_PFctrl.dyr; AemoMaxSCR - Pmin 186: SUMSF_SMIB_V1_PFctrl.dyr; AemoMaxSCR - Pmin 187: SUMSF_SMIB_V1_PFctrl.dyr; AemoMaxSCR - Pmin 188: SUMSF_SMIB_V1_PFctrl.dyr; AemoMaxSCR - Pmin 189: SUMSF_SMIB_V1_PFctrl.dyr; AemoMaxSCR - Pmin 190: SUMSF_SMIB_V1_PFctrl.dyr; INF SCR - Pmax 191: SUMSF_SMIB_V1_PFctrl.dyr; INF SCR - Pmax 192: SUMSF_SMIB_V1_PFctrl.dyr; INF SCR - Pmax 193: SUMSF_SMIB_V1_PFctrl.dyr; INF SCR - Pmax 194: SUMSF_SMIB_V1_PFctrl.dyr; INF SCR - Pmax 195: SUMSF_SMIB_V1_PFctrl.dyr; INF SCR - Pmin 196: SUMSF_SMIB_V1_PFctrl.dyr; INF SCR - Pmin 197: SUMSF_SMIB_V1_PFctrl.dyr; INF SCR - Pmin 198: SUMSF_SMIB_V1_PFctrl.dyr; INF SCR - Pmin 199: SUMSF_SMIB_V1_PFctrl.dyr; INF SCR - Pmin 200: SUMSF_SMIB_V1_PFctrl.dyr; PV only max export 241: SUMSF_SMIB_V1_Qctrl.dyr; PV only max export 242: SUMSF_SMIB_V1_Qctrl.dyr; PV only max export 243: SUMSF_SMIB_V1_Qctrl.dyr; PV only max export 244: SUMSF_SMIB_V1_Qctrl.dyr; PV only max export 245: SUMSF_SMIB_V1_Qctrl.dyr; PV and BESS combined max export 246: SUMSF_SMIB_V1_Qctrl.dyr; PV and BESS combined max export 247: SUMSF_SMIB_V1_Qctrl.dyr; PV and BESS combined max export 248: SUMSF_SMIB_V1_Qctrl.dyr; PV and BESS combined max export 249: SUMSF_SMIB_V1_Qctrl.dyr; PV and BESS combined max export 250: SUMSF_SMIB_V1_Qctrl.dyr; BESS only export 251: SUMSF_SMIB_V1_Qctrl.dyr; BESS only export 252: SUMSF_SMIB_V1_Qctrl.dyr; BESS only export 253: SUMSF_SMIB_V1_Qctrl.dyr; BESS only export 254: SUMSF_SMIB_V1_Qctrl.dyr; BESS only export 255: SUMSF_SMIB_V1_Qctrl.dyr; Charging while exporting too 256: SUMSF_SMIB_V1_Qctrl.dyr; Charging while exporting too 257: SUMSF_SMIB_V1_Qctrl.dyr; Charging while exporting too 258: SUMSF_SMIB_V1_Qctrl.dyr; Charging while exporting too 259: SUMSF_SMIB_V1_Qctrl.dyr; Charging while exporting too 260: SUMSF_SMIB_V1_Qctrl.dyr; 0MW dispatch from both 261: SUMSF_SMIB_V1_Qctrl.dyr; 0MW dispatch from both 262: SUMSF_SMIB_V1_Qctrl.dyr; 0MW dispatch from both 263: SUMSF_SMIB_V1_Qctrl.dyr; 0MW dispatch from both 264: SUMSF_SMIB_V1_Qctrl.dyr; 0MW dispatch from both 265: SUMSF_SMIB_V1_Qctrl.dyr; Net zero dispatch while PV charge BESS 266: SUMSF_SMIB_V1_Qctrl.dyr; Net zero dispatch while PV charge BESS 267: SUMSF_SMIB_V1_Qctrl.dyr; Net zero dispatch while PV charge BESS 268: SUMSF_SMIB_V1_Qctrl.dyr; Net zero dispatch while PV charge BESS 269: SUMSF_SMIB_V1_Qctrl.dyr; Net zero dispatch while PV charge BESS 270: SUMSF_SMIB_V1_Qctrl.dyr; BESS Charging from grid and PV 271: SUMSF_SMIB_V1_Qctrl.dyr; BESS Charging from grid and PV 272: SUMSF_SMIB_V1_Qctrl.dyr; BESS Charging from grid and PV 273: SUMSF_SMIB_V1_Qctrl.dyr; BESS Charging from grid and PV 274: SUMSF_SMIB_V1_Qctrl.dyr; BESS Charging from grid and PV 275: SUMSF_SMIB_V1_Qctrl.dyr; BESS charging from Grid only 276: SUMSF_SMIB_V1_Qctrl.dyr; BESS charging from Grid only 277: SUMSF_SMIB_V1_Qctrl.dyr; BESS charging from Grid only 278: SUMSF_SMIB_V1_Qctrl.dyr; BESS charging from Grid only 279: SUMSF_SMIB_V1_Qctrl.dyr; BESS charging from Grid only 280: SUMSF_SMIB_V1_Qctrl.dyr; PV only max export 281: SUMSF_SMIB_V1_PFctrl.dyr; PV only max export 282: SUMSF_SMIB_V1_PFctrl.dyr; PV only max export 283: SUMSF_SMIB_V1_PFctrl.dyr; PV only max export 284: SUMSF_SMIB_V1_PFctrl.dyr; PV only max export 285: SUMSF_SMIB_V1_PFctrl.dyr; PV and BESS combined max export 286: SUMSF_SMIB_V1_PFctrl.dyr; PV and BESS combined max export 287: SUMSF_SMIB_V1_PFctrl.dyr; PV and BESS combined max export 288: SUMSF_SMIB_V1_PFctrl.dyr; PV and BESS combined max export 289: SUMSF_SMIB_V1_PFctrl.dyr; PV and BESS combined max export 290: SUMSF_SMIB_V1_PFctrl.dyr; BESS only export 291: SUMSF_SMIB_V1_PFctrl.dyr; BESS only export 292: SUMSF_SMIB_V1_PFctrl.dyr; BESS only export 293: SUMSF_SMIB_V1_PFctrl.dyr; BESS only export 294: SUMSF_SMIB_V1_PFctrl.dyr; BESS only export 295: SUMSF_SMIB_V1_PFctrl.dyr; Charging while exporting too 296: SUMSF_SMIB_V1_PFctrl.dyr; Charging while exporting too 297: SUMSF_SMIB_V1_PFctrl.dyr; Charging while exporting too 298: SUMSF_SMIB_V1_PFctrl.dyr; Charging while exporting too 299: SUMSF_SMIB_V1_PFctrl.dyr; Charging while exporting too 300: SUMSF_SMIB_V1_PFctrl.dyr; 0MW dispatch from both 301: SUMSF_SMIB_V1_PFctrl.dyr; 0MW dispatch from both 302: SUMSF_SMIB_V1_PFctrl.dyr; 0MW dispatch from both 303: SUMSF_SMIB_V1_PFctrl.dyr; 0MW dispatch from both 304: SUMSF_SMIB_V1_PFctrl.dyr; 0MW dispatch from both 305: SUMSF_SMIB_V1_PFctrl.dyr; Net zero dispatch while PV charge BESS 306: SUMSF_SMIB_V1_PFctrl.dyr; Net zero dispatch while PV charge BESS 307: SUMSF_SMIB_V1_PFctrl.dyr; Net zero dispatch while PV charge BESS 308: SUMSF_SMIB_V1_PFctrl.dyr; Net zero dispatch while PV charge BESS 309: SUMSF_SMIB_V1_PFctrl.dyr; Net zero dispatch while PV charge BESS 310: SUMSF_SMIB_V1_PFctrl.dyr; BESS Charging from grid and PV 311: SUMSF_SMIB_V1_PFctrl.dyr; BESS Charging from grid and PV 312: SUMSF_SMIB_V1_PFctrl.dyr; BESS Charging from grid and PV 313: SUMSF_SMIB_V1_PFctrl.dyr; BESS Charging from grid and PV 314: SUMSF_SMIB_V1_PFctrl.dyr; BESS Charging from grid and PV 315: SUMSF_SMIB_V1_PFctrl.dyr; BESS charging from Grid only 316: SUMSF_SMIB_V1_PFctrl.dyr; BESS charging from Grid only 317: SUMSF_SMIB_V1_PFctrl.dyr; BESS charging from Grid only 318: SUMSF_SMIB_V1_PFctrl.dyr; BESS charging from Grid only 319: SUMSF_SMIB_V1_PFctrl.dyr; BESS charging from Grid only 320: SUMSF_SMIB_V1_PFctrl.dyr; PV only max export 361: SUMSF_SMIB_V1_Qctrl.dyr; PV only max export 362: SUMSF_SMIB_V1_Qctrl.dyr; PV only max export 363: SUMSF_SMIB_V1_Qctrl.dyr; PV only max export 364: SUMSF_SMIB_V1_Qctrl.dyr; PV only max export 365: SUMSF_SMIB_V1_Qctrl.dyr; PV and BESS combined max export 366: SUMSF_SMIB_V1_Qctrl.dyr; PV and BESS combined max export 367: SUMSF_SMIB_V1_Qctrl.dyr; PV and BESS combined max export 368: SUMSF_SMIB_V1_Qctrl.dyr; PV and BESS combined max export 369: SUMSF_SMIB_V1_Qctrl.dyr; PV and BESS combined max export 370: SUMSF_SMIB_V1_Qctrl.dyr; BESS only export 371: SUMSF_SMIB_V1_Qctrl.dyr; BESS only export 372: SUMSF_SMIB_V1_Qctrl.dyr; BESS only export 373: SUMSF_SMIB_V1_Qctrl.dyr; BESS only export 374: SUMSF_SMIB_V1_Qctrl.dyr; BESS only export 375: SUMSF_SMIB_V1_Qctrl.dyr; Charging while exporting too 376: SUMSF_SMIB_V1_Qctrl.dyr; Charging while exporting too 377: SUMSF_SMIB_V1_Qctrl.dyr; Charging while exporting too 378: SUMSF_SMIB_V1_Qctrl.dyr; Charging while exporting too 379: SUMSF_SMIB_V1_Qctrl.dyr; Charging while exporting too 380: SUMSF_SMIB_V1_Qctrl.dyr; 0MW dispatch from both 381: SUMSF_SMIB_V1_Qctrl.dyr; 0MW dispatch from both 382: SUMSF_SMIB_V1_Qctrl.dyr; 0MW dispatch from both 383: SUMSF_SMIB_V1_Qctrl.dyr; 0MW dispatch from both 384: SUMSF_SMIB_V1_Qctrl.dyr; 0MW dispatch from both 385: SUMSF_SMIB_V1_Qctrl.dyr; Net zero dispatch while PV charge BESS 386: SUMSF_SMIB_V1_Qctrl.dyr; Net zero dispatch while PV charge BESS 387: SUMSF_SMIB_V1_Qctrl.dyr; Net zero dispatch while PV charge BESS 388: SUMSF_SMIB_V1_Qctrl.dyr; Net zero dispatch while PV charge BESS 389: SUMSF_SMIB_V1_Qctrl.dyr; Net zero dispatch while PV charge BESS 390: SUMSF_SMIB_V1_Qctrl.dyr; BESS Charging from grid and PV 391: SUMSF_SMIB_V1_Qctrl.dyr; BESS Charging from grid and PV 392: SUMSF_SMIB_V1_Qctrl.dyr; BESS Charging from grid and PV 393: SUMSF_SMIB_V1_Qctrl.dyr; BESS Charging from grid and PV 394: SUMSF_SMIB_V1_Qctrl.dyr; BESS Charging from grid and PV 395: SUMSF_SMIB_V1_Qctrl.dyr; BESS charging from Grid only 396: SUMSF_SMIB_V1_Qctrl.dyr; BESS charging from Grid only 397: SUMSF_SMIB_V1_Qctrl.dyr; BESS charging from Grid only 398: SUMSF_SMIB_V1_Qctrl.dyr; BESS charging from Grid only 399: SUMSF_SMIB_V1_Qctrl.dyr; BESS charging from Grid only 400: SUMSF_SMIB_V1_Qctrl.dyr; PV only max export 401: SUMSF_SMIB_V1_PFctrl.dyr; PV only max export 402: SUMSF_SMIB_V1_PFctrl.dyr; PV only max export 403: SUMSF_SMIB_V1_PFctrl.dyr; PV only max export 404: SUMSF_SMIB_V1_PFctrl.dyr; PV only max export 405: SUMSF_SMIB_V1_PFctrl.dyr; PV and BESS combined max export 406: SUMSF_SMIB_V1_PFctrl.dyr; PV and BESS combined max export 407: SUMSF_SMIB_V1_PFctrl.dyr; PV and BESS combined max export 408: SUMSF_SMIB_V1_PFctrl.dyr; PV and BESS combined max export 409: SUMSF_SMIB_V1_PFctrl.dyr; PV and BESS combined max export 410: SUMSF_SMIB_V1_PFctrl.dyr; BESS only export 411: SUMSF_SMIB_V1_PFctrl.dyr; BESS only export 412: SUMSF_SMIB_V1_PFctrl.dyr; BESS only export 413: SUMSF_SMIB_V1_PFctrl.dyr; BESS only export 414: SUMSF_SMIB_V1_PFctrl.dyr; BESS only export 415: SUMSF_SMIB_V1_PFctrl.dyr; Charging while exporting too 416: SUMSF_SMIB_V1_PFctrl.dyr; Charging while exporting too 417: SUMSF_SMIB_V1_PFctrl.dyr; Charging while exporting too 418: SUMSF_SMIB_V1_PFctrl.dyr; Charging while exporting too 419: SUMSF_SMIB_V1_PFctrl.dyr; Charging while exporting too 420: SUMSF_SMIB_V1_PFctrl.dyr; 0MW dispatch from both 421: SUMSF_SMIB_V1_PFctrl.dyr; 0MW dispatch from both 422: SUMSF_SMIB_V1_PFctrl.dyr; 0MW dispatch from both 423: SUMSF_SMIB_V1_PFctrl.dyr; 0MW dispatch from both 424: SUMSF_SMIB_V1_PFctrl.dyr; 0MW dispatch from both 425: SUMSF_SMIB_V1_PFctrl.dyr; Net zero dispatch while PV charge BESS 426: SUMSF_SMIB_V1_PFctrl.dyr; Net zero dispatch while PV charge BESS 427: SUMSF_SMIB_V1_PFctrl.dyr; Net zero dispatch while PV charge BESS 428: SUMSF_SMIB_V1_PFctrl.dyr; Net zero dispatch while PV charge BESS 429: SUMSF_SMIB_V1_PFctrl.dyr; Net zero dispatch while PV charge BESS 430: SUMSF_SMIB_V1_PFctrl.dyr; BESS Charging from grid and PV 431: SUMSF_SMIB_V1_PFctrl.dyr; BESS Charging from grid and PV 432: SUMSF_SMIB_V1_PFctrl.dyr; BESS Charging from grid and PV 433: SUMSF_SMIB_V1_PFctrl.dyr; BESS Charging from grid and PV 434: SUMSF_SMIB_V1_PFctrl.dyr; BESS Charging from grid and PV 435: SUMSF_SMIB_V1_PFctrl.dyr; BESS charging from Grid only 436: SUMSF_SMIB_V1_PFctrl.dyr; BESS charging from Grid only 437: SUMSF_SMIB_V1_PFctrl.dyr; BESS charging from Grid only 438: SUMSF_SMIB_V1_PFctrl.dyr; BESS charging from Grid only 439: SUMSF_SMIB_V1_PFctrl.dyr; BESS charging from Grid only 440: SUMSF_SMIB_V1_PFctrl.dyr; PV only max export 481: SUMSF_SMIB_V1_Qctrl.dyr; PV only max export 482: SUMSF_SMIB_V1_Qctrl.dyr; PV only max export 483: SUMSF_SMIB_V1_Qctrl.dyr; PV only max export 484: SUMSF_SMIB_V1_Qctrl.dyr; PV only max export 485: SUMSF_SMIB_V1_Qctrl.dyr; PV and BESS combined max export 486: SUMSF_SMIB_V1_Qctrl.dyr; PV and BESS combined max export 487: SUMSF_SMIB_V1_Qctrl.dyr; PV and BESS combined max export 488: SUMSF_SMIB_V1_Qctrl.dyr; PV and BESS combined max export 489: SUMSF_SMIB_V1_Qctrl.dyr; PV and BESS combined max export 490: SUMSF_SMIB_V1_Qctrl.dyr; BESS only export 491: SUMSF_SMIB_V1_Qctrl.dyr; BESS only export 492: SUMSF_SMIB_V1_Qctrl.dyr; BESS only export 493: SUMSF_SMIB_V1_Qctrl.dyr; BESS only export 494: SUMSF_SMIB_V1_Qctrl.dyr; BESS only export 495: SUMSF_SMIB_V1_Qctrl.dyr; Charging while exporting too 496: SUMSF_SMIB_V1_Qctrl.dyr; Charging while exporting too 497: SUMSF_SMIB_V1_Qctrl.dyr; Charging while exporting too 498: SUMSF_SMIB_V1_Qctrl.dyr; Charging while exporting too 499: SUMSF_SMIB_V1_Qctrl.dyr; Charging while exporting too 500: SUMSF_SMIB_V1_Qctrl.dyr; 0MW dispatch from both 501: SUMSF_SMIB_V1_Qctrl.dyr; 0MW dispatch from both 502: SUMSF_SMIB_V1_Qctrl.dyr; 0MW dispatch from both 503: SUMSF_SMIB_V1_Qctrl.dyr; 0MW dispatch from both 504: SUMSF_SMIB_V1_Qctrl.dyr; 0MW dispatch from both 505: SUMSF_SMIB_V1_Qctrl.dyr; Net zero dispatch while PV charge BESS 506: SUMSF_SMIB_V1_Qctrl.dyr; Net zero dispatch while PV charge BESS 507: SUMSF_SMIB_V1_Qctrl.dyr; Net zero dispatch while PV charge BESS 508: SUMSF_SMIB_V1_Qctrl.dyr; Net zero dispatch while PV charge BESS 509: SUMSF_SMIB_V1_Qctrl.dyr; Net zero dispatch while PV charge BESS 510: SUMSF_SMIB_V1_Qctrl.dyr; BESS Charging from grid and PV 511: SUMSF_SMIB_V1_Qctrl.dyr; BESS Charging from grid and PV 512: SUMSF_SMIB_V1_Qctrl.dyr; BESS Charging from grid and PV 513: SUMSF_SMIB_V1_Qctrl.dyr; BESS Charging from grid and PV 514: SUMSF_SMIB_V1_Qctrl.dyr; BESS Charging from grid and PV 515: SUMSF_SMIB_V1_Qctrl.dyr; BESS charging from Grid only 516: SUMSF_SMIB_V1_Qctrl.dyr; BESS charging from Grid only 517: SUMSF_SMIB_V1_Qctrl.dyr; BESS charging from Grid only 518: SUMSF_SMIB_V1_Qctrl.dyr; BESS charging from Grid only 519: SUMSF_SMIB_V1_Qctrl.dyr; BESS charging from Grid only 520: SUMSF_SMIB_V1_Qctrl.dyr; PV only max export 521: SUMSF_SMIB_V1_PFctrl.dyr; PV only max export 522: SUMSF_SMIB_V1_PFctrl.dyr; PV only max export 523: SUMSF_SMIB_V1_PFctrl.dyr; PV only max export 524: SUMSF_SMIB_V1_PFctrl.dyr; PV only max export 525: SUMSF_SMIB_V1_PFctrl.dyr; PV and BESS combined max export 526: SUMSF_SMIB_V1_PFctrl.dyr; PV and BESS combined max export 527: SUMSF_SMIB_V1_PFctrl.dyr; PV and BESS combined max export 528: SUMSF_SMIB_V1_PFctrl.dyr; PV and BESS combined max export 529: SUMSF_SMIB_V1_PFctrl.dyr; PV and BESS combined max export 530: SUMSF_SMIB_V1_PFctrl.dyr; BESS only export 531: SUMSF_SMIB_V1_PFctrl.dyr; BESS only export 532: SUMSF_SMIB_V1_PFctrl.dyr; BESS only export 533: SUMSF_SMIB_V1_PFctrl.dyr; BESS only export 534: SUMSF_SMIB_V1_PFctrl.dyr; BESS only export 535: SUMSF_SMIB_V1_PFctrl.dyr; Charging while exporting too 536: SUMSF_SMIB_V1_PFctrl.dyr; Charging while exporting too 537: SUMSF_SMIB_V1_PFctrl.dyr; Charging while exporting too 538: SUMSF_SMIB_V1_PFctrl.dyr; Charging while exporting too 539: SUMSF_SMIB_V1_PFctrl.dyr; Charging while exporting too 540: SUMSF_SMIB_V1_PFctrl.dyr; 0MW dispatch from both 541: SUMSF_SMIB_V1_PFctrl.dyr; 0MW dispatch from both 542: SUMSF_SMIB_V1_PFctrl.dyr; 0MW dispatch from both 543: SUMSF_SMIB_V1_PFctrl.dyr; 0MW dispatch from both 544: SUMSF_SMIB_V1_PFctrl.dyr; 0MW dispatch from both 545: SUMSF_SMIB_V1_PFctrl.dyr; Net zero dispatch while PV charge BESS 546: SUMSF_SMIB_V1_PFctrl.dyr; Net zero dispatch while PV charge BESS 547: SUMSF_SMIB_V1_PFctrl.dyr; Net zero dispatch while PV charge BESS 548: SUMSF_SMIB_V1_PFctrl.dyr; Net zero dispatch while PV charge BESS 549: SUMSF_SMIB_V1_PFctrl.dyr; Net zero dispatch while PV charge BESS 550: SUMSF_SMIB_V1_PFctrl.dyr; BESS Charging from grid and PV 551: SUMSF_SMIB_V1_PFctrl.dyr; BESS Charging from grid and PV 552: SUMSF_SMIB_V1_PFctrl.dyr; BESS Charging from grid and PV 553: SUMSF_SMIB_V1_PFctrl.dyr; BESS Charging from grid and PV 554: SUMSF_SMIB_V1_PFctrl.dyr; BESS Charging from grid and PV 555: SUMSF_SMIB_V1_PFctrl.dyr; BESS charging from Grid only 556: SUMSF_SMIB_V1_PFctrl.dyr; BESS charging from Grid only 557: SUMSF_SMIB_V1_PFctrl.dyr; BESS charging from Grid only 558: SUMSF_SMIB_V1_PFctrl.dyr; BESS charging from Grid only 559: SUMSF_SMIB_V1_PFctrl.dyr; BESS charging from Grid only 560: SUMSF_SMIB_V1_PFctrl.dyr
PSCAD-specific | Name | ProjectNo | Module | PSCAD ID | Symbol
| GridSource | Project1 | Main | 1927070795 | SCL | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 357 | 595 | 595 | 595 | 595 | 595 | 595 | 595 | 595 | 595 | 595 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 1190 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 483 | 1109 | 483 | 1109 | 483 | 1109 | 483 | 1109 | 357 | 357 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 357 | 1190 | 357 | 1190 | 357 | 1190 | 357 | 1190 | 1189881 | 1189881 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 132220.9 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 1109 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 839.1 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999
| GridSource | Project1 | Main | 1927070795 | X_R | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3 | 3.77 | 3 | 3.77 | 3 | 3.77 | 14 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 14 | 14 | 14 | 14 | 3 | 3 | 3 | 3 | 3 | 14 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| V setpoint | Project1 | Main | 163769877 | VstpDefault | 1.03 | 1.0804 | 0.97962 | 1.0993 | 0.96067 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 1.03 | 1.03 | 1.0804 | 0.97962 | 1.0993 | 0.96067 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 1.03 | 1.03 | 1.0804 | 0.97962 | 1.0993 | 0.96067 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 1.03 | 1.03 | 1.0804 | 0.97962 | 1.0993 | 0.96067 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 1.03 | 1.03 | 1.0804 | 0.97962 | 1.0993 | 0.96067 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 1.03 | 1.03 | 1.0804 | 0.97962 | 1.0993 | 0.96067 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 1.03 | 1.03 | 1.0804 | 0.97962 | 1.0993 | 0.96067 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 1.03 | 1.03 | 1.0804 | 0.97962 | 1.0993 | 0.96067 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 1.03 | 1.03 | 1.0804 | 0.97962 | 1.0993 | 0.96067 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 1.03 | 1.03 | 1.0804 | 0.97962 | 1.0993 | 0.96067 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 1.03 | 1.03 | 1.0804 | 0.97962 | 1.0993 | 0.96067 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 1.03 | 1.03 | 1.0804 | 0.97962 | 1.0993 | 0.96067 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 0.96367 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 1.02 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 0.96367 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 1.02 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 0.96367 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 1.02 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.02 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 0.96367 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 1.02 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 0.96367 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 1.02 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 0.96367 | 1.03 | 1.0804 | 0.97962 | 1.0963 | 1.02 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984 | 1.02 | 1.0581 | 0.9819 | 1.0702 | 0.96984
| Q setpoint | Project1 | Main | 163769877 | QstpDefault | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395 | 0 | 0.3 | -0.3 | 0.395 | -0.395
| PF setpoint | Project1 | Main | 163769877 | PFstpDefault | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.1644 | -0.1644 | 0.12558 | -0.12558 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.94178 | -0.94178 | 0.90501 | -0.90501 | 1 | 0.85938 | -0.85938 | 0.7872 | -0.7872 | 1 | 2.8011e-07 | -2.8011e-07 | 2.1274e-07 | -2.1274e-07 | 1 | 2.8011e-07 | -2.8011e-07 | 2.1274e-07 | -2.1274e-07 | 1 | 0.81384 | -0.81384 | 0.72859 | -0.72859 | 1 | 0.94178 | -0.94178 | 0.90501 | -0.90501 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.94178 | -0.94178 | 0.90501 | -0.90501 | 1 | 0.85938 | -0.85938 | 0.7872 | -0.7872 | 1 | 2.8011e-07 | -2.8011e-07 | 2.1274e-07 | -2.1274e-07 | 1 | 2.8011e-07 | -2.8011e-07 | 2.1274e-07 | -2.1274e-07 | 1 | 0.81384 | -0.81384 | 0.72859 | -0.72859 | 1 | 0.94178 | -0.94178 | 0.90501 | -0.90501 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.94178 | -0.94178 | 0.90501 | -0.90501 | 1 | 0.85938 | -0.85938 | 0.7872 | -0.7872 | 1 | 2.8011e-07 | -2.8011e-07 | 2.1274e-07 | -2.1274e-07 | 1 | 2.8011e-07 | -2.8011e-07 | 2.1274e-07 | -2.1274e-07 | 1 | 0.81384 | -0.81384 | 0.72859 | -0.72859 | 1 | 0.94178 | -0.94178 | 0.90501 | -0.90501 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.94178 | -0.94178 | 0.90501 | -0.90501 | 1 | 0.85938 | -0.85938 | 0.7872 | -0.7872 | 1 | 2.8011e-07 | -2.8011e-07 | 2.1274e-07 | -2.1274e-07 | 1 | 2.8011e-07 | -2.8011e-07 | 2.1274e-07 | -2.1274e-07 | 1 | 0.81384 | -0.81384 | 0.72859 | -0.72859 | 1 | 0.94178 | -0.94178 | 0.90501 | -0.90501 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.94178 | -0.94178 | 0.90501 | -0.90501 | 1 | 0.85938 | -0.85938 | 0.7872 | -0.7872 | 1 | 2.8011e-07 | -2.8011e-07 | 2.1274e-07 | -2.1274e-07 | 1 | 2.8011e-07 | -2.8011e-07 | 2.1274e-07 | -2.1274e-07 | 1 | 0.81384 | -0.81384 | 0.72859 | -0.72859 | 1 | 0.94178 | -0.94178 | 0.90501 | -0.90501 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.94178 | -0.94178 | 0.90501 | -0.90501 | 1 | 0.85938 | -0.85938 | 0.7872 | -0.7872 | 1 | 2.8011e-07 | -2.8011e-07 | 2.1274e-07 | -2.1274e-07 | 1 | 2.8011e-07 | -2.8011e-07 | 2.1274e-07 | -2.1274e-07 | 1 | 0.81384 | -0.81384 | 0.72859 | -0.72859 | 1 | 0.94178 | -0.94178 | 0.90501 | -0.90501 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.94178 | -0.94178 | 0.90501 | -0.90501 | 1 | 0.85938 | -0.85938 | 0.7872 | -0.7872 | 1 | 2.8011e-07 | -2.8011e-07 | 2.1274e-07 | -2.1274e-07 | 1 | 2.8011e-07 | -2.8011e-07 | 2.1274e-07 | -2.1274e-07 | 1 | 0.81384 | -0.81384 | 0.72859 | -0.72859 | 1 | 0.94178 | -0.94178 | 0.90501 | -0.90501 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.94178 | -0.94178 | 0.90501 | -0.90501 | 1 | 0.85938 | -0.85938 | 0.7872 | -0.7872 | 1 | 2.8011e-07 | -2.8011e-07 | 2.1274e-07 | -2.1274e-07 | 1 | 2.8011e-07 | -2.8011e-07 | 2.1274e-07 | -2.1274e-07 | 1 | 0.81384 | -0.81384 | 0.72859 | -0.72859 | 1 | 0.94178 | -0.94178 | 0.90501 | -0.90501 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.95783 | -0.95783 | 0.93007 | -0.93007 | 1 | 0.94178 | -0.94178 | 0.90501 | -0.90501 | 1 | 0.85938 | -0.85938 | 0.7872 | -0.7872 | 1 | 2.8011e-07 | -2.8011e-07 | 2.1274e-07 | -2.1274e-07 | 1 | 2.8011e-07 | -2.8011e-07 | 2.1274e-07 | -2.1274e-07 | 1 | 0.81384 | -0.81384 | 0.72859 | -0.72859 | 1 | 0.94178 | -0.94178 | 0.90501 | -0.90501
| P setpoint | Project1 | Main | 163769877 | PstpDefault | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.5 | 0.5 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 0.05 | 0.05 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.42017 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034
| P1 setpoint | Project1 | Main | 163769877 | P1stpDefault | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.25 | 0.25 | 0.25 | 0.25 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0 | 0 | 0 | 0 | 0 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | 0 | 0 | 0 | 0 | 0 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 0 | 0 | 0 | 0 | 0 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | 0 | 0 | 0 | 0 | 0 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 0 | 0 | 0 | 0 | 0 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | 0 | 0 | 0 | 0 | 0 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 0 | 0 | 0 | 0 | 0 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | 0 | 0 | 0 | 0 | 0 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 0 | 0 | 0 | 0 | 0 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | 0 | 0 | 0 | 0 | 0 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 0 | 0 | 0 | 0 | 0 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | 0 | 0 | 0 | 0 | 0 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 0 | 0 | 0 | 0 | 0 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | 0 | 0 | 0 | 0 | 0 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 0 | 0 | 0 | 0 | 0 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | 0 | 0 | 0 | 0 | 0 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | 0 | 0 | 0 | 0 | 0 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.4958 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | 0.84034 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | -0.4958 | 0 | 0 | 0 | 0 | 0 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034 | -0.84034
| Irradiance | Project1 | Main | 163769877 | AUXstpDefault | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 500 | 500 | 500 | 500 | 50 | 50 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
| PV Breaker | Project1 | Main | 1857394408 | Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PV switch | Project1 | Main | 2080782626 | Value | bar: AemoMinSCR - Pmax 1 to BESS charging from Grid only 560
| BESS Breaker | Project1 | Main | 1279062394 | Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| INF bus Breaker time | Project1 | Main | 1406746118 | Value | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
| HV_tap | Project1 | Main | 534238275 | Pos0 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 11 | 14 | 8 | 15 | 8 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11 | 12 | 13 | 12 | 14 | 11
| Q Control Mode | Project1 | Main | 1899582292 | FileNum | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Number of BESS INVs | Project1 | Main | 1248158520 | Value | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
| Initial P BESS | Project1 | Main | 1899582292 | BatPwrAtInit | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 29750 | 29750 | 29750 | 29750 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 2975 | 2975 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 0 | 0 | 0 | 0 | 0 | 56050 | 56050 | 56050 | 56050 | 56050 | 95000 | 95000 | 95000 | 95000 | 95000 | -56050 | -56050 | -56050 | -56050 | -56050 | 0 | 0 | 0 | 0 | 0 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | 0 | 0 | 0 | 0 | 0 | 56050 | 56050 | 56050 | 56050 | 56050 | 95000 | 95000 | 95000 | 95000 | 95000 | -56050 | -56050 | -56050 | -56050 | -56050 | 0 | 0 | 0 | 0 | 0 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | 0 | 0 | 0 | 0 | 0 | 56050 | 56050 | 56050 | 56050 | 56050 | 95000 | 95000 | 95000 | 95000 | 95000 | -56050 | -56050 | -56050 | -56050 | -56050 | 0 | 0 | 0 | 0 | 0 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | 0 | 0 | 0 | 0 | 0 | 56050 | 56050 | 56050 | 56050 | 56050 | 95000 | 95000 | 95000 | 95000 | 95000 | -56050 | -56050 | -56050 | -56050 | -56050 | 0 | 0 | 0 | 0 | 0 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | 0 | 0 | 0 | 0 | 0 | 56050 | 56050 | 56050 | 56050 | 56050 | 95000 | 95000 | 95000 | 95000 | 95000 | -56050 | -56050 | -56050 | -56050 | -56050 | 0 | 0 | 0 | 0 | 0 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | 0 | 0 | 0 | 0 | 0 | 56050 | 56050 | 56050 | 56050 | 56050 | 95000 | 95000 | 95000 | 95000 | 95000 | -56050 | -56050 | -56050 | -56050 | -56050 | 0 | 0 | 0 | 0 | 0 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | 0 | 0 | 0 | 0 | 0 | 56050 | 56050 | 56050 | 56050 | 56050 | 95000 | 95000 | 95000 | 95000 | 95000 | -56050 | -56050 | -56050 | -56050 | -56050 | 0 | 0 | 0 | 0 | 0 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | 0 | 0 | 0 | 0 | 0 | 56050 | 56050 | 56050 | 56050 | 56050 | 95000 | 95000 | 95000 | 95000 | 95000 | -56050 | -56050 | -56050 | -56050 | -56050 | 0 | 0 | 0 | 0 | 0 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | 0 | 0 | 0 | 0 | 0 | 56050 | 56050 | 56050 | 56050 | 56050 | 95000 | 95000 | 95000 | 95000 | 95000 | -56050 | -56050 | -56050 | -56050 | -56050 | 0 | 0 | 0 | 0 | 0 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000 | -95000
| Initial Q BESS | Project1 | Main | 1899582292 | BatPwrRtInit | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375
| Initial P PV | Project1 | Main | 1899582292 | PvPwrAtInit | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 29750 | 29750 | 29750 | 29750 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 2975 | 2975 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 59500 | 59500 | 59500 | 59500 | 59500 | 2975 | 2975 | 2975 | 2975 | 2975 | 113050 | 113050 | 113050 | 113050 | 113050 | 57000 | 57000 | 57000 | 57000 | 57000 | 0 | 0 | 0 | 0 | 0 | 113050 | 113050 | 113050 | 113050 | 113050 | 0 | 0 | 0 | 0 | 0 | 95000 | 95000 | 95000 | 95000 | 95000 | 47500 | 47500 | 47500 | 47500 | 47500 | 0 | 0 | 0 | 0 | 0 | 113050 | 113050 | 113050 | 113050 | 113050 | 57000 | 57000 | 57000 | 57000 | 57000 | 0 | 0 | 0 | 0 | 0 | 113050 | 113050 | 113050 | 113050 | 113050 | 0 | 0 | 0 | 0 | 0 | 95000 | 95000 | 95000 | 95000 | 95000 | 47500 | 47500 | 47500 | 47500 | 47500 | 0 | 0 | 0 | 0 | 0 | 113050 | 113050 | 113050 | 113050 | 113050 | 57000 | 57000 | 57000 | 57000 | 57000 | 0 | 0 | 0 | 0 | 0 | 113050 | 113050 | 113050 | 113050 | 113050 | 0 | 0 | 0 | 0 | 0 | 95000 | 95000 | 95000 | 95000 | 95000 | 47500 | 47500 | 47500 | 47500 | 47500 | 0 | 0 | 0 | 0 | 0 | 113050 | 113050 | 113050 | 113050 | 113050 | 57000 | 57000 | 57000 | 57000 | 57000 | 0 | 0 | 0 | 0 | 0 | 113050 | 113050 | 113050 | 113050 | 113050 | 0 | 0 | 0 | 0 | 0 | 95000 | 95000 | 95000 | 95000 | 95000 | 47500 | 47500 | 47500 | 47500 | 47500 | 0 | 0 | 0 | 0 | 0 | 113050 | 113050 | 113050 | 113050 | 113050 | 57000 | 57000 | 57000 | 57000 | 57000 | 0 | 0 | 0 | 0 | 0 | 113050 | 113050 | 113050 | 113050 | 113050 | 0 | 0 | 0 | 0 | 0 | 95000 | 95000 | 95000 | 95000 | 95000 | 47500 | 47500 | 47500 | 47500 | 47500 | 0 | 0 | 0 | 0 | 0 | 113050 | 113050 | 113050 | 113050 | 113050 | 57000 | 57000 | 57000 | 57000 | 57000 | 0 | 0 | 0 | 0 | 0 | 113050 | 113050 | 113050 | 113050 | 113050 | 0 | 0 | 0 | 0 | 0 | 95000 | 95000 | 95000 | 95000 | 95000 | 47500 | 47500 | 47500 | 47500 | 47500 | 0 | 0 | 0 | 0 | 0 | 113050 | 113050 | 113050 | 113050 | 113050 | 57000 | 57000 | 57000 | 57000 | 57000 | 0 | 0 | 0 | 0 | 0 | 113050 | 113050 | 113050 | 113050 | 113050 | 0 | 0 | 0 | 0 | 0 | 95000 | 95000 | 95000 | 95000 | 95000 | 47500 | 47500 | 47500 | 47500 | 47500 | 0 | 0 | 0 | 0 | 0 | 113050 | 113050 | 113050 | 113050 | 113050 | 57000 | 57000 | 57000 | 57000 | 57000 | 0 | 0 | 0 | 0 | 0 | 113050 | 113050 | 113050 | 113050 | 113050 | 0 | 0 | 0 | 0 | 0 | 95000 | 95000 | 95000 | 95000 | 95000 | 47500 | 47500 | 47500 | 47500 | 47500 | 0 | 0 | 0 | 0 | 0 | 113050 | 113050 | 113050 | 113050 | 113050 | 57000 | 57000 | 57000 | 57000 | 57000 | 0 | 0 | 0 | 0 | 0 | 113050 | 113050 | 113050 | 113050 | 113050 | 0 | 0 | 0 | 0 | 0 | 95000 | 95000 | 95000 | 95000 | 95000 | 47500 | 47500 | 47500 | 47500 | 47500 | 0 | 0 | 0 | 0 | 0
| Initial Q PV | Project1 | Main | 1899582292 | PvPwrRtInit | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 17850 | -17850 | 23502.5 | -23502.5 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375 | 0 | 16957.5 | -16957.5 | 22327.375 | -22327.375
Note on G4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Min from Transgrid: 251.5 Withstand value: 1.2*90 = 108
Note on F10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Q contribution from INV1 (at terminal). Leave empty if initialise with values for two branches below.
Note on F13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: to be specified in MW Reply: P at POC
Note on F25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: transformer tap settinngs are not required to be provided, but can be provided explicitly in the given format to enforce a specific tap setting.
Note on G38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on GY38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on IM38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on KA38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LO38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on NC38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on OQ38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on QE38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on RS38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on TG38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on G39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on GY39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on IM39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on KA39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on LO39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on NC39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on OQ39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on QE39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on RS39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on TG39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: on; 0: off
Note on G40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on GY40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on IM40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on KA40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LO40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on NC40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on OQ40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on QE40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on RS40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on TG40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on G41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Time to open CB (sec)
Note on GY41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on IM41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on KA41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on LO41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on NC41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on OQ41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on QE41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on RS41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open
Note on TG41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: close; 1: open

## Profiles
category
profile name | MAT_V_STEP_Fig3 |  | MAT_V_STEP_Fig8 |  | MAT_V_STEP_Fig9 |  | MAT_V_STEP_Fig10.1 |  | MAT_V_STEP_Fig10.2 |  | MAT_V_STEP_Fig10.3 |  | MAT_VREF_STEP_Fig2 |  | MAT_QREF_STEP_Fig4 |  | MAT_QREF_STEP_Fig4.1 |  | MAT_P_STEP_Fig5 |  | MAT_ANG_STEP+/-20deg |  | MAT_ANG_STEP+/-40deg |  | MAT_ANG_STEP+/-60deg |  | MAT_ANG_STEP |  | MAT_P_STEP_Fig12 |  | AVAIL_P_-20% |  | AVAIL_P_+20% |  | MAT_F_RAMP_4Hzs |  | MAT_F_RAMP_2Hzs |  | MAT_P_STEP |  | V_STP_STEP_+/-5% |  | V_STEP_+/-5% |  | V_STP_STEP_-/+5% |  | V_STEP_-/+5% |  | P_STEP_+25% |  | P_STEP_+75% |  | P_STEP_-25% |  | P_STEP_-75% |  | F_RAMP_+/-1Hz_4Hzs |  | F_PROFILE_Fig6_1 |  | F_PROFILE_Fig6_2 |  | F_PROFILE_Fig6_3 |  | F_PROFILE_Fig6_4 |  | F_PROFILE_Fig7_1 |  | F_PROFILE_Fig7_2 |  | S5.2.5.3_47Hz |  | FLAT_RUN_300 |  | FLAT_RUN_5 |  | FLAT_RUN_12 |  | FLAT_RUN_lowSCR_Qmax |  | FLAT_RUN_lowSCR_Qmin |  | S5253_UF |  | S5253_OF |  | S5253_UF_short |  | S5253_OF_short |  | S5253_+/-1Hz_4Hzs |  | S5254_LVRT |  | S5254_LVRT_Qmin |  | S5254_LVRT_Qmax |  | S5254_HVRT |  | S5254_HVRT_Qmin |  | S5254_HVRT_Qmax |  | S5254_090_CUO |  | S5254_110_CUO |  | S5254_090_CUO_short |  | S5254_110_CUO_short |  | S5254_115 |  | S5254_090_AEMO |  | S5254_080_AEMO |  | S5257_OF_ShedLoad |  | S5258_OF_TRIP |  | S5258_UF_TRIP |  | S5258_OV_TRIP |  | S5258_UV_TRIP |  | S5258_UF_46.8Hz |  | S5258_OV_130 |  | S5258_OV_123 |  | S5258_OV_120 |  | S5258_UV_85 |  | S5258_UV_79 |  | S5258_UV_50 |  | S52511_F_db_up |  | S52511_F_db_dwn |  | S52511_+1Hz |  | S52511_-1Hz |  | S52511_F_db |  | S52511_+/-1Hz |  | S52511_AEMO |  | S52513_V0+/-5% |  | S52513_Vmax-2.5%/+5% |  | S52513_Vmin+2.5%/-5% |  | S52513_Q0+/-15 |  | S52513_Qmax-10/+20 |  | S52513_Qmin+10/-20 |  | S52513_PF0+/-0.02 |  | S52513_PFMax-0.01/+0.03 |  | S52513_PFMin+0.01/-0.03 |  | S52513_V_STEP_+/-5% |  | S52514_-/+50% |  | S52514_AEMO |  | S52514_AEMO_2 |  | LowSCR_V0-/+5% |  | LowSCR_V0-5% |  | LowSCR_V0-10% |  | LowSCR_V_inf |  | S52513_Network_up |  | S52513_Network_down
Scaling: the setpoint profiles: will be scaled using the bases defined in the context menu of the Setpoint block if the selected option is "absolute". If the selected option is "relative", the profile will be based on the initial value from the "setpoints" sheet. This can be useful for applying X% variation to a quantity. For the Grid source profiles: the voltage will be scaled on basekV defined in the context menu of the GridSourceBlock (absolute) or based on the initial voltage (relative). The frequency is always absolute and expressed in Hz and the setting is ignored THe Angle Profile will always be in degrees relative to the initial value, henve the setting is also ignored | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative |  | absolute |  | absolute |  | relative |  | relative |  | relative |  | relative |  |  |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | relative |  | absolute |  | relative |  | absolute |  | relative |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute | [15 empty] | relative |  | relative |  | absolute |  | relative |  | relative | [9 empty] | absolute |  | relative |  | relative |  | relative |  | relative |  | relative |  | relative | [53 empty] | relative |  | relative |  | relative |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | relative |  | relative |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | absolute |  | relative |  | relative
scaling factor (PSCAD / PSSE) |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | 1 | 1 | 1 | 90000 | 1 | 90000 | 1 | 1 | [8 empty] | 1 | 90000 | 0.33578 | 0.00041667 | 0.3415 | 0.00041667 | [5 empty] | 1 | [122 empty] | 0.011111 | 1000 | 0.011111 | 1000 | 0.011111 | 1000 |  | 1 |  | 1 |  | 1 | [5 empty] | 90000 |  | 90000
offset (PSCAD / PSSE) | [30 empty] | 0 |  | 0
| time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y | time | Y
point 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 1000 | 0 | 1000 | 0 | 50 | 0 | 50 | 0 | 1 | 0 | 1.06 | 0 | 1 | 0 | 1.06 | 0 | 1 | 0 | 0.05 | 0 | 0.05 | 0 | 1 | 0 | 1 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 1 | 0 | 1 | 0 | 1.04 | 0 | 1.08 | 0 | 0.85 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 1 | 0 | 1 | 0 | 50 | 0 | 0.99917 | 0 | 0.99917 | 0 | 0.99917 | 0 | 0.99917 | 0 | 0.99917 | 0 | 0.99917 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 50 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 35.55 | 0 | -35.55 | 0 | 1 | 0 | 0.93 | 0 | -0.93 | 0 | 1 | 0 | 1 | 0 | 0.5 | 0 | -0.5 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0.95 | 0 | 1 | 0 | 1
point 2 | 7 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 0 | 5 | 0 | 5 | 1 | 5 | 20 | 5 | 40 | 5 | 60 | 5 | 20 | 5 | 0.05 | 5 | 1000 | 0.5 | 1000 | 5 | 50 | 5 | 50 | 5 | 1 | 5 | 1.06 | 5 | 1 | 5 | 1.06 | 5 | 1 | 5 | 0.05 | 5 | 0.05 | 5 | 1 | 5 | 1 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 2 | 1 | 2 | 1 | 2 | 1.04 | 2.2 | 1.02 | 2.2 | 0.95 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 1 | 5 | 1 | 5 | 50 | 5 | 0.99917 | 5 | 0.99917 | 5 | 0.99917 | 5 | 0.99917 | 5 | 0.99917 | 5 | 0.99917 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 50 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 0 | 5 | 35.55 | 5 | -35.55 | 5 | 1 | 5 | 0.93 | 5 | -0.93 | 5 | 1 | 5 | 1 | 5 | 0.5 | 5 | -0.5 | 10 | 1 | 10 | 1 | 10 | 1 | 5 | 0.95 | 5 | 1 | 5 | 1
. | 7.001 | 1.05 | 11 | 0.9 | 5.001 | 1.1 | 5.001 | 0.1 | 5.001 | 0.5 | 5.001 | 0.8 | 5.001 | 1.05 | 5.001 | -0.3 | 5.001 | -0.15 | 5.001 | 0.5 | 15 | 0 | 15 | 0 | 15 | 0 | 15 | 0 | 5.001 | 0.2 | 15 | 800 | 0.51 | 500 | 5.5 | 52 | 6 | 52 | 7 | 1 | 5.001 | 1.114 | 5.001 | 1.05 | 5.001 | 1.007 | 5.001 | 0.95 | 5.001 | 0.3 | 5.001 | 0.8 | 5.001 | 0.75 | 5.001 | 0.25 | 5.5 | 51 | 5.5 | 52 | 5.4375 | 51.75 | 5.375 | 51.5 | 8 | 52 | 5.75 | 47 | 8 | 47 | 5.75 | 47 | 300 | 1 | 5 | 1 | 12 | 1.04 | 2.5 | 1 | 2.5 | 1 | 5.75 | 47 | 5.5 | 52 | 5.75 | 47 | 5.5 | 52 | 5.25 | 51 | 5.001 | 0.7 | 5.001 | 0.7 | 5.001 | 0.7 | 5.001 | 1.35 | 5.001 | 1.35 | 5.001 | 1.35 | 5.001 | 0.9 | 5.001 | 1.1 | 5.001 | 0.9 | 5.001 | 1.1 | 5.001 | 1.15 | 5.001 | 0.9 | 5.001 | 0.8 | 5.5 | 50.5 | 5.5 | 53 | 5.5 | 46 | 5.5 | 1.8 | 5.5 | 0.1 | 5.5 | 46.8 | 5.001 | 1.4 | 5.001 | 1.3 | 5.001 | 1.2 | 5.001 | 0.8 | 5.001 | 0.6 | 5.001 | 0.3 | 5.5 | 50.015 | 5.5 | 49.985 | 5.5 | 51 | 5.5 | 49 | 5.5 | 50.015 | 5.5 | 51 | 5.5 | 47.5 | 5.001 | 1.05 | 5.001 | 0.975 | 5.001 | 1.025 | 5.001 | -15 | 5.001 | 25.55 | 5.001 | -25.55 | 5.001 | 0.98 | 5.001 | 0.94 | 5.001 | -0.94 | 5.001 | 1.05 | 15 | 0.5 | 5.001 | 0.25 | 5.001 | -0.25 | 10.001 | 0.95 | 10.001 | 0.95 | 10.001 | 0.9 | 5.001 | 1.02 | 5.001 | 1.05 | 5.001 | 0.95
. | 17 | 1.05 | 20 | 0.9 | 15 | 1.1 | 5.43 | 0.1 | 5.43 | 0.5 | 5.43 | 0.8 | 15 | 1.05 | 15 | -0.3 | 15 | -0.15 | 15 | 0.5 | 30 | 0 | 30 | 0 | 30 | 0 | 30 | 0 | 10 | 0.2 | 20 | 800 | 5 | 500 | 15 | 52 | 15 | 52 | 7.001 | 0.8 | 12.5 | 1.113 | 12.5 | 1.05 | 12.5 | 1.007 | 12.5 | 0.95 | 10 | 0.3 | 10 | 0.8 | 10 | 0.75 | 10 | 0.25 | 15 | 51 | 15 | 52 | 15 | 51.75 | 15 | 51.5 | 15 | 52 | 15 | 47 | 15 | 47 | 600.75 | 47 | [6 empty] | 5 | 1 | 5 | 1 | 125.75 | 47 | 605.5 | 52 | 15.75 | 47 | 15.5 | 52 | 15 | 51 | 7 | 0.7 | 7 | 0.7 | 7 | 0.7 | 5.02 | 1.35 | 5.02 | 1.35 | 5.02 | 1.35 | 605 | 0.9 | 605 | 1.1 | 30 | 0.9 | 30 | 1.1 | 605 | 1.15 | 55 | 0.9 | 15 | 0.8 | 15.5 | 50.5 | 70.5 | 53 | 70.5 | 46 | 15.5 | 1.8 | 15.5 | 0.1 | 6.5 | 46.8 | 10 | 1.4 | 10 | 1.3 | 30 | 1.2 | 20 | 0.8 | 10 | 0.6 | 10 | 0.3 | 10.5 | 50.015 | 10.5 | 49.985 | 10.5 | 51 | 10.5 | 49 | 10.5 | 50.015 | 10.5 | 51 | 30 | 47.5 | 12.5 | 1.05 | 12.5 | 0.975 | 12.5 | 1.025 | 12.5 | -15 | 12.5 | 25.55 | 12.5 | -25.55 | 12.5 | 0.98 | 12.5 | 0.94 | 12.5 | -0.94 | 12.5 | 1.05 | 25 | 0.5 | 15 | 0.25 | 15 | -0.25 | 15 | 0.95 | 10.04 | 0.95 | 10.04 | 0.9 | 20 | 1.02 | 15 | 1.05 | 15 | 0.95
. | 17.001 | 1 | 26 | 1.1 | 15.01 | 0.9 | 5.431 | 0.8 | 5.431 | 0.8 | 5.431 | 0.8 | 15.001 | 1 | 15.001 | 0 | 15.001 | 0 | 15.001 | 0.05 | [8 empty] | 10.001 | 0.4 |  |  | 15 | 700 | 15.5 | 50 | 16 | 50 | 12 | 0.8 | 12.5001 | 1.06 | 12.5001 | 1 | 12.5001 | 1.06 | 12.5001 | 1 | 10.001 | 0.05 | 10.001 | 0.05 | 10.001 | 1 | 10.001 | 1 | 15.5 | 50 | 15.5 | 50 | 15.4375 | 50 | 15.375 | 50 | 18 | 50 | 15.75 | 50 | 18 | 50 | 606.5 | 50 | [10 empty] | 126 | 48 | 606 | 50 | 16 | 48 | 16 | 50 | 15.25 | 50 | 7.001 | 0.8 | 7.001 | 0.8 | 7.001 | 0.8 | 5.021 | 1.3 | 5.021 | 1.3 | 5.021 | 1.3 | 605.01 | 1 | 605.01 | 1 | 30.01 | 1 | 30.01 | 1 | 605.01 | 1 | 55.01 | 1 | 15.01 | 1 | 16 | 50 | 71 | 50 | 71 | 50 | 16 | 1 | 16 | 1 | 7 | 50 | 10.01 | 0.99917 | 10.01 | 0.99917 | 30.01 | 0.99917 | 20.01 | 0.99917 | 10.01 | 0.99917 | 10.01 | 0.99917 | 11 | 50 | 11 | 50 | 11 | 50 | 11 | 50 | 11 | 50 | 11 | 50 |  |  | 12.5001 | 1 | 12.5001 | 1.05 | 12.5001 | 0.95 | 12.5001 | 0 | 12.5001 | 45.55 | 12.5001 | -45.55 | 12.5001 | 1 | 12.5001 | 0.9 | 12.5001 | -0.9 | 12.5001 | 1 | 35 | 1 | 15.001 | 0 | 15.001 | 0 | 15.001 | 1 | 10.041 | 1 | 10.041 | 1
. | 27 | 1 | 35 | 1.1 | 25 | 0.9 | 6.43 | 1 | 6.43 | 1 | 6.43 | 1 | 25 | 1 | 25 | 0 | 25 | 0 | 25 | 0.05 | [8 empty] | 15 | 0.4 |  |  | 20 | 700 | 25 | 50 | 25 | 50 | 12.001 | 0.6 | 20 | 1.06 | 20 | 1 | 20 | 1.06 | 20 | 1 | 15 | 0.05 | 15 | 0.05 | 15 | 1 | 15 | 1 | 25 | 50 | 28.001 | 50 | 28.001 | 50 | 28.001 | 50 | 28.001 | 50 | 28.001 | 50 | 28.001 | 50 | 616 | 50 | [10 empty] | 605.75 | 48 | 700 | 50 | 25.75 | 48 | 25.5 | 50 | 25 | 50 | 15 | 0.8 | 15 | 0.8 | 15 | 0.8 | 5.2 | 1.3 | 5.2 | 1.3 | 5.2 | 1.3 | 650 | 1 | 650 | 1 | 40 | 1 | 40 | 1 | 700 | 1 | 65 | 1 | 20 | 1 | 20 | 50 | 75 | 50 | 75 | 50 | 20 | 1 | 20 | 1 | 11 | 50 | 15 | 0.99917 | 15 | 0.99917 | 35 | 0.99917 | 25 | 0.99917 | 15 | 0.99917 | 15 | 0.99917 | 15 | 50 | 15 | 50 | 15 | 50 | 15 | 50 | 15 | 50 | 15 | 50 |  |  | 20 | 1 | 20 | 1.05 | 20 | 0.95 | 20 | 0 | 20 | 45.55 | 20 | -45.55 | 20 | 1 | 20 | 0.9 | 20 | -0.9 | 20 | 1 | 45 | 1 | 25 | 0 | 25 | 0 | 20 | 1 | 20 | 1 | 20 | 1
. | 27.001 | 0.95 | 41 | 0.9 | 25.01 | 1.1 | 12 | 1 | 12 | 1 | 12 | 1 | 25.001 | 0.95 | 25.001 | 0.3 | 25.001 | 0.15 | 25.001 | 1 | [8 empty] | 15.001 | 0.6 | [8 empty] | 17 | 0.6 | [42 empty] | 606.25 | 49.5 |  |  | 26.25 | 49.5 |  |  |  |  | 15.001 | 0.9 | 15.001 | 0.9 | 15.001 | 0.9 | 5.201 | 1.25 | 5.201 | 1.25 | 5.201 | 1.25 | [46 empty] | 15.5 | 49.985 | 15.5 | 49 |  |  | 20.001 | 0.95 | 20.001 | 1 | 20.001 | 1 | 20.001 | 15 | 20.001 | 35.55 | 20.001 | -35.55 | 20.001 | -0.98 | 20.001 | 0.93 | 20.001 | -0.93 | 20.001 | 0.95 |  |  | 25.001 | -0.25 | 25.001 | 0.5
. | 37 | 0.95 | 50 | 0.9 | 35 | 1.1 | [6 empty] | 35 | 0.95 | 35 | 0.3 | 35 | 0.15 | 50 | 1 | [8 empty] | 20 | 0.6 | [8 empty] | 17.001 | 0.4 | [42 empty] | 700 | 49.5 |  |  | 35.75 | 49.5 |  |  |  |  | 35 | 0.9 | 35 | 0.9 | 35 | 0.9 | 7 | 1.25 | 7 | 1.25 | 7 | 1.25 | [46 empty] | 20.5 | 49.985 | 20.5 | 49 |  |  | 27.5 | 0.95 | 25 | 1 | 25 | 1 | 27.5 | 15 | 25 | 35.55 | 25 | -35.55 | 27.5 | -0.98 | 25 | 0.93 | 25 | -0.93 | 27.5 | 0.95 |  |  | 35 | -0.25 | 35 | 0.5
. | 37.001 | 1 | 56 | 1 | 35.001 | 1 | [6 empty] | 35.001 | 1 | 35.001 | 0 | 35.001 | 0 | [10 empty] | 20.001 | 0.8 | [8 empty] | 22 | 0.4 | [52 empty] | 35.01 | 1 | 35.01 | 1 | 35.01 | 1 | 7.001 | 1.2 | 7.001 | 1.2 | 7.001 | 1.2 | [46 empty] | 21 | 50 | 21 | 50 |  |  | 27.5001 | 1 |  |  |  |  | 27.5001 | 0 |  |  |  |  | 27.5001 | 1 |  |  |  |  | 27.5001 | 1 |  |  | 35.001 | -0.5 | 35.001 | 1
. | 47 | 1 | 65 | 1 | 45 | 1 | [6 empty] | 45 | 1 | 43 | 0 | 43 | 0 | [10 empty] | 25 | 0.8 | [8 empty] | 22.001 | 0.2 | [52 empty] | 43 | 1 | 43 | 1 | 43 | 1 | 25 | 1.2 | 25 | 1.2 | 25 | 1.2 | [46 empty] | 25 | 50 | 25 | 50 |  |  | 35 | 1 |  |  |  |  | 35 | 0 |  |  |  |  | 35 | 1 |  |  |  |  | 35 | 1 |  |  | 45 | -0.5 | 45 | 1
. | [28 empty] | 25.001 | 1 | [8 empty] | 27 | 0.2 | [58 empty] | 25.001 | 1.15 | 25.001 | 1.15 | 25.001 | 1.15 | [74 empty] | 45.001 | 0.5 | 45.001 | -0.5
. | [28 empty] | 30 | 1 | [8 empty] | 27.001 | 1 | [58 empty] | 35 | 1.15 | 35 | 1.15 | 35 | 1.15 | [74 empty] | 55 | 0.5 | 55 | -0.5
. | [38 empty] | 42 | 1 | [58 empty] | 35.001 | 1 | 35.001 | 1 | 35.001 | 1
point n | [98 empty] | 43 | 1 | 43 | 1 | 43 | 1
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Category always has to be defined in the first column belonging to a new category. Every profile defined in this sheet must have a corresponging category assigned. This is used for the labelling of the output data generated by the test script.
Note on A4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: will only be used if profile type is "absolute" Reply: Used for SMA model as the voltage to be controlled at absolute Volt value
Note on A5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: will only be applied if profile type is "absolute"
Note on FO7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: PSSE: 0 -> Q = tan(0) = 0 PSCAD: 1 -> cos(phi) = 1 -> Q = 0
Note on FO9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: PSSE input: 0.2 -> tan(0.2) PSCAD input: 0.980580676 -> cos(0.980580676)

## SteadyStateStudies
This sheet lists the contingency scenarios to be considered in Steady State studies. + CaseNr: name of the contingency scenarios; If left blank, the event occuring on that row is considered to be in the same scenario above it. + TestType: Contingency (trip, disconnect) or setpoint changes (Generation output changes, voltage change, tap changes) *note: + TestType is contingency, inputs are ini_status and end_status + TestType is setpoint changes, inputs are ini_value and end_value + Element: the element to which contingency is apply; if TestType setpoint change type, then element depends on type of change (e.g. Genchange -> machine; Tap change -> Tx) + i_bus, j_bus, k_bus, id: Connected buses and identification number of the element. If contingency element is a machine or a Shunt, the j_bus and k_bus are not needed. Similarly, k_bus is only used for three winding transformer contingency. + status: either 1 or 0: the element is activated or not - applicable to contingency + value: the specific values implemented - only applicable for setpoint change
CaseNr | TestType | Element | i_bus | j_bus | k_bus | id | ini_status | end_status | ini_value | end_value | run in PSS/E? | CaseDescription | Case_Code | test group | simulation batch
1 | Trip | Line | 215290 | 288090 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Bayswater 500kV and Wollar 500kV_id1 | 2BAYSWT_500A - 2WOLLAR_500A_id1 | trip a line | S52512
2 | Trip | Line | 215290 | 257690 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Bayswater 500kV and Mt Piper 500kV_id1 | 2BAYSWT_500A - 2MTPIPR_500A_id1 | trip a line | S52512
3 | Trip | Line | 275292 | 260890 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Tamworth 330kV and Muswellbrook 330kV_id1 | 2TAMWTH_330C - 2MUSWLB_330A_id1 | trip a line | S52512
| ChgMW | Load | 277690 |  |  | 2 | 1 | 1 |  | 100 | yes | ChgMW Load Tomago_id2 | Trip Load 2TOMAGO_330A_id2 | trip a line | S52512
| ChgMW | Load | 277690 |  |  | 4C | 1 | 1 |  | 100 | yes | ChgMW Load Tomago_id4C | Trip Load 2TOMAGO_330A_id4C | trip a line | S52512
4 | Trip | Line | 211693 | 226893 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Armidale 330kV and Coffs Harbour 330kV_id1 | 2ARMIDL_330D - COFF_330_id1 | trip a line | S52512
5 | Trip | Line | 211690 | 275290 |  | 2 | 1 | 0 |  |  | yes | Trip Line between Armidale 330kV and Tamworth 330kV_id2 | 2ARMIDL_330A - 2TAMWTH_330A_id2 | trip a line | S52512
6 | Trip | Line | 275291 | 249290 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Tamworth 330kV and Liddell 330kV_id1 | 2TAMWTH_330B - 2LIDDEL_330A_id1 | trip a line | S52512
| ChgMW | Load | 277690 |  |  | 2 | 1 | 1 |  | 100 | yes | ChgMW Load Tomago_id2 | Trip Load 2TOMAGO_330A_id2 | trip a line | S52512
| ChgMW | Load | 277690 |  |  | 4C | 1 | 1 |  | 100 | yes | ChgMW Load Tomago_id4C | Trip Load 2TOMAGO_330A_id4C | trip a line | S52512
7 | Trip | Line | 260890 | 249290 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Muswellbrook 330kV and Liddell 330kV_id1 | 2MUSWLB_330A - 2LIDDEL_330A_id1 | trip a line | S52512
8 | Trip | Line | 231691 | 270390 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Dumaresq 330kV and Sapphire WF 330kV_id1 | 2DUMARQ_330B - 2SAPHIR_330A_id1 | trip a line | S52512
9 | Trip | Line | 270390 | 211691 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Sapphire WF 330kV and Armidale 330kV_id1 | 2SAPHIR_330A - 2ARMIDL_330B_id1 | trip a line | S52512
10 | Trip | Line | 231693 | 211692 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Dumaresq 330kV and Armidale 330kV_id1 | 2DUMARQ_330D - 2ARMIDL_330C_id1 | trip a line | S52512
11 | Trip | Line | 226893 | 250491 |  | 1 | 1 | 0 |  |  | no | Trip Line between Coffs Harbour 330kV and Lismore 330kV_id1 | COFF_330 - LSM_330_id1 | trip a line | S52512
12 | Trip | Line | 211690 | 800002 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Armidale 330kV and New England SF POC_id1 | 2ARMIDL_330A - New_England_SF_POC_id1 | trip a line | S52512
13 | Trip | Line | 800002 | 275290 |  | 1 | 1 | 0 |  |  | yes | Trip Line between New England SF POC and Tamworth 330kV_id1 | New_England_SF_POC - 2TAMWTH_330A_id1 | trip a line | S52512
14 | Trip | Line | 275240 | 261640 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Tamworth 132kV and Narrabri 132kV_id1 | 2TAMWTH_132A - 2NARABR_132A_id1 | trip a line | S52512
15 | Trip | Line | 209446 | 218640 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Boggabri East 132kV and Boggabri North 132kV_id1 | 2BOGABR_132G - 2BGNBRY_132A_id1 | trip a line | S52512
16 | Trip | Line | 218640 | 261640 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Boggabri North 132kV and Narrabri 132kV_id1 | 2BGNBRY_132A - 2NARABR_132A_id1 | trip a line | S52512
17 | Trip | Line | 261640 | 257240 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Narrabri 132kV and Moree 132kV_id1 | 2NARABR_132A - 2_MOREE_132A_id1 | trip a line | S52512
18 | Trip | Line | 257240 | 242040 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Moree 132kV and Inverell 132kV_id1 | 2_MOREE_132A - 2INVERL_132A_id1 | trip a line | S52512
19 | Trip | Line | 242040 | 287040 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Inverell 132kV and White Rock 132kV_id1 | 2INVERL_132A - 2WHITER_132A_id1 | trip a line | S52512
20 | Trip | Line | 287040 | 235640 |  | 1 | 1 | 0 |  |  | yes | Trip Line between White Rock 132kV and Glen Innes 132kV_id1 | 2WHITER_132A - 2GLENIN_132A_id1 | trip a line | S52512
21 | Trip | Line | 235640 | 211640 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Glen Innes 132kV and Armidale 132kV_id1 | 2GLENIN_132A - ARM_132_id1 | trip a line | S52512
22 | Trip | Line | 211640 | 242040 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Armidale 132kV and Inverell 132kV_id1 | ARM_132 - 2INVERL_132A_id1 | trip a line | S52512
23 | Trip | Line | 235640 | 276041 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Glen Innes 132kV and Tenterfield 132kV_id1 | 2GLENIN_132A - 2TENTFD_132B_id1 | trip a line | S52512
24 | Trip | Line | 275240 | 800003 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Tamworth 132kV and Tamworth SF POC_id1 | 2TAMWTH_132A - Tamworth_SF_POC_id1 | trip a line | S52512
| Trip | Bus | 2200 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus GUNSF_POC_id1 | Trip Bus GUNSF_POC_id1 | trip a line | S52512
| Trip | Bus | 2300 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus GUNSF_MV2_id1 | Trip Bus GUNSF_MV2_id1 | trip a line | S52512
| Trip | Bus | 2400 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus GUNSF_MV1_id1 | Trip Bus GUNSF_MV1_id1 | trip a line | S52512
| Trip | Bus | 2500 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus GUNSF_GEN_id1 | Trip Bus GUNSF_GEN_id1 | trip a line | S52512
| Trip | Bus | 106 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus TAMSF_POC_id1 | Trip Bus TAMSF_POC_id1 | trip a line | S52512
| Trip | Bus | 105 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus TAMSF_BUS1_id1 | Trip Bus TAMSF_BUS1_id1 | trip a line | S52512
| Trip | Bus | 103 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus TAMSF_BUS2_id1 | Trip Bus TAMSF_BUS2_id1 | trip a line | S52512
| Trip | Bus | 1031 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus TAMSF_BUS3_id1 | Trip Bus TAMSF_BUS3_id1 | trip a line | S52512
| Trip | Bus | 1032 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus TAMSF_BUS4_id1 | Trip Bus TAMSF_BUS4_id1 | trip a line | S52512
| Trip | Bus | 102 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus TAMSF_BUS5_id1 | Trip Bus TAMSF_BUS5_id1 | trip a line | S52512
| Trip | Bus | 101 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus TAMSF_BUS6_id1 | Trip Bus TAMSF_BUS6_id1 | trip a line | S52512
| Trip | Bus | 100 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus TAMSF_GEN_id1 | Trip Bus TAMSF_GEN_id1 | trip a line | S52512
25 | Trip | Line | 800003 | 238441 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Tamworth SF POC and Gunnedah 132kV_id1 | Tamworth_SF_POC - 2GUNDAH_132B_id1 | trip a line | S52512
| Trip | Bus | 106 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus TAMSF_POC_id1 | Trip Bus TAMSF_POC_id1 | trip a line | S52512
| Trip | Bus | 105 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus TAMSF_BUS1_id1 | Trip Bus TAMSF_BUS1_id1 | trip a line | S52512
| Trip | Bus | 103 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus TAMSF_BUS2_id1 | Trip Bus TAMSF_BUS2_id1 | trip a line | S52512
| Trip | Bus | 1031 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus TAMSF_BUS3_id1 | Trip Bus TAMSF_BUS3_id1 | trip a line | S52512
| Trip | Bus | 1032 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus TAMSF_BUS4_id1 | Trip Bus TAMSF_BUS4_id1 | trip a line | S52512
| Trip | Bus | 102 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus TAMSF_BUS5_id1 | Trip Bus TAMSF_BUS5_id1 | trip a line | S52512
| Trip | Bus | 101 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus TAMSF_BUS6_id1 | Trip Bus TAMSF_BUS6_id1 | trip a line | S52512
| Trip | Bus | 100 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus TAMSF_GEN_id1 | Trip Bus TAMSF_GEN_id1 | trip a line | S52512
| Trip | Bus | 2200 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus GUNSF_POC_id1 | Trip Bus GUNSF_POC_id1 | trip a line | S52512
| Trip | Bus | 2300 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus GUNSF_MV2_id1 | Trip Bus GUNSF_MV2_id1 | trip a line | S52512
| Trip | Bus | 2400 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus GUNSF_MV1_id1 | Trip Bus GUNSF_MV1_id1 | trip a line | S52512
| Trip | Bus | 2500 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus GUNSF_GEN_id1 | Trip Bus GUNSF_GEN_id1 | trip a line | S52512
26 | Trip | Line | 238441 | 238740 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Gunnedah 132kV and Gunnedah East_id1 | 2GUNDAH_132B - 2GUN_BO_132A_id1 | trip a line | S52512
| Trip | Bus | 2200 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus GUNSF_POC_id1 | Trip Bus GUNSF_POC_id1 | trip a line | S52512
| Trip | Bus | 2300 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus GUNSF_MV2_id1 | Trip Bus GUNSF_MV2_id1 | trip a line | S52512
| Trip | Bus | 2400 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus GUNSF_MV1_id1 | Trip Bus GUNSF_MV1_id1 | trip a line | S52512
| Trip | Bus | 2500 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus GUNSF_GEN_id1 | Trip Bus GUNSF_GEN_id1 | trip a line | S52512
27 | Trip | Line | 238740 | 800001 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Gunnedah East and Gunnedah SF POC_id1 | 2GUN_BO_132A - Gunnedah_SF_POC_id1 | trip a line | S52512
| Trip | Bus | 2200 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus GUNSF_POC_id1 | Trip Bus GUNSF_POC_id1 | trip a line | S52512
| Trip | Bus | 2300 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus GUNSF_MV2_id1 | Trip Bus GUNSF_MV2_id1 | trip a line | S52512
| Trip | Bus | 2400 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus GUNSF_MV1_id1 | Trip Bus GUNSF_MV1_id1 | trip a line | S52512
| Trip | Bus | 2500 |  |  | 1 | 1 | 0 |  |  | yes | Trip Bus GUNSF_GEN_id1 | Trip Bus GUNSF_GEN_id1 | trip a line | S52512
28 | Trip | Line | 800001 | 209446 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Gunnedah SF POC and Boggabri East 132kV_id1 | Gunnedah_SF_POC - 2BOGABR_132G_id1 | trip a line | S52512
29 | Trip | Line | 276041 | 294840 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Tenterfield 132kV and Casino 132kV_id1 | 2TENTFD_132B - CASN_132_id1 | trip a line | S52512
30 | Trip | Line | 294840 | 250401 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Casino 132kV and Lismore 132kV_id1 | CASN_132 - LSM_132_id1 | trip a line | S52512
31 | Trip | Line | 211640 | 800000 |  | 1 | 1 | 0 |  |  | no | Trip Line between Armidale 132kV and Metz SF POC_id1 | ARM_132 - MSF_132_id1 | trip a line | S52512
32 | Trip | Line | 800000 | 245641 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Metz SF POC and Koolkhan 132kV_id1 | MSF_132 - KOLK_132_id1 | trip a line | S52512
33 | Trip | Line | 245641 | 236942 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Koolkhan 132kV and Graffton East 132kV_id1 | KOLK_132 - GRAF_132_id1 | trip a line | S52512
34 | Trip | Line | 236942 | 226843 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Graffton East 132kV and Coffs Harbour 132kV_id1 | GRAF_132 - COFF_132_id1 | trip a line | S52512
35 | Trip | Line | 250401 | 273540 |  | 1 | 1 | 0 |  |  | yes | Trip Line between Lismore 132kV and SUM_POC_id1 | LSM_132 - SUM_POC_id1 | trip a line | S52512
36 | Trip | Line | 273540 | 245641 |  | 1 | 1 | 0 |  |  | yes | Trip Line between SUM_POC and Koolkhan 132kV_id1 | SUM_POC - KOLK_132_id1 | trip a line | S52512
37 | Trip | Tx_2w | 250490 | 250401 |  | 1 | 1 | 0 |  |  | yes | Trip Tx_2w between Lismore 330kV_A and Lismore 132kV_id1 | LSM_330 - LSM_132_id1 | trip a Tx | S52512
38 | ChgMW | Machine | 273501 |  |  | 1 | 1 | 1 | 91 | 68.25 | yes | ChgMW Machine SUM_LV_PV_id1 | GenChange (100% to 75%) | change generation output | S52512
39 | ChgMW | Machine | 273501 |  |  | 1 | 1 | 1 | 91 | 45.5 | yes | ChgMW Machine SUM_LV_PV_id1 | GenChange (100% to 50%) | change generation output | S52512
40 | ChgMW | Machine | 273501 |  |  | 1 | 1 | 1 | 91 | 22.75 | yes | ChgMW Machine SUM_LV_PV_id1 | GenChange (100% to 25%) | change generation output | S52512
41 | ChgMW | Machine | 273501 |  |  | 1 | 1 | 1 | -46 | -34.5 | yes | ChgMW Machine SUM_LV_PV_id1 | GenChange (-100% to -75%) | change generation output | S52512
42 | ChgMW | Machine | 273501 |  |  | 1 | 1 | 1 | -46 | -23 | yes | ChgMW Machine SUM_LV_PV_id1 | GenChange (-100% to -50%) | change generation output | S52512
43 | ChgMW | Machine | 273501 |  |  | 1 | 1 | 1 | -46 | -11.5 | yes | ChgMW Machine SUM_LV_PV_id1 | GenChange (-100% to -25%) | change generation output | S52512
44 | Trip | Machine | 273501 |  |  | 1 | 1 | 1 | 91 | 0 | yes | Trip Machine SUM_LV_PV_id1 | GenTrip (100% to 0%) | Trip a generator | S52512
|  | Shunt | 273530 |  |  | 1 | 1 | 1 |  | 0 | yes | Shunt SUM_MV_id1 |  | runback | S52512
|  | Shunt | 273530 |  |  | 2 | 1 | 1 |  | 0 | yes | Shunt SUM_MV_id2 |  | runback | S52512
45 | Trip | Machine | 273501 |  |  | 1 | 1 | 1 | 68.25 | 0 | yes | Trip Machine SUM_LV_PV_id1 | GenTrip (75% to 0%) | Trip a generator | S52512
|  | Shunt | 273530 |  |  | 1 | 1 | 1 |  | 0 | yes | Shunt SUM_MV_id1 |  | runback | S52512
|  | Shunt | 273530 |  |  | 2 | 1 | 1 |  | 0 | yes | Shunt SUM_MV_id2 |  | runback | S52512
46 | Trip | Machine | 273501 |  |  | 1 | 1 | 1 | 45.5 | 0 | yes | Trip Machine SUM_LV_PV_id1 | GenTrip (50% to 0%) | Trip a generator | S52512
|  | Shunt | 273530 |  |  | 1 | 1 | 1 |  | 0 | yes | Shunt SUM_MV_id1 |  | runback | S52512
|  | Shunt | 273530 |  |  | 2 | 1 | 1 |  | 0 | yes | Shunt SUM_MV_id2 |  | runback | S52512
47 | Trip | Machine | 273501 |  |  | 1 | 1 | 1 | 22.75 | 0 | yes | Trip Machine SUM_LV_PV_id1 | GenTrip (25% to 0%) | Trip a generator | S52512
|  | Shunt | 273530 |  |  | 1 | 1 | 1 |  | 0 | yes | Shunt SUM_MV_id1 |  | runback | S52512
|  | Shunt | 273530 |  |  | 2 | 1 | 1 |  | 0 | yes | Shunt SUM_MV_id2 |  | runback | S52512
48 | Trip | Machine | 273501 |  |  | 1 | 1 | 1 | -46 | 0 | yes | Trip Machine SUM_LV_PV_id1 | GenTrip (-100% to 0%) | Trip a generator | S52512
|  | Shunt | 273530 |  |  | 1 | 1 | 1 |  | 0 | yes | Shunt SUM_MV_id1 |  | runback | S52512
|  | Shunt | 273530 |  |  | 2 | 1 | 1 |  | 0 | yes | Shunt SUM_MV_id2 |  | runback | S52512
49 | Trip | Machine | 273501 |  |  | 1 | 1 | 1 | -23 | 0 | yes | Trip Machine SUM_LV_PV_id1 | GenTrip (50% to 0%) | Trip a generator | S52512
|  | Shunt | 273530 |  |  | 1 | 1 | 1 |  | 0 | yes | Shunt SUM_MV_id1 |  | runback | S52512
|  | Shunt | 273530 |  |  | 2 | 1 | 1 |  | 0 | yes | Shunt SUM_MV_id2 |  | runback | S52512
50 | FaultCal | Bus | 273540 | [7 empty] | yes | FaultCal Bus SUM_POC_id | SUMSF_high_genon.sav | Fault Level calculations | S528
|  | Bus | 273541 | [7 empty] | yes | Bus SUM_HV_id |  | Fault Level calculations | S528
|  | Bus | 273530 | [7 empty] | yes | Bus SUM_MV_id |  | Fault Level calculations | S528
|  | Bus | 273531 | [7 empty] | yes | Bus SUM_MV_PV_id |  | Fault Level calculations | S528
|  | Bus | 273501 | [7 empty] | yes | Bus SUM_LV_PV_id |  | Fault Level calculations | S528
|  | Bus | 273532 | [7 empty] | yes | Bus SUM_MV_BESS_id |  | Fault Level calculations | S528
|  | Bus | 273502 | [7 empty] | yes | Bus SUM_LV_BESS_id |  | Fault Level calculations | S528
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Consecutive cases. leave empty if it belong to / associated with previous contingency case
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: if Element is a Machine, shunt or Bus, then J_bus = empty
Note on J2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: dedicated for generation output before contingency occurs
Note on K2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: dedicated for generation output after contingency occurs
Note on A6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Need to shed load at Liddell side when tripping line from Tam to Mus (Lid) as the load on the line is80% -> overload the remaining line.
Note on A10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: LL Not converged when executing the contingency
Note on A11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Need to shed load at Liddell side when tripping line from Tam to Mus (Lid) as the load on the line is80% -> overload the remaining line.
Note on A18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Added to account for connection of New England SF 800002
Note on A19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Added to account for connection of New England SF 800002
Note on A22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Added as with bus 294840 in middle
Note on A23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not avaible as with bus 294840 in middle
Note on A24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: added contingency - nearby network
Note on A25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: added contingency - nearby network
Note on A26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: added contingency - nearby network
Note on A27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: added contingency - nearby network
Note on A30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Added as with newly committed Tamworth SF 800003 Reply: Tripping scheme: Trip line 969-0 -> trip Tamworth SF -> trip Gunneah SF
Note on A43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Added as with newly committed Tamworth SF 800003 Reply: Tripping scheme: Trip line 969-0 -> trip Tamworth SF -> trip Gunneah SF
Note on A56: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Added as with newly committed Gunnedah SF 800001 and bus 238740 Reply: Tripping scheme: Trip line 9U3/1-0 -> trip Gunneah SF
Note on A61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Added as with newly committed Gunnedah SF 800001 and bus 238740 Reply: Tripping scheme: Trip line 9U3/2-0 -> trip Gunneah SF
Note on A66: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Added as with newly committed Gunnedah SF 800001 and bus 238740
Note on A67: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Added as with bus 294840 in middle
Note on A68: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not avaible as with bus 294840 in middle
Note on A69: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: added contingency - nearby network
Note on A70: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: added contingency - nearby network
Note on A71: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: added contingency - nearby network
Note on A72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: added contingency - nearby network
Note on A73: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: added contingency - nearby network
Note on A74: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: added contingency - nearby network

## NetworkScenarios
For the contingency comes along with the runback scheme: + Define the contingency with the CaseNr as normal + In the following row, change the option Runback? To 1
CaseNr | Test Type | Test profile | Runback? | Event_Element | Event_Type | Event_Time | F resistance | F reactance | i_bus | j_bus | k_bus | id | location | trip_near | trip_far | arc_time | arc_success | base_kV | run in PSS/E? | CaseDescription | Case_Code | test group | simulation batch
1 | Fault | - | no | Line | 3PHG | 3 |  |  | 215290 | 288090 |  | 1 |  | 0.155 | 0.175 | 15 | 0 | 500 | no | Line fault 2BAYSWT_500A - 2WOLLAR_500A -- 3PHG | Bayswater 500kV_Wollar 500kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
2 | Fault | - | no | Line | 3PHG | 3 |  |  | 215290 | 257690 |  | 1 |  | 0.155 | 0.175 | 15 | 0 | 500 | no | Line fault 2BAYSWT_500A - 2MTPIPR_500A -- 3PHG | Bayswater 500kV_Mt Piper 500kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
3 | Fault | - | no | Line | 3PHG | 3 |  |  | 275292 | 260890 |  | 1 |  | 0.23 | 0.25 | 15 | -1 | 500 | no | Line fault 2TAMWTH_330C - 2MUSWLB_330A -- 3PHG | Tamworth 330kV_Muswellbrook 330kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
4 | Fault | - | no | Line | 3PHG | 3 |  |  | 211693 | 226893 |  | 1 |  | 0.23 | 0.25 | 15 | -1 | 330 | no | Line fault 2ARMIDL_330D - COFF_330 -- 3PHG | Armidale 330kV_Coffs Harbour 330kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
5 | Fault | - | no | Line | 3PHG | 3 |  |  | 211690 | 275290 |  | 2 |  | 0.23 | 0.24 | 15 | -1 | 330 | no | Line fault 2ARMIDL_330A - 2TAMWTH_330A -- 3PHG | Armidale 330kV_Tamworth 330kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
6 | Fault | - | no | Line | 3PHG | 3 |  |  | 275291 | 249290 |  | 1 |  | 0.23 | 0.25 | 15 | -1 | 330 | no | Line fault 2TAMWTH_330B - 2LIDDEL_330A -- 3PHG | Tamworth 330kV_Liddell 330kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
7 | Fault | - | no | Line | 3PHG | 3 |  |  | 260890 | 249290 |  | 1 |  | 0.23 | 0.25 | 15 | -1 | 330 | no | Line fault 2MUSWLB_330A - 2LIDDEL_330A -- 3PHG | Muswellbrook 330kV_Liddell 330kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
8 | Fault | - | no | Line | 3PHG | 3 |  |  | 231691 | 270390 |  | 1 |  | 0.23 | 0.25 | 15 | -1 | 330 | no | Line fault 2DUMARQ_330B - 2SAPHIR_330A -- 3PHG | Dumaresq 330kV_Sapphire WF 330kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
9 | Fault | - | no | Line | 3PHG | 3 |  |  | 270390 | 211691 |  | 1 |  | 0.23 | 0.25 | 15 | -1 | 330 | no | Line fault 2SAPHIR_330A - 2ARMIDL_330B -- 3PHG | Sapphire WF 330kV_Armidale 330kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
10 | Fault | - | no | Line | 3PHG | 3 |  |  | 231693 | 211692 |  | 1 |  | 0.23 | 0.25 | 15 | -1 | 330 | no | Line fault 2DUMARQ_330D - 2ARMIDL_330C -- 3PHG | Dumaresq 330kV_Armidale 330kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
11 | Fault | - | no | Line | 3PHG | 3 |  |  | 226893 | 250491 |  | 1 |  | 0.23 | 0.25 | 15 | -1 | 330 | no | Line fault COFF_330 - LSM_330 -- 3PHG | Coffs Harbour 330kV_Lismore 330kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
12 | Fault | - | no | Line | 3PHG | 3 |  |  | 211690 | 800002 |  | 1 |  | 0.23 | 0.25 | 15 | -1 | 330 | no | Line fault 2ARMIDL_330A - New_England_SF_POC -- 3PHG | Armidale 330kV_New England SF POC | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
13 | Fault | - | no | Line | 3PHG | 3 |  |  | 800002 | 275290 |  | 1 |  | 0.23 | 0.25 | 15 | -1 | 330 | no | Line fault New_England_SF_POC - 2TAMWTH_330A -- 3PHG | New England SF POC_Tamworth 330kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
14 | Fault | - | no | Line | 3PHG | 3 |  |  | 275240 | 261640 |  | 1 |  | 0.33 | 0.365 | 5 | -1 | 132 | no | Line fault 2TAMWTH_132A - 2NARABR_132A -- 3PHG | Tamworth 132kV_Narrabri 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
15 | Fault | - | no | Line | 3PHG | 3 |  |  | 209446 | 218640 |  | 1 |  | 0.33 | 0.36 | 5 | -1 | 132 | no | Line fault 2BOGABR_132G - 2BGNBRY_132A -- 3PHG | Boggabri East 132kV_Boggabri North 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
16 | Fault | - | no | Line | 3PHG | 3 |  |  | 218640 | 261640 |  | 1 |  | 0.33 | 0.365 | 5 | -1 | 132 | no | Line fault 2BGNBRY_132A - 2NARABR_132A -- 3PHG | Boggabri North 132kV_Narrabri 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
17 | Fault | - | no | Line | 3PHG | 3 |  |  | 261640 | 257240 |  | 1 |  | 0.33 | 0.365 | 5 | -1 | 132 | no | Line fault 2NARABR_132A - 2_MOREE_132A -- 3PHG | Narrabri 132kV_Moree 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
18 | Fault | - | no | Line | 3PHG | 3 |  |  | 257240 | 242040 |  | 1 |  | 0.33 | 0.73 | 5 | -1 | 132 | yes | Line fault 2_MOREE_132A - 2INVERL_132A -- 3PHG | Moree 132kV_Inverell 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
19 | Fault | - | no | Line | 3PHG | 3 |  |  | 242040 | 287040 |  | 1 |  | 0.43 | 0.53 | 5 | -1 | 132 | no | Line fault 2INVERL_132A - 2WHITER_132A -- 3PHG | Inverell 132kV_White Rock 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
20 | Fault | - | no | Line | 3PHG | 3 |  |  | 287040 | 235640 |  | 1 |  | 0.43 | 0.53 | 5 | -1 | 132 | no | Line fault 2WHITER_132A - 2GLENIN_132A -- 3PHG | White Rock 132kV_Glen Innes 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
21 | Fault | - | no | Line | 3PHG | 3 |  |  | 235640 | 211640 |  | 1 |  | 0.33 | 0.73 | 5 | -1 | 132 | no | Line fault 2GLENIN_132A - ARM_132 -- 3PHG | Glen Innes 132kV_Armidale 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
22 | Fault | - | no | Line | 3PHG | 3 |  |  | 211640 | 242040 |  | 1 |  | 0.33 | 0.73 | 5 | -1 | 132 | no | Line fault ARM_132 - 2INVERL_132A -- 3PHG | Armidale 132kV_Inverell 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
23 | Fault | - | no | Line | 3PHG | 3 |  |  | 235640 | 276041 |  | 1 |  | 0.33 | 1.77 | 5 | -1 | 132 | no | Line fault 2GLENIN_132A - 2TENTFD_132B -- 3PHG | Glen Innes 132kV_Tenterfield 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
24 | Fault | - | no | Line | 3PHG | 3 |  |  | 275240 | 800003 |  | 1 |  | 0.33 | 0.43 | 5 | -1 | 132 | no | Line fault 2TAMWTH_132A - Tamworth_SF_POC -- 3PHG | Tamworth 132kV_Tamworth SF POC | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
25 | Fault | - | no | Line | 3PHG | 3 |  |  | 800003 | 238441 |  | 1 |  | 0.33 | 0.43 | 5 | -1 | 132 | no | Line fault Tamworth_SF_POC - 2GUNDAH_132B -- 3PHG | Tamworth SF POC_Gunnedah 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
26 | Fault | - | no | Line | 3PHG | 3 |  |  | 238441 | 238740 |  | 1 |  | 0.33 | 0.43 | 5 | -1 | 132 | no | Line fault 2GUNDAH_132B - 2GUN_BO_132A -- 3PHG | Gunnedah 132kV_Gunnedah East | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
27 | Fault | - | no | Line | 3PHG | 3 |  |  | 238740 | 800001 |  | 1 |  | 0.33 | 0.43 | 5 | -1 | 132 | no | Line fault 2GUN_BO_132A - Gunnedah_SF_POC -- 3PHG | Gunnedah East_Gunnedah SF POC | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
28 | Fault | - | no | Line | 3PHG | 3 |  |  | 800001 | 209446 |  | 1 |  | 0.33 | 0.43 | 5 | -1 | 132 | no | Line fault Gunnedah_SF_POC - 2BOGABR_132G -- 3PHG | Gunnedah SF POC_Boggabri East 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
29 | Fault | - | no | Line | 3PHG | 3 |  |  | 276041 | 294840 |  | 1 |  | 0.33 | 0.43 | 5 | -1 | 132 | no | Line fault 2TENTFD_132B - CASN_132 -- 3PHG | Tenterfield 132kV_Casino 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
30 | Fault | - | no | Line | 3PHG | 3 |  |  | 294840 | 250401 |  | 1 |  | 0.33 | 0.43 | 5 | -1 | 132 | no | Line fault CASN_132 - LSM_132 -- 3PHG | Casino 132kV_Lismore 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
31 | Fault | - | no | Line | 3PHG | 3 |  |  | 211640 | 800000 |  | 1 |  | 0.33 | 0.43 | 5 | -1 | 132 | no | Line fault ARM_132 - MSF_132 -- 3PHG | Armidale 132kV_Metz SF POC | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
32 | Fault | - | no | Line | 3PHG | 3 |  |  | 800000 | 245641 |  | 1 |  | 0.33 | 0.43 | 5 | -1 | 132 | no | Line fault MSF_132 - KOLK_132 -- 3PHG | Metz SF POC_Koolkhan 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
33 | Fault | - | no | Line | 3PHG | 3 |  |  | 245641 | 236942 |  | 1 |  | 0.33 | 0.43 | 5 | -1 | 132 | no | Line fault KOLK_132 - GRAF_132 -- 3PHG | Koolkhan 132kV_Graffton East 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
34 | Fault | - | no | Line | 3PHG | 3 |  |  | 236942 | 226843 |  | 1 |  | 0.33 | 0.43 | 5 | -1 | 132 | no | Line fault GRAF_132 - COFF_132 -- 3PHG | Graffton East 132kV_Coffs Harbour 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
35 | Fault | - | no | Line | 3PHG | 3 |  |  | 250401 | 273540 |  | 1 |  | 0.33 | 0.43 | 5 | -1 | 132 | no | Line fault LSM_132 - SUM_POC -- 3PHG | Lismore 132kV_SUM_POC | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
36 | Fault | - | no | Line | 3PHG | 3 |  |  | 273540 | 245641 |  | 1 |  | 0.33 | 0.43 | 5 | -1 | 132 | no | Line fault SUM_POC - KOLK_132 -- 3PHG | SUM_POC_Koolkhan 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
37 | Fault | - | no | Tx_2w | 3PHG | 3 |  |  | 250490 | 250401 |  | 1 |  | 0.33 | - | - | - | - | no | Tx_2w fault LSM_330 - LSM_132 -- 3PHG | Lismore 330kV_A_Lismore 132kV | Balanced fault – large disturbance test cases [PSS®E] | S5255_NW
38 | V_stp_profile | S52513_Network_up | no | PPC | var_change_rel | - | [12 empty] | no | Voltage setpoint change test | S52513_Network | S52513_Network | S52513_NW
39 | V_stp_profile | S52513_Network_down | no | PPC | var_change_rel | - | [12 empty] | no | Voltage setpoint change test | S52513_Network | S52513_Network | S52513_NW
40 | Tx_tap_profile |  | no | Tx_2w |  | 3 |  |  | 273541 | 273530 |  | 1 | [6 empty] | no | Voltage disturbance test | S52513_Network | S52513_Network | S52513_NW
41 | Fault | - | no | Line | 3PHG | 3 |  |  | 215290 | 288090 |  | 1 |  | 0.155 | 0.175 | 0 | 0 | 500 | no | Line fault 2BAYSWT_500A - 2WOLLAR_500A -- 3PHG | Bayswater 500kV_Wollar 500kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
42 | Fault | - | no | Line | 3PHG | 3 |  |  | 215290 | 257690 |  | 1 |  | 0.155 | 0.175 | 0 | 0 | 500 | no | Line fault 2BAYSWT_500A - 2MTPIPR_500A -- 3PHG | Bayswater 500kV_Mt Piper 500kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
43 | Fault | - | no | Line | 3PHG | 3 |  |  | 275292 | 260890 |  | 1 |  | 0.23 | 0.25 | 0 | 0 | 500 | no | Line fault 2TAMWTH_330C - 2MUSWLB_330A -- 3PHG | Tamworth 330kV_Muswellbrook 330kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
44 | Fault | - | no | Line | 3PHG | 3 |  |  | 211693 | 226893 |  | 1 |  | 0.23 | 0.25 | 0 | 0 | 330 | no | Line fault 2ARMIDL_330D - COFF_330 -- 3PHG | Armidale 330kV_Coffs Harbour 330kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
45 | Fault | - | no | Line | 3PHG | 3 |  |  | 211690 | 275290 |  | 2 |  | 0.23 | 0.24 | 0 | 0 | 330 | no | Line fault 2ARMIDL_330A - 2TAMWTH_330A -- 3PHG | Armidale 330kV_Tamworth 330kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
46 | Fault | - | no | Line | 3PHG | 3 |  |  | 275291 | 249290 |  | 1 |  | 0.23 | 0.25 | 0 | 0 | 330 | no | Line fault 2TAMWTH_330B - 2LIDDEL_330A -- 3PHG | Tamworth 330kV_Liddell 330kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
47 | Fault | - | no | Line | 3PHG | 3 |  |  | 260890 | 249290 |  | 1 |  | 0.23 | 0.25 | 0 | 0 | 330 | no | Line fault 2MUSWLB_330A - 2LIDDEL_330A -- 3PHG | Muswellbrook 330kV_Liddell 330kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
48 | Fault | - | no | Line | 3PHG | 3 |  |  | 231691 | 270390 |  | 1 |  | 0.23 | 0.25 | 0 | 0 | 330 | no | Line fault 2DUMARQ_330B - 2SAPHIR_330A -- 3PHG | Dumaresq 330kV_Sapphire WF 330kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
49 | Fault | - | no | Line | 3PHG | 3 |  |  | 270390 | 211691 |  | 1 |  | 0.23 | 0.25 | 0 | 0 | 330 | no | Line fault 2SAPHIR_330A - 2ARMIDL_330B -- 3PHG | Sapphire WF 330kV_Armidale 330kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
50 | Fault | - | no | Line | 3PHG | 3 |  |  | 231693 | 211692 |  | 1 |  | 0.23 | 0.25 | 0 | 0 | 330 | no | Line fault 2DUMARQ_330D - 2ARMIDL_330C -- 3PHG | Dumaresq 330kV_Armidale 330kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
51 | Fault | - | no | Line | 3PHG | 3 |  |  | 226893 | 250491 |  | 1 |  | 0.23 | 0.25 | 0 | 0 | 330 | no | Line fault COFF_330 - LSM_330 -- 3PHG | Coffs Harbour 330kV_Lismore 330kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
52 | Fault | - | no | Line | 3PHG | 3 |  |  | 211690 | 800002 |  | 1 |  | 0.23 | 0.25 | 0 | 0 | 330 | no | Line fault 2ARMIDL_330A - New_England_SF_POC -- 3PHG | Armidale 330kV_New England SF POC | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
53 | Fault | - | no | Line | 3PHG | 3 |  |  | 800002 | 275290 |  | 1 |  | 0.23 | 0.25 | 0 | 0 | 330 | no | Line fault New_England_SF_POC - 2TAMWTH_330A -- 3PHG | New England SF POC_Tamworth 330kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
54 | Fault | - | no | Line | 3PHG | 3 |  |  | 275240 | 261640 |  | 1 |  | 0.33 | 0.365 | 0 | 0 | 132 | no | Line fault 2TAMWTH_132A - 2NARABR_132A -- 3PHG | Tamworth 132kV_Narrabri 132kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
55 | Fault | - | no | Line | 3PHG | 3 |  |  | 209446 | 218640 |  | 1 |  | 0.33 | 0.36 | 0 | 0 | 132 | no | Line fault 2BOGABR_132G - 2BGNBRY_132A -- 3PHG | Boggabri East 132kV_Boggabri North 132kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
56 | Fault | - | no | Line | 3PHG | 3 |  |  | 218640 | 261640 |  | 1 |  | 0.33 | 0.365 | 0 | 0 | 132 | no | Line fault 2BGNBRY_132A - 2NARABR_132A -- 3PHG | Boggabri North 132kV_Narrabri 132kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
57 | Fault | - | no | Line | 3PHG | 3 |  |  | 261640 | 257240 |  | 1 |  | 0.33 | 0.365 | 0 | 0 | 132 | no | Line fault 2NARABR_132A - 2_MOREE_132A -- 3PHG | Narrabri 132kV_Moree 132kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
58 | Fault | - | no | Line | 3PHG | 3 |  |  | 257240 | 242040 |  | 1 |  | 0.33 | 0.73 | 0 | 0 | 132 | no | Line fault 2_MOREE_132A - 2INVERL_132A -- 3PHG | Moree 132kV_Inverell 132kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
59 | Fault | - | no | Line | 3PHG | 3 |  |  | 242040 | 287040 |  | 1 |  | 0.43 | 0.53 | 0 | 0 | 132 | no | Line fault 2INVERL_132A - 2WHITER_132A -- 3PHG | Inverell 132kV_White Rock 132kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
60 | Fault | - | no | Line | 3PHG | 3 |  |  | 287040 | 235640 |  | 1 |  | 0.43 | 0.53 | 0 | 0 | 132 | no | Line fault 2WHITER_132A - 2GLENIN_132A -- 3PHG | White Rock 132kV_Glen Innes 132kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
61 | Fault | - | no | Line | 3PHG | 3 |  |  | 235640 | 211640 |  | 1 |  | 0.33 | 0.73 | 0 | 0 | 132 | no | Line fault 2GLENIN_132A - ARM_132 -- 3PHG | Glen Innes 132kV_Armidale 132kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
62 | Fault | - | no | Line | 3PHG | 3 |  |  | 211640 | 242040 |  | 1 |  | 0.33 | 0.73 | 0 | 0 | 132 | no | Line fault ARM_132 - 2INVERL_132A -- 3PHG | Armidale 132kV_Inverell 132kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
63 | Fault | - | no | Line | 3PHG | 3 |  |  | 235640 | 276041 |  | 1 |  | 0.33 | 1.77 | 0 | 0 | 132 | no | Line fault 2GLENIN_132A - 2TENTFD_132B -- 3PHG | Glen Innes 132kV_Tenterfield 132kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
64 | Fault | - | no | Line | 3PHG | 3 |  |  | 275240 | 800003 |  | 1 |  | 0.33 | 0.43 | 0 | 0 | 132 | no | Line fault 2TAMWTH_132A - Tamworth_SF_POC -- 3PHG | Tamworth 132kV_Tamworth SF POC | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
65 | Fault | - | no | Line | 3PHG | 3 |  |  | 800003 | 238441 |  | 1 |  | 0.33 | 0.43 | 0 | 0 | 132 | no | Line fault Tamworth_SF_POC - 2GUNDAH_132B -- 3PHG | Tamworth SF POC_Gunnedah 132kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
66 | Fault | - | no | Line | 3PHG | 3 |  |  | 238441 | 238740 |  | 1 |  | 0.33 | 0.43 | 0 | 0 | 132 | no | Line fault 2GUNDAH_132B - 2GUN_BO_132A -- 3PHG | Gunnedah 132kV_Gunnedah East | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
67 | Fault | - | no | Line | 3PHG | 3 |  |  | 238740 | 800001 |  | 1 |  | 0.33 | 0.43 | 0 | 0 | 132 | no | Line fault 2GUN_BO_132A - Gunnedah_SF_POC -- 3PHG | Gunnedah East_Gunnedah SF POC | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
68 | Fault | - | no | Line | 3PHG | 3 |  |  | 800001 | 209446 |  | 1 |  | 0.33 | 0.43 | 0 | 0 | 132 | no | Line fault Gunnedah_SF_POC - 2BOGABR_132G -- 3PHG | Gunnedah SF POC_Boggabri East 132kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
69 | Fault | - | no | Line | 3PHG | 3 |  |  | 276041 | 294840 |  | 1 |  | 0.33 | 0.43 | 0 | 0 | 132 | no | Line fault 2TENTFD_132B - CASN_132 -- 3PHG | Tenterfield 132kV_Casino 132kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
70 | Fault | - | no | Line | 3PHG | 3 |  |  | 294840 | 250401 |  | 1 |  | 0.33 | 0.43 | 0 | 0 | 132 | no | Line fault CASN_132 - LSM_132 -- 3PHG | Casino 132kV_Lismore 132kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
71 | Fault | - | no | Line | 3PHG | 3 |  |  | 211640 | 800000 |  | 1 |  | 0.33 | 0.43 | 0 | 0 | 132 | no | Line fault ARM_132 - MSF_132 -- 3PHG | Armidale 132kV_Metz SF POC | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
72 | Fault | - | no | Line | 3PHG | 3 |  |  | 800000 | 245641 |  | 1 |  | 0.33 | 0.43 | 0 | 0 | 132 | no | Line fault MSF_132 - KOLK_132 -- 3PHG | Metz SF POC_Koolkhan 132kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
73 | Fault | - | no | Line | 3PHG | 3 |  |  | 245641 | 236942 |  | 1 |  | 0.33 | 0.43 | 0 | 0 | 132 | no | Line fault KOLK_132 - GRAF_132 -- 3PHG | Koolkhan 132kV_Graffton East 132kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
74 | Fault | - | no | Line | 3PHG | 3 |  |  | 236942 | 226843 |  | 1 |  | 0.33 | 0.43 | 0 | 0 | 132 | no | Line fault GRAF_132 - COFF_132 -- 3PHG | Graffton East 132kV_Coffs Harbour 132kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
75 | Fault | - | no | Line | 3PHG | 3 |  |  | 250401 | 273540 |  | 1 |  | 0.33 | 0.43 | 0 | 0 | 132 | no | Line fault LSM_132 - SUM_POC -- 3PHG | Lismore 132kV_SUM_POC | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
76 | Fault | - | no | Line | 3PHG | 3 |  |  | 273540 | 245641 |  | 1 |  | 0.33 | 0.43 | 0 | 0 | 132 | no | Line fault SUM_POC - KOLK_132 -- 3PHG | SUM_POC_Koolkhan 132kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
77 | Fault | - | no | Tx_2w | 3PHG | 3 |  |  | 250490 | 250401 |  | 1 |  | 0.33 | - | - | - | - | no | Tx_2w fault LSM_330 - LSM_132 -- 3PHG | Lismore 330kV_A_Lismore 132kV | Balanced fault – large disturbance test cases [PSS®E] | S52512_NW
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Consecutive cases. leave empty if it belong to / associated with previous contingency case
Note on B2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Test type must be selected from the pre-defined drop-list for studies to run.
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1. Test profile not applicable for Fault 2. Test profile is used in Vstp change test
Note on D2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Runback is defined as any dependent event(s) which is required following a particular event. When Runback is "yes", associated Case number should be empty.
Note on E2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1. Event Element depends on the Test Type: Tx_2W is only option for Tx_tap_profile 2. With Tx_3w is selected, k_bus should be provided
Note on F2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Event_Type depends on the selected Test Type 1. Options ON, OFF are only applicable for Switching studies 2. Options var_change_rel, var_change_abs are only applicable for the control
Note on N2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Distance from i_bus in pu. Default: 0.001
Note on A3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Consecutive cases. leave empty if it belong to / associated with previous contingency case
Note on J34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: LL: 101502 HL: 800000
Note on A37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kernel die HL
Note on J74: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: LL: 101502 HL: 800000
Note on A77: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kernel die HL

## PowerCapability
category
profile name | Dis-OE_35_0.9 |  | Dis-UE_35_0.9 |  | Cha-OE_35_0.9 |  | Cha-UE_35_0.9 |  | Dis-OE_35_1.0 |  | Dis-UE_35_1.0 |  | Cha-OE_35_1.0 |  | Cha-UE_35_1.0 |  | Dis-OE_35_1.1 |  | Dis-UE_35_1.1 |  | Cha-OE_35_1.1 |  | Cha-UE_35_1.1 |  | Dis-OE_40_0.9 |  | Dis-UE_40_0.9 |  | Cha-OE_40_0.9 |  | Cha-UE_40_0.9 |  | Dis-OE_40_1.0 |  | Dis-UE_40_1.0 |  | Cha-OE_40_1.0 |  | Cha-UE_40_1.0 |  | Dis-OE_40_1.1 |  | Dis-UE_40_1.1 |  | Cha-OE_40_1.1 |  | Cha-UE_40_1.1 |  | Dis-OE_50_0.9 |  | Dis-UE_50_0.9 |  | Cha-OE_50_0.9 |  | Cha-UE_50_0.9 |  | Dis-OE_50_1.0 |  | Dis-UE_50_1.0 |  | Cha-OE_50_1.0 |  | Cha-UE_50_1.0 |  | Dis-OE_50_1.1 |  | Dis-UE_50_1.1 |  | Cha-OE_50_1.1 |  | Cha-UE_50_1.1 |  | PV_OE_35_0.9 |  | PV_UE_35_0.9 |  | PV_OE_35_1.0 |  | PV_UE_35_1.0 |  | PV_OE_35_1.1 |  | PV_UE_35_1.1 |  | PV_OE_40_0.9 |  | PV_UE_40_0.9 |  | PV_OE_40_1.0 |  | PV_UE_40_1.0 |  | PV_OE_40_1.1 |  | PV_UE_40_1.1 |  | PV_OE_50_0.9 |  | PV_UE_50_0.9 |  | PV_OE_50_1.0 |  | PV_UE_50_1.0 |  | PV_OE_50_1.1 |  | PV_UE_50_1.1
PQ curve of individual INV: BESS: Including 4 quadrant operations at differnt temperature and voltage levels. At each level of active power, the avaiable apparent power is represented by percentage of the rated apparent power PV: When active power level is less than 80% of sbase, Q is limited to
scaling factor (PSCAD / PSSE)
offset (PSCAD / PSSE)
| P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr) | P (MW) | Qlim (MVAr)
point 1 | 0 | 2.268 | 0 | -2.268 | 0 | 2.268 | 0 | -2.268 | 0 | 2.52 | 0 | -2.52 | 0 | 2.52 | 0 | -2.52 | 0 | 2.52 | 0 | -2.52 | 0 | 2.52 | 0 | -2.52 | 0 | 2.268 | 0 | -2.268 | 0 | 2.268 | 0 | -2.268 | 0 | 2.52 | 0 | -2.52 | 0 | 2.52 | 0 | -2.52 | 0 | 2.52 | 0 | -2.52 | 0 | 2.52 | 0 | -2.52 | 0 | 2.268 | 0 | -2.268 | 0 | 2.268 | 0 | -2.268 | 0 | 2.52 | 0 | -2.52 | 0 | 2.52 | 0 | -2.52 | 0 | 2.52 | 0 | -2.52 | 0 | 2.52 | 0 | -2.52 | 0 | 2.52 | 0 | -2.52 | 0 | 2.52 | 0 | -2.52 | 0 | 2.52 | 0 | -2.52 | 0 | 2.52 | 0 | -2.52 | 0 | 2.52 | 0 | 2.52 | 0 | 2.52 | 0 | 2.52 | 0 | 2.52 | 0 | -2.52 | 0 | 2.52 | 0 | -2.52 | 0 | 2.52 | 0 | -2.52
point 2 | 2.268e-05 | 2.268 | 2.268e-05 | -2.268 | -2.268e-05 | 2.268 | -2.268e-05 | -2.268 | 2.52e-05 | 2.52 | 2.52e-05 | -2.52 | -2.52e-05 | 2.52 | -2.52e-05 | -2.52 | 2.52e-05 | 2.52 | 2.52e-05 | -2.52 | -2.52e-05 | 2.52 | -2.52e-05 | -2.52 | 2.268e-05 | 2.268 | 2.268e-05 | -2.268 | -2.268e-05 | 2.268 | -2.268e-05 | -2.268 | 2.52e-05 | 2.52 | 2.52e-05 | -2.52 | -2.52e-05 | 2.52 | -2.52e-05 | -2.52 | 2.52e-05 | 2.52 | 2.52e-05 | -2.52 | -2.52e-05 | 2.52 | -2.52e-05 | -2.52 | 2.268e-05 | 2.268 | 2.268e-05 | -2.268 | -2.268e-05 | 2.268 | -2.268e-05 | -2.268 | 2.52e-05 | 2.52 | 2.52e-05 | -2.52 | -2.52e-05 | 2.52 | -2.52e-05 | -2.52 | 2.52e-05 | 2.52 | 2.52e-05 | -2.52 | -2.52e-05 | 2.52 | -2.52e-05 | -2.52 | 0.042 | 2.52 | 0.042 | -2.52 | 0.042 | 2.52 | 0.042 | -2.52 | 0.042 | 2.52 | 0.042 | -2.52 | 0.042 | 2.52 | 0.042 | -2.52 | 0.042 | 2.52 | 0.042 | -2.52 | 0.042 | 2.52 | 0.042 | -2.52 | 0.042 | 2.52 | 0.042 | -2.52 | 0.042 | 2.52 | 0.042 | -2.52 | 0.042 | 2.52 | 0.042 | -2.52
. | 0.11402 | 2.268 | 0.1139 | -2.268 | -0.11394 | 2.268 | -0.11383 | -2.268 | 0.12669 | 2.52 | 0.12655 | -2.52 | -0.1266 | 2.52 | -0.12647 | -2.52 | 0.12674 | 2.52 | 0.12658 | -2.52 | -0.12673 | 2.52 | -0.12656 | -2.52 | 0.11397 | 2.268 | 0.11386 | -2.268 | -0.1139 | 2.268 | -0.11379 | -2.268 | 0.12664 | 2.52 | 0.12651 | -2.52 | -0.12655 | 2.52 | -0.12644 | -2.52 | 0.12669 | 2.52 | 0.12655 | -2.52 | -0.12668 | 2.52 | -0.12652 | -2.52 | 0.1139 | 2.268 | 0.1138 | -2.268 | -0.11383 | 2.268 | -0.11374 | -2.268 | 0.12656 | 2.52 | 0.12644 | -2.52 | -0.12648 | 2.52 | -0.12638 | -2.52 | 0.12656 | 2.52 | 0.12644 | -2.52 | -0.12648 | 2.52 | -0.12638 | -2.52 | 2.814 | 2.52 | 2.814 | -2.52 | 3.36 | 2.52 | 3.36 | -2.52 | 3.36 | 2.52 | 3.36 | -2.52 | 2.646 | 2.52 | 2.646 | -2.52 | 3.15 | 2.52 | 3.15 | -2.52 | 3.15 | 2.52 | 3.15 | -2.52 | 2.226 | 2.52 | 2.226 | -2.52 | 2.814 | 2.52 | 2.814 | -2.52 | 2.814 | 2.52 | 2.814 | -2.52
. | 0.22928 | 2.268 | 0.22878 | -2.268 | -0.22895 | 2.268 | -0.2285 | -2.268 | 0.25475 | 2.52 | 0.2542 | -2.52 | -0.25439 | 2.52 | -0.25389 | -2.52 | 0.25498 | 2.52 | 0.25433 | -2.52 | -0.25492 | 2.52 | -0.25423 | -2.52 | 0.2291 | 2.268 | 0.22864 | -2.268 | -0.22879 | 2.268 | -0.22837 | -2.268 | 0.25455 | 2.52 | 0.25404 | -2.52 | -0.25421 | 2.52 | -0.25374 | -2.52 | 0.25475 | 2.52 | 0.25418 | -2.52 | -0.25472 | 2.52 | -0.25408 | -2.52 | 0.22882 | 2.268 | 0.22839 | -2.268 | -0.22852 | 2.268 | -0.22816 | -2.268 | 0.25424 | 2.52 | 0.25377 | -2.52 | -0.25391 | 2.52 | -0.25351 | -2.52 | 0.25424 | 2.52 | 0.25377 | -2.52 | -0.25391 | 2.52 | -0.25351 | -2.52 | 2.835 | 2.5002 | 2.835 | -2.5002 | 3.381 | 2.4918 | 3.381 | -2.4918 | 3.381 | 2.4918 | 3.381 | -2.4918 | 2.667 | 2.4978 | 2.667 | -2.4978 | 3.171 | 2.52 | 3.171 | -2.52 | 3.171 | 2.52 | 3.171 | -2.52 | 2.247 | 2.52 | 2.247 | -2.52 | 2.835 | 2.5002 | 2.835 | -2.5002 | 2.835 | 2.5002 | 2.835 | -2.5002
. | 0.34944 | 2.268 | 0.3477 | -2.268 | -0.3481 | 2.268 | -0.34638 | -2.268 | 0.38827 | 2.52 | 0.38633 | -2.52 | -0.38678 | 2.52 | -0.38487 | -2.52 | 0.38914 | 2.52 | 0.38679 | -2.52 | -0.38876 | 2.52 | -0.38614 | -2.52 | 0.34877 | 2.268 | 0.34715 | -2.268 | -0.34753 | 2.268 | -0.34591 | -2.268 | 0.38753 | 2.52 | 0.38572 | -2.52 | -0.38614 | 2.52 | -0.38435 | -2.52 | 0.38831 | 2.52 | 0.38623 | -2.52 | -0.388 | 2.52 | -0.38559 | -2.52 | 0.34774 | 2.268 | 0.34626 | -2.268 | -0.34654 | 2.268 | -0.34514 | -2.268 | 0.38637 | 2.52 | 0.38473 | -2.52 | -0.38505 | 2.52 | -0.38349 | -2.52 | 0.38637 | 2.52 | 0.38473 | -2.52 | -0.38505 | 2.52 | -0.38349 | -2.52 | 2.856 | 2.4762 | 2.856 | -2.4762 | 3.402 | 2.463 | 3.402 | -2.463 | 3.402 | 2.463 | 3.402 | -2.463 | 2.688 | 2.4752 | 2.688 | -2.4752 | 3.192 | 2.52 | 3.192 | -2.52 | 3.192 | 2.52 | 3.192 | -2.52 | 2.268 | 2.52 | 2.268 | -2.52 | 2.856 | 2.4762 | 2.856 | -2.4762 | 2.856 | 2.4762 | 2.856 | -2.4762
. | 0.47328 | 2.268 | 0.46962 | -2.268 | -0.47037 | 2.268 | -0.46667 | -2.268 | 0.52587 | 2.52 | 0.5218 | -2.52 | -0.52263 | 2.52 | -0.51853 | -2.52 | 0.52775 | 2.52 | 0.52277 | -2.52 | -0.52684 | 2.52 | -0.52126 | -2.52 | 0.47187 | 2.268 | 0.46845 | -2.268 | -0.46915 | 2.268 | -0.4657 | -2.268 | 0.5243 | 2.52 | 0.5205 | -2.52 | -0.52128 | 2.52 | -0.51744 | -2.52 | 0.526 | 2.52 | 0.5216 | -2.52 | -0.52525 | 2.52 | -0.52007 | -2.52 | 0.46967 | 2.268 | 0.46657 | -2.268 | -0.46707 | 2.268 | -0.46406 | -2.268 | 0.52185 | 2.52 | 0.51841 | -2.52 | -0.51897 | 2.52 | -0.51562 | -2.52 | 0.52185 | 2.52 | 0.51841 | -2.52 | -0.51897 | 2.52 | -0.51562 | -2.52 | 2.877 | 2.4518 | 2.877 | -2.4518 | 3.423 | 2.4337 | 3.423 | -2.4337 | 3.423 | 2.4337 | 3.423 | -2.4337 | 2.709 | 2.4521 | 2.709 | -2.4521 | 3.213 | 2.5048 | 3.213 | -2.5048 | 3.213 | 2.5048 | 3.213 | -2.5048 | 2.289 | 2.5168 | 2.289 | -2.5168 | 2.877 | 2.4518 | 2.877 | -2.4518 | 2.877 | 2.4518 | 2.877 | -2.4518
. | 0.60661 | 2.268 | 0.59963 | -2.268 | -0.60034 | 2.268 | -0.59291 | -2.268 | 0.67401 | 2.52 | 0.66626 | -2.52 | -0.66704 | 2.52 | -0.65879 | -2.52 | 0.67743 | 2.52 | 0.66836 | -2.52 | -0.67521 | 2.52 | -0.66427 | -2.52 | 0.60372 | 2.268 | 0.59732 | -2.268 | -0.59798 | 2.268 | -0.59098 | -2.268 | 0.6708 | 2.52 | 0.66368 | -2.52 | -0.66442 | 2.52 | -0.65664 | -2.52 | 0.67403 | 2.52 | 0.66586 | -2.52 | -0.67206 | 2.52 | -0.66192 | -2.52 | 0.59937 | 2.268 | 0.59353 | -2.268 | -0.59378 | 2.268 | -0.58775 | -2.268 | 0.66597 | 2.52 | 0.65947 | -2.52 | -0.65975 | 2.52 | -0.65306 | -2.52 | 0.66597 | 2.52 | 0.65947 | -2.52 | -0.65975 | 2.52 | -0.65306 | -2.52 | 2.898 | 2.4269 | 2.898 | -2.4269 | 3.444 | 2.4039 | 3.444 | -2.4039 | 3.444 | 2.4039 | 3.444 | -2.4039 | 2.73 | 2.4287 | 2.73 | -2.4287 | 3.234 | 2.4776 | 3.234 | -2.4776 | 3.234 | 2.4776 | 3.234 | -2.4776 | 2.31 | 2.4975 | 2.31 | -2.4975 | 2.898 | 2.4269 | 2.898 | -2.4269 | 2.898 | 2.4269 | 2.898 | -2.4269
. | 0.74594 | 2.268 | 0.73469 | -2.268 | -0.73526 | 2.268 | -0.72297 | -2.268 | 0.82882 | 2.52 | 0.81632 | -2.52 | -0.81696 | 2.52 | -0.8033 | -2.52 | 0.83419 | 2.52 | 0.8199 | -2.52 | -0.83024 | 2.52 | -0.81235 | -2.52 | 0.74112 | 2.268 | 0.73089 | -2.268 | -0.73143 | 2.268 | -0.7198 | -2.268 | 0.82347 | 2.52 | 0.8121 | -2.52 | -0.8127 | 2.52 | -0.79978 | -2.52 | 0.82868 | 2.52 | 0.81567 | -2.52 | -0.82508 | 2.52 | -0.80851 | -2.52 | 0.73399 | 2.268 | 0.72461 | -2.268 | -0.72447 | 2.268 | -0.71451 | -2.268 | 0.81554 | 2.52 | 0.80512 | -2.52 | -0.80496 | 2.52 | -0.7939 | -2.52 | 0.81554 | 2.52 | 0.80512 | -2.52 | -0.80496 | 2.52 | -0.7939 | -2.52 | 2.919 | 2.4016 | 2.919 | -2.4016 | 3.465 | 2.3736 | 3.465 | -2.3736 | 3.465 | 2.3736 | 3.465 | -2.3736 | 2.751 | 2.4049 | 2.751 | -2.4049 | 3.255 | 2.45 | 3.255 | -2.45 | 3.255 | 2.45 | 3.255 | -2.45 | 2.331 | 2.4779 | 2.331 | -2.4779 | 2.919 | 2.4016 | 2.919 | -2.4016 | 2.919 | 2.4016 | 2.919 | -2.4016
. | 0.89892 | 2.268 | 0.88172 | -2.268 | -0.88049 | 2.268 | -0.86124 | -2.268 | 0.9988 | 2.52 | 0.97969 | -2.52 | -0.97832 | 2.52 | -0.95694 | -2.52 | 1.0063 | 2.52 | 0.98536 | -2.52 | -0.99868 | 2.52 | -0.9709 | -2.52 | 0.89174 | 2.268 | 0.87559 | -2.268 | -0.87443 | 2.268 | -0.85628 | -2.268 | 0.99082 | 2.52 | 0.97288 | -2.52 | -0.97159 | 2.52 | -0.95142 | -2.52 | 0.9979 | 2.52 | 0.97855 | -2.52 | -0.99046 | 2.52 | -0.96492 | -2.52 | 0.88034 | 2.268 | 0.86559 | -2.268 | -0.86366 | 2.268 | -0.83736 | -2.2411 | 0.97815 | 2.52 | 0.96176 | -2.52 | -0.95963 | 2.52 | -0.9304 | -2.4902 | 0.97815 | 2.52 | 0.96176 | -2.52 | -0.95963 | 2.52 | -0.9304 | -2.4902 | 2.94 | 2.3759 | 2.94 | -2.3759 | 3.486 | 2.3426 | 3.486 | -2.3426 | 3.486 | 2.3426 | 3.486 | -2.3426 | 2.772 | 2.3807 | 2.772 | -2.3807 | 3.276 | 2.4218 | 3.276 | -2.4218 | 3.276 | 2.4218 | 3.276 | -2.4218 | 2.352 | 2.458 | 2.352 | -2.458 | 2.94 | 2.3759 | 2.94 | -2.3759 | 2.94 | 2.3759 | 2.94 | -2.3759
. | 1.0601 | 2.268 | 1.0358 | -2.268 | -1.0322 | 2.268 | -1.0046 | -2.268 | 1.1779 | 2.52 | 1.1509 | -2.52 | -1.1469 | 2.52 | -1.1162 | -2.52 | 1.1878 | 2.52 | 1.1591 | -2.52 | -1.1757 | 2.52 | -1.1361 | -2.52 | 1.0501 | 2.268 | 1.0268 | -2.268 | -1.0235 | 2.268 | -0.99747 | -2.268 | 1.1668 | 2.52 | 1.1409 | -2.52 | -1.1372 | 2.52 | -1.1083 | -2.52 | 1.176 | 2.52 | 1.1491 | -2.52 | -1.1638 | 2.52 | -1.1275 | -2.52 | 1.0335 | 2.268 | 1.0123 | -2.268 | -1.0081 | 2.268 | -0.9613 | -2.2026 | 1.1484 | 2.52 | 1.1248 | -2.52 | -1.1201 | 2.52 | -1.0681 | -2.4473 | 1.1484 | 2.52 | 1.1248 | -2.52 | -1.1201 | 2.52 | -1.0681 | -2.4473 | 2.961 | 2.3497 | 2.961 | -2.3497 | 3.507 | 2.311 | 3.507 | -2.311 | 3.507 | 2.311 | 3.507 | -2.311 | 2.793 | 2.356 | 2.793 | -2.356 | 3.297 | 2.3932 | 3.297 | -2.3932 | 3.297 | 2.3932 | 3.297 | -2.3932 | 2.373 | 2.4377 | 2.373 | -2.4377 | 2.961 | 2.3497 | 2.961 | -2.3497 | 2.961 | 2.3497 | 2.961 | -2.3497
. | 1.2366 | 2.268 | 1.2055 | -2.268 | -1.196 | 2.268 | -1.1522 | -2.268 | 1.374 | 2.52 | 1.3394 | -2.52 | -1.3289 | 2.52 | -1.2802 | -2.52 | 1.3872 | 2.52 | 1.3508 | -2.52 | -1.3684 | 2.52 | -1.314 | -2.52 | 1.2227 | 2.268 | 1.193 | -2.268 | -1.1837 | 2.268 | -1.1395 | -2.2613 | 1.3585 | 2.52 | 1.3256 | -2.52 | -1.3153 | 2.52 | -1.2661 | -2.5126 | 1.371 | 2.52 | 1.3371 | -2.52 | -1.3521 | 2.52 | -1.3021 | -2.52 | 1.1998 | 2.268 | 1.172 | -2.268 | -1.1628 | 2.268 | -1.0771 | -2.1376 | 1.3331 | 2.52 | 1.3022 | -2.52 | -1.292 | 2.52 | -1.1968 | -2.3751 | 1.3331 | 2.52 | 1.3022 | -2.52 | -1.292 | 2.52 | -1.1968 | -2.3751 | 2.982 | 2.3229 | 2.982 | -2.3229 | 3.528 | 2.2789 | 3.528 | -2.2789 | 3.528 | 2.2789 | 3.528 | -2.2789 | 2.814 | 2.3309 | 2.814 | -2.3309 | 3.318 | 2.364 | 3.318 | -2.364 | 3.318 | 2.364 | 3.318 | -2.364 | 2.394 | 2.4171 | 2.394 | -2.4171 | 2.982 | 2.3229 | 2.982 | -2.3229 | 2.982 | 2.3229 | 2.982 | -2.3229
. | 1.4228 | 2.268 | 1.3841 | -2.268 | -1.3676 | 2.268 | -1.3047 | -2.2597 | 1.5809 | 2.52 | 1.5379 | -2.52 | -1.5195 | 2.52 | -1.4496 | -2.5108 | 1.5978 | 2.52 | 1.553 | -2.52 | -1.5713 | 2.52 | -1.5 | -2.52 | 1.4044 | 2.268 | 1.3677 | -2.268 | -1.3512 | 2.268 | -1.2854 | -2.2263 | 1.5605 | 2.52 | 1.5196 | -2.52 | -1.5013 | 2.52 | -1.4282 | -2.4737 | 1.5767 | 2.52 | 1.5349 | -2.52 | -1.55 | 2.52 | -1.484 | -2.52 | 1.3743 | 2.268 | 1.339 | -2.268 | -1.3239 | 2.268 | -1.192 | -2.0646 | 1.527 | 2.52 | 1.4877 | -2.52 | -1.471 | 2.52 | -1.3244 | -2.294 | 1.527 | 2.52 | 1.4877 | -2.52 | -1.471 | 2.52 | -1.3244 | -2.294 | 3.003 | 2.2957 | 3.003 | -2.2957 | 3.549 | 2.246 | 3.549 | -2.246 | 3.549 | 2.246 | 3.549 | -2.246 | 2.835 | 2.3053 | 2.835 | -2.3053 | 3.339 | 2.3342 | 3.339 | -2.3342 | 3.339 | 2.3342 | 3.339 | -2.3342 | 2.415 | 2.3961 | 2.415 | -2.3961 | 3.003 | 2.2957 | 3.003 | -2.2957 | 3.003 | 2.2957 | 3.003 | -2.2957
. | 1.4628 | 2.268 | 1.4227 | -2.268 | -1.4037 | 2.268 | -1.3341 | -2.2501 | 1.6254 | 2.52 | 1.5808 | -2.52 | -1.5596 | 2.52 | -1.4823 | -2.5001 | 1.643 | 2.52 | 1.5968 | -2.52 | -1.6141 | 2.52 | -1.54 | -2.52 | 1.4435 | 2.268 | 1.4053 | -2.268 | -1.3864 | 2.268 | -1.3117 | -2.2124 | 1.6039 | 2.52 | 1.5614 | -2.52 | -1.5405 | 2.52 | -1.4575 | -2.4582 | 1.6207 | 2.52 | 1.5775 | -2.52 | -1.5919 | 2.52 | -1.5231 | -2.52 | 1.4115 | 2.268 | 1.375 | -2.268 | -1.3535 | 2.268 | -1.2163 | -2.0515 | 1.5684 | 2.52 | 1.5278 | -2.52 | -1.5039 | 2.52 | -1.3515 | -2.2795 | 1.5684 | 2.52 | 1.5278 | -2.52 | -1.5039 | 2.52 | -1.3515 | -2.2795 | 3.024 | 2.268 | 3.024 | -2.268 | 3.57 | 2.2125 | 3.57 | -2.2125 | 3.57 | 2.2125 | 3.57 | -2.2125 | 2.856 | 2.2792 | 2.856 | -2.2792 | 3.36 | 2.3039 | 3.36 | -2.3039 | 3.36 | 2.3039 | 3.36 | -2.3039 | 2.436 | 2.3748 | 2.436 | -2.3748 | 3.024 | 2.268 | 3.024 | -2.268 | 3.024 | 2.268 | 3.024 | -2.268
point n | 1.5033 | 2.268 | 1.4618 | -2.268 | -1.4401 | 2.268 | -1.3636 | -2.2399 | 1.6703 | 2.52 | 1.6242 | -2.52 | -1.6001 | 2.52 | -1.5151 | -2.4888 | 1.6886 | 2.52 | 1.6411 | -2.52 | -1.6574 | 2.52 | -1.5803 | -2.52 | 1.4829 | 2.268 | 1.4433 | -2.268 | -1.422 | 2.268 | -1.3381 | -2.198 | 1.6477 | 2.52 | 1.6037 | -2.52 | -1.58 | 2.52 | -1.4868 | -2.4422 | 1.6653 | 2.52 | 1.6207 | -2.52 | -1.6342 | 2.52 | -1.5626 | -2.52 | 1.4492 | 2.268 | 1.4114 | -2.268 | -1.3833 | 2.268 | -1.2407 | -2.038 | 1.6102 | 2.52 | 1.5683 | -2.52 | -1.537 | 2.52 | -1.3786 | -2.2645 | 1.6102 | 2.52 | 1.5683 | -2.52 | -1.537 | 2.52 | -1.3786 | -2.2645 | 3.045 | 2.2397 | 3.045 | -2.2397 | 3.591 | 2.1782 | 3.591 | -2.1782 | 3.591 | 2.1782 | 3.591 | -2.1782 | 2.877 | 2.2527 | 2.877 | -2.2527 | 3.381 | 2.273 | 3.381 | -2.273 | 3.381 | 2.273 | 3.381 | -2.273 | 2.457 | 2.353 | 2.457 | -2.353 | 3.045 | 2.2397 | 3.045 | -2.2397 | 3.045 | 2.2397 | 3.045 | -2.2397
| 1.5442 | 2.268 | 1.5012 | -2.268 | -1.4769 | 2.268 | -1.3933 | -2.2292 | 1.7158 | 2.52 | 1.668 | -2.52 | -1.641 | 2.52 | -1.5481 | -2.4769 | 1.7348 | 2.52 | 1.6859 | -2.52 | -1.7011 | 2.52 | -1.6211 | -2.52 | 1.5228 | 2.268 | 1.4818 | -2.268 | -1.458 | 2.268 | -1.3645 | -2.1832 | 1.692 | 2.52 | 1.6464 | -2.52 | -1.62 | 2.52 | -1.5161 | -2.4258 | 1.7104 | 2.52 | 1.6643 | -2.52 | -1.677 | 2.52 | -1.6024 | -2.52 | 1.4873 | 2.268 | 1.4482 | -2.268 | -1.4132 | 2.261 | -1.2651 | -2.0242 | 1.6525 | 2.52 | 1.6091 | -2.52 | -1.5702 | 2.5123 | -1.4057 | -2.2491 | 1.6525 | 2.52 | 1.6091 | -2.52 | -1.5702 | 2.5123 | -1.4057 | -2.2491 | 3.066 | 2.2109 | 3.066 | -2.2109 | 3.612 | 2.1432 | 3.612 | -2.1432 | 3.612 | 2.1432 | 3.612 | -2.1432 | 2.898 | 2.2256 | 2.898 | -2.2256 | 3.402 | 2.2414 | 3.402 | -2.2414 | 3.402 | 2.2414 | 3.402 | -2.2414 | 2.478 | 2.3309 | 2.478 | -2.3309 | 3.066 | 2.2109 | 3.066 | -2.2109 | 3.066 | 2.2109 | 3.066 | -2.2109
| 1.5856 | 2.268 | 1.5411 | -2.268 | -1.5141 | 2.268 | -1.4231 | -2.218 | 1.7618 | 2.52 | 1.7123 | -2.52 | -1.6823 | 2.52 | -1.5812 | -2.4645 | 1.7815 | 2.52 | 1.7312 | -2.52 | -1.7453 | 2.52 | -1.6622 | -2.52 | 1.5631 | 2.268 | 1.5206 | -2.268 | -1.4942 | 2.268 | -1.391 | -2.168 | 1.7368 | 2.52 | 1.6896 | -2.52 | -1.6602 | 2.52 | -1.5455 | -2.4089 | 1.7559 | 2.52 | 1.7083 | -2.52 | -1.7201 | 2.52 | -1.6426 | -2.52 | 1.5257 | 2.268 | 1.4854 | -2.268 | -1.4432 | 2.2494 | -1.2895 | -2.0099 | 1.6953 | 2.52 | 1.6504 | -2.52 | -1.6035 | 2.4993 | -1.4328 | -2.2332 | 1.6953 | 2.52 | 1.6504 | -2.52 | -1.6035 | 2.4993 | -1.4328 | -2.2332 | 3.087 | 2.1815 | 3.087 | -2.1815 | 3.633 | 2.1074 | 3.633 | -2.1074 | 3.633 | 2.1074 | 3.633 | -2.1074 | 2.919 | 2.198 | 2.919 | -2.198 | 3.423 | 2.2092 | 3.423 | -2.2092 | 3.423 | 2.2092 | 3.423 | -2.2092 | 2.499 | 2.3084 | 2.499 | -2.3084 | 3.087 | 2.1815 | 3.087 | -2.1815 | 3.087 | 2.1815 | 3.087 | -2.1815
| 1.6274 | 2.268 | 1.5814 | -2.268 | -1.5516 | 2.268 | -1.453 | -2.2063 | 1.8082 | 2.52 | 1.7571 | -2.52 | -1.724 | 2.52 | -1.6144 | -2.4515 | 1.8287 | 2.52 | 1.777 | -2.52 | -1.7899 | 2.52 | -1.7037 | -2.52 | 1.6039 | 2.268 | 1.5599 | -2.268 | -1.5308 | 2.268 | -1.4174 | -2.1523 | 1.7821 | 2.52 | 1.7332 | -2.52 | -1.7008 | 2.52 | -1.5749 | -2.3915 | 1.802 | 2.52 | 1.7529 | -2.52 | -1.7638 | 2.52 | -1.6831 | -2.52 | 1.5646 | 2.268 | 1.5229 | -2.268 | -1.4733 | 2.2372 | -1.3139 | -1.9952 | 1.7384 | 2.52 | 1.6921 | -2.52 | -1.637 | 2.4857 | -1.4599 | -2.2169 | 1.7384 | 2.52 | 1.6921 | -2.52 | -1.637 | 2.4857 | -1.4599 | -2.2169 | 3.108 | 2.1514 | 3.108 | -2.1514 | 3.654 | 2.0708 | 3.654 | -2.0708 | 3.654 | 2.0708 | 3.654 | -2.0708 | 2.94 | 2.1698 | 2.94 | -2.1698 | 3.444 | 2.1763 | 3.444 | -2.1763 | 3.444 | 2.1763 | 3.444 | -2.1763 | 2.52 | 2.2854 | 2.52 | -2.2854 | 3.108 | 2.1514 | 3.108 | -2.1514 | 3.108 | 2.1514 | 3.108 | -2.1514
| 1.6697 | 2.268 | 1.6221 | -2.268 | -1.5894 | 2.268 | -1.483 | -2.1941 | 1.8552 | 2.52 | 1.8024 | -2.52 | -1.766 | 2.52 | -1.6478 | -2.4379 | 1.8764 | 2.52 | 1.8233 | -2.52 | -1.8349 | 2.52 | -1.7456 | -2.52 | 1.645 | 2.268 | 1.5995 | -2.268 | -1.5677 | 2.268 | -1.4439 | -2.1362 | 1.8278 | 2.52 | 1.7773 | -2.52 | -1.7418 | 2.52 | -1.6043 | -2.3736 | 1.8485 | 2.52 | 1.7979 | -2.52 | -1.8078 | 2.52 | -1.724 | -2.52 | 1.6038 | 2.268 | 1.5608 | -2.268 | -1.5035 | 2.2244 | -1.3384 | -1.9801 | 1.782 | 2.52 | 1.7342 | -2.52 | -1.6706 | 2.4716 | -1.4871 | -2.2001 | 1.782 | 2.52 | 1.7342 | -2.52 | -1.6706 | 2.4716 | -1.4871 | -2.2001 | 3.129 | 2.1208 | 3.129 | -2.1208 | 3.675 | 2.0333 | 3.675 | -2.0333 | 3.675 | 2.0333 | 3.675 | -2.0333 | 2.961 | 2.1411 | 2.961 | -2.1411 | 3.465 | 2.1427 | 3.465 | -2.1427 | 3.465 | 2.1427 | 3.465 | -2.1427 | 2.541 | 2.2621 | 2.541 | -2.2621 | 3.129 | 2.1208 | 3.129 | -2.1208 | 3.129 | 2.1208 | 3.129 | -2.1208
| 1.7124 | 2.268 | 1.6633 | -2.268 | -1.6276 | 2.268 | -1.5132 | -2.1813 | 1.9027 | 2.52 | 1.8481 | -2.52 | -1.8084 | 2.52 | -1.6813 | -2.4236 | 1.9247 | 2.52 | 1.8701 | -2.52 | -1.8805 | 2.52 | -1.7879 | -2.52 | 1.6866 | 2.268 | 1.6396 | -2.268 | -1.6049 | 2.268 | -1.4704 | -2.1196 | 1.874 | 2.52 | 1.8218 | -2.52 | -1.7832 | 2.52 | -1.6338 | -2.3551 | 1.8955 | 2.52 | 1.8434 | -2.52 | -1.8522 | 2.52 | -1.7653 | -2.52 | 1.6434 | 2.268 | 1.599 | -2.268 | -1.5339 | 2.2111 | -1.3628 | -1.9645 | 1.826 | 2.52 | 1.7767 | -2.52 | -1.7044 | 2.4568 | -1.5143 | -2.1828 | 1.826 | 2.52 | 1.7767 | -2.52 | -1.7044 | 2.4568 | -1.5143 | -2.1828 | 3.15 | 2.0895 | 3.15 | -2.0895 | 3.696 | 1.9949 | 3.696 | -1.9949 | 3.696 | 1.9949 | 3.696 | -1.9949 | 2.982 | 2.1117 | 2.982 | -2.1117 | 3.486 | 2.1084 | 3.486 | -2.1084 | 3.486 | 2.1084 | 3.486 | -2.1084 | 2.562 | 2.2382 | 2.562 | -2.2382 | 3.15 | 2.0895 | 3.15 | -2.0895 | 3.15 | 2.0895 | 3.15 | -2.0895
| 1.7556 | 2.268 | 1.7049 | -2.268 | -1.6661 | 2.268 | -1.5435 | -2.1679 | 1.9507 | 2.52 | 1.8943 | -2.52 | -1.8512 | 2.52 | -1.715 | -2.4088 | 1.9734 | 2.52 | 1.9174 | -2.52 | -1.9264 | 2.52 | -1.8306 | -2.52 | 1.7287 | 2.268 | 1.6801 | -2.268 | -1.6424 | 2.268 | -1.497 | -2.1025 | 1.9207 | 2.52 | 1.8667 | -2.52 | -1.8249 | 2.52 | -1.6633 | -2.3361 | 1.9431 | 2.52 | 1.8893 | -2.52 | -1.8971 | 2.52 | -1.807 | -2.52 | 1.6834 | 2.268 | 1.6376 | -2.268 | -1.5644 | 2.1972 | -1.3873 | -1.9485 | 1.8704 | 2.52 | 1.8196 | -2.52 | -1.7382 | 2.4414 | -1.5415 | -2.165 | 1.8704 | 2.52 | 1.8196 | -2.52 | -1.7382 | 2.4414 | -1.5415 | -2.165 | 3.171 | 2.0575 | 3.171 | -2.0575 | 3.717 | 1.9555 | 3.717 | -1.9555 | 3.717 | 1.9555 | 3.717 | -1.9555 | 3.003 | 2.0818 | 3.003 | -2.0818 | 3.507 | 2.0733 | 3.507 | -2.0733 | 3.507 | 2.0733 | 3.507 | -2.0733 | 2.583 | 2.214 | 2.583 | -2.214 | 3.171 | 2.0575 | 3.171 | -2.0575 | 3.171 | 2.0575 | 3.171 | -2.0575
| 1.7992 | 2.268 | 1.7469 | -2.268 | -1.705 | 2.268 | -1.574 | -2.1539 | 1.9992 | 2.52 | 1.941 | -2.52 | -1.8944 | 2.52 | -1.7488 | -2.3933 | 2.0227 | 2.52 | 1.9652 | -2.52 | -1.9728 | 2.52 | -1.8737 | -2.52 | 1.7711 | 2.268 | 1.7209 | -2.268 | -1.6803 | 2.268 | -1.5235 | -2.0849 | 1.9679 | 2.52 | 1.9121 | -2.52 | -1.867 | 2.52 | -1.6928 | -2.3166 | 1.9911 | 2.52 | 1.9357 | -2.52 | -1.9424 | 2.52 | -1.849 | -2.52 | 1.7237 | 2.268 | 1.6766 | -2.268 | -1.595 | 2.1828 | -1.4118 | -1.9321 | 1.9153 | 2.52 | 1.8629 | -2.52 | -1.7723 | 2.4253 | -1.5687 | -2.1467 | 1.9153 | 2.52 | 1.8629 | -2.52 | -1.7723 | 2.4253 | -1.5687 | -2.1467 | 3.192 | 2.0247 | 3.192 | -2.0247 | 3.738 | 1.915 | 3.738 | -1.915 | 3.738 | 1.915 | 3.738 | -1.915 | 3.024 | 2.0511 | 3.024 | -2.0511 | 3.528 | 2.0373 | 3.528 | -2.0373 | 3.528 | 2.0373 | 3.528 | -2.0373 | 2.604 | 2.1892 | 2.604 | -2.1892 | 3.192 | 2.0247 | 3.192 | -2.0247 | 3.192 | 2.0247 | 3.192 | -2.0247
| 1.8433 | 2.268 | 1.7894 | -2.268 | -1.7442 | 2.268 | -1.6045 | -2.1394 | 2.0482 | 2.52 | 1.9882 | -2.52 | -1.938 | 2.52 | -1.7828 | -2.3771 | 2.0725 | 2.52 | 2.0135 | -2.52 | -2.0197 | 2.52 | -1.9172 | -2.52 | 1.814 | 2.268 | 1.7622 | -2.268 | -1.7184 | 2.268 | -1.5501 | -2.0668 | 2.0156 | 2.52 | 1.958 | -2.52 | -1.9094 | 2.52 | -1.7224 | -2.2965 | 2.0396 | 2.52 | 1.9826 | -2.52 | -1.9882 | 2.52 | -1.8914 | -2.52 | 1.7645 | 2.268 | 1.7159 | -2.268 | -1.6258 | 2.1677 | -1.4364 | -1.9152 | 1.9605 | 2.52 | 1.9066 | -2.52 | -1.8064 | 2.4086 | -1.596 | -2.1279 | 1.9605 | 2.52 | 1.9066 | -2.52 | -1.8064 | 2.4086 | -1.596 | -2.1279 | 3.213 | 1.9912 | 3.213 | -1.9912 | 3.759 | 1.8735 | 3.759 | -1.8735 | 3.759 | 1.8735 | 3.759 | -1.8735 | 3.045 | 2.0198 | 3.045 | -2.0198 | 3.549 | 2.0005 | 3.549 | -2.0005 | 3.549 | 2.0005 | 3.549 | -2.0005 | 2.625 | 2.164 | 2.625 | -2.164 | 3.213 | 1.9912 | 3.213 | -1.9912 | 3.213 | 1.9912 | 3.213 | -1.9912
| 1.8894 | 2.268 | 1.8348 | -2.268 | -1.7786 | 2.268 | -1.6332 | -2.1216 | 2.0994 | 2.52 | 2.0386 | -2.52 | -1.9762 | 2.52 | -1.8147 | -2.3573 | 2.1245 | 2.52 | 2.0651 | -2.52 | -2.0682 | 2.52 | -1.9553 | -2.52 | 1.8589 | 2.268 | 1.8063 | -2.268 | -1.7487 | 2.268 | -1.5773 | -2.0489 | 2.0655 | 2.52 | 2.007 | -2.52 | -1.943 | 2.52 | -1.7525 | -2.2766 | 2.0904 | 2.52 | 2.0326 | -2.52 | -2.0353 | 2.52 | -1.9248 | -2.5003 | 1.806 | 2.268 | 1.7511 | -2.268 | -1.6514 | 2.1452 | -1.4615 | -1.8985 | 2.0067 | 2.52 | 1.9457 | -2.52 | -1.8349 | 2.3836 | -1.6239 | -2.1094 | 2.0067 | 2.52 | 1.9457 | -2.52 | -1.8349 | 2.3836 | -1.6239 | -2.1094 | 3.234 | 1.9569 | 3.234 | -1.9569 | 3.78 | 1.8307 | 3.78 | -1.8307 | 3.78 | 1.8307 | 3.78 | -1.8307 | 3.066 | 1.9878 | 3.066 | -1.9878 | 3.57 | 1.9628 | 3.57 | -1.9628 | 3.57 | 1.9628 | 3.57 | -1.9628 | 2.646 | 2.1383 | 2.646 | -2.1383 | 3.234 | 1.9569 | 3.234 | -1.9569 | 3.234 | 1.9569 | 3.234 | -1.9569
| 1.9361 | 2.268 | 1.8807 | -2.268 | -1.8132 | 2.268 | -1.662 | -2.1033 | 2.1512 | 2.52 | 2.0896 | -2.52 | -2.0146 | 2.52 | -1.8467 | -2.337 | 2.1771 | 2.52 | 2.1173 | -2.52 | -2.1172 | 2.52 | -1.9936 | -2.52 | 1.9043 | 2.268 | 1.8509 | -2.268 | -1.779 | 2.2513 | -1.6045 | -2.0304 | 2.1159 | 2.52 | 2.0565 | -2.52 | -1.9767 | 2.5015 | -1.7827 | -2.256 | 2.1418 | 2.52 | 2.0831 | -2.52 | -2.083 | 2.52 | -1.9582 | -2.478 | 1.848 | 2.268 | 1.7866 | -2.2609 | -1.677 | 2.1222 | -1.4867 | -1.8813 | 2.0533 | 2.52 | 1.9851 | -2.5121 | -1.8633 | 2.358 | -1.6518 | -2.0904 | 2.0533 | 2.52 | 1.9851 | -2.5121 | -1.8633 | 2.358 | -1.6518 | -2.0904 | 3.255 | 1.9218 | 3.255 | -1.9218 | 3.801 | 1.7867 | 3.801 | -1.7867 | 3.801 | 1.7867 | 3.801 | -1.7867 | 3.087 | 1.955 | 3.087 | -1.955 | 3.591 | 1.9241 | 3.591 | -1.9241 | 3.591 | 1.9241 | 3.591 | -1.9241 | 2.667 | 2.112 | 2.667 | -2.112 | 3.255 | 1.9218 | 3.255 | -1.9218 | 3.255 | 1.9218 | 3.255 | -1.9218
| 1.9832 | 2.268 | 1.9271 | -2.268 | -1.8479 | 2.268 | -1.6909 | -2.0843 | 2.2035 | 2.52 | 2.1412 | -2.52 | -2.0532 | 2.52 | -1.8787 | -2.3159 | 2.2303 | 2.52 | 2.1701 | -2.52 | -2.1667 | 2.52 | -2.0322 | -2.5051 | 1.9502 | 2.268 | 1.8959 | -2.268 | -1.8094 | 2.2304 | -1.6317 | -2.0114 | 2.1669 | 2.52 | 2.1066 | -2.52 | -2.0104 | 2.4782 | -1.813 | -2.2349 | 2.1937 | 2.52 | 2.1341 | -2.52 | -2.1311 | 2.52 | -1.9916 | -2.4551 | 1.8904 | 2.268 | 1.8222 | -2.2462 | -1.7025 | 2.0987 | -1.5119 | -1.8637 | 2.1004 | 2.52 | 2.0247 | -2.4958 | -1.8917 | 2.3319 | -1.6798 | -2.0707 | 2.1004 | 2.52 | 2.0247 | -2.4958 | -1.8917 | 2.3319 | -1.6798 | -2.0707 | 3.276 | 1.8858 | 3.276 | -1.8858 | 3.822 | 1.7414 | 3.822 | -1.7414 | 3.822 | 1.7414 | 3.822 | -1.7414 | 3.108 | 1.9215 | 3.108 | -1.9215 | 3.612 | 1.8844 | 3.612 | -1.8844 | 3.612 | 1.8844 | 3.612 | -1.8844 | 2.688 | 2.0852 | 2.688 | -2.0852 | 3.276 | 1.8858 | 3.276 | -1.8858 | 3.276 | 1.8858 | 3.276 | -1.8858
| 2.0308 | 2.268 | 1.974 | -2.268 | -1.8828 | 2.2605 | -1.7198 | -2.0647 | 2.2565 | 2.52 | 2.1934 | -2.52 | -2.092 | 2.5117 | -1.9108 | -2.2941 | 2.2841 | 2.52 | 2.2235 | -2.52 | -2.2168 | 2.52 | -2.071 | -2.4864 | 1.9966 | 2.268 | 1.9415 | -2.268 | -1.8398 | 2.2088 | -1.659 | -1.9917 | 2.2185 | 2.52 | 2.1572 | -2.52 | -2.0442 | 2.4543 | -1.8433 | -2.213 | 2.2462 | 2.52 | 2.1857 | -2.52 | -2.1796 | 2.52 | -2.0251 | -2.4314 | 1.9331 | 2.268 | 1.8581 | -2.2308 | -1.728 | 2.0746 | -1.5371 | -1.8454 | 2.1479 | 2.52 | 2.0645 | -2.4787 | -1.92 | 2.3051 | -1.7079 | -2.0505 | 2.1479 | 2.52 | 2.0645 | -2.4787 | -1.92 | 2.3051 | -1.7079 | -2.0505 | 3.297 | 1.8488 | 3.297 | -1.8488 | 3.843 | 1.6945 | 3.843 | -1.6945 | 3.843 | 1.6945 | 3.843 | -1.6945 | 3.129 | 1.8871 | 3.129 | -1.8871 | 3.633 | 1.8436 | 3.633 | -1.8436 | 3.633 | 1.8436 | 3.633 | -1.8436 | 2.709 | 2.0579 | 2.709 | -2.0579 | 3.297 | 1.8488 | 3.297 | -1.8488 | 3.297 | 1.8488 | 3.297 | -1.8488
| 2.079 | 2.268 | 2.0215 | -2.268 | -1.9179 | 2.2423 | -1.7487 | -2.0445 | 2.3099 | 2.52 | 2.2461 | -2.52 | -2.131 | 2.4915 | -1.943 | -2.2717 | 2.3384 | 2.52 | 2.2775 | -2.52 | -2.2672 | 2.52 | -2.1099 | -2.4668 | 2.0435 | 2.268 | 1.9875 | -2.268 | -1.8703 | 2.1866 | -1.6863 | -1.9715 | 2.2705 | 2.52 | 2.2083 | -2.52 | -2.0781 | 2.4295 | -1.8736 | -2.1905 | 2.2993 | 2.52 | 2.2379 | -2.52 | -2.2286 | 2.52 | -2.0587 | -2.4069 | 1.9763 | 2.268 | 1.8942 | -2.2145 | -1.7534 | 2.05 | -1.5624 | -1.8266 | 2.1959 | 2.52 | 2.1046 | -2.4606 | -1.9483 | 2.2778 | -1.736 | -2.0296 | 2.1959 | 2.52 | 2.1046 | -2.4606 | -1.9483 | 2.2778 | -1.736 | -2.0296 | 3.318 | 1.8109 | 3.318 | -1.8109 | 3.864 | 1.6461 | 3.864 | -1.6461 | 3.864 | 1.6461 | 3.864 | -1.6461 | 3.15 | 1.8518 | 3.15 | -1.8518 | 3.654 | 1.8016 | 3.654 | -1.8016 | 3.654 | 1.8016 | 3.654 | -1.8016 | 2.73 | 2.03 | 2.73 | -2.03 | 3.318 | 1.8109 | 3.318 | -1.8109 | 3.318 | 1.8109 | 3.318 | -1.8109
| 2.1276 | 2.268 | 2.0694 | -2.268 | -1.9532 | 2.2233 | -1.7778 | -2.0236 | 2.364 | 2.52 | 2.2994 | -2.52 | -2.1702 | 2.4703 | -1.9753 | -2.2484 | 2.3933 | 2.52 | 2.3321 | -2.52 | -2.3182 | 2.52 | -2.1491 | -2.4462 | 2.0908 | 2.268 | 2.034 | -2.268 | -1.9008 | 2.1636 | -1.7136 | -1.9506 | 2.3231 | 2.52 | 2.26 | -2.52 | -2.112 | 2.4041 | -1.904 | -2.1673 | 2.3529 | 2.52 | 2.2906 | -2.52 | -2.2781 | 2.52 | -2.0924 | -2.3817 | 2.0198 | 2.268 | 1.9305 | -2.1974 | -1.7788 | 2.0248 | -1.5877 | -1.8072 | 2.2442 | 2.52 | 2.145 | -2.4416 | -1.9765 | 2.2498 | -1.7641 | -2.0081 | 2.2442 | 2.52 | 2.145 | -2.4416 | -1.9765 | 2.2498 | -1.7641 | -2.0081 | 3.339 | 1.7719 | 3.339 | -1.7719 | 3.885 | 1.5959 | 3.885 | -1.5959 | 3.885 | 1.5959 | 3.885 | -1.5959 | 3.171 | 1.8156 | 3.171 | -1.8156 | 3.675 | 1.7584 | 3.675 | -1.7584 | 3.675 | 1.7584 | 3.675 | -1.7584 | 2.751 | 2.0014 | 2.751 | -2.0014 | 3.339 | 1.7719 | 3.339 | -1.7719 | 3.339 | 1.7719 | 3.339 | -1.7719
| 2.1767 | 2.268 | 2.1179 | -2.268 | -1.9887 | 2.2035 | -1.8069 | -2.002 | 2.4186 | 2.52 | 2.3532 | -2.52 | -2.2096 | 2.4483 | -2.0076 | -2.2245 | 2.4488 | 2.52 | 2.3872 | -2.52 | -2.3697 | 2.52 | -2.1884 | -2.4248 | 2.1386 | 2.268 | 2.081 | -2.268 | -1.9314 | 2.14 | -1.741 | -1.9291 | 2.3762 | 2.52 | 2.3122 | -2.52 | -2.146 | 2.3778 | -1.9345 | -2.1434 | 2.407 | 2.52 | 2.3438 | -2.52 | -2.3281 | 2.52 | -2.1261 | -2.3557 | 2.0638 | 2.268 | 1.967 | -2.1795 | -1.8041 | 1.999 | -1.6131 | -1.7873 | 2.2931 | 2.52 | 2.1856 | -2.4216 | -2.0046 | 2.2211 | -1.7923 | -1.9859 | 2.2931 | 2.52 | 2.1856 | -2.4216 | -2.0046 | 2.2211 | -1.7923 | -1.9859 | 3.36 | 1.7317 | 3.36 | -1.7317 | 3.906 | 1.5437 | 3.906 | -1.5437 | 3.906 | 1.5437 | 3.906 | -1.5437 | 3.192 | 1.7784 | 3.192 | -1.7784 | 3.696 | 1.7138 | 3.696 | -1.7138 | 3.696 | 1.7138 | 3.696 | -1.7138 | 2.772 | 1.9722 | 2.772 | -1.9722 | 3.36 | 1.7317 | 3.36 | -1.7317 | 3.36 | 1.7317 | 3.36 | -1.7317
| 2.2264 | 2.268 | 2.1669 | -2.268 | -2.0243 | 2.1827 | -1.836 | -1.9797 | 2.4738 | 2.52 | 2.4076 | -2.52 | -2.2492 | 2.4252 | -2.04 | -2.1997 | 2.5048 | 2.52 | 2.443 | -2.52 | -2.4217 | 2.52 | -2.228 | -2.4023 | 2.1869 | 2.268 | 2.1285 | -2.268 | -1.962 | 2.1156 | -1.7685 | -1.9069 | 2.4299 | 2.52 | 2.365 | -2.52 | -2.18 | 2.3506 | -1.965 | -2.1188 | 2.4617 | 2.52 | 2.3977 | -2.52 | -2.3784 | 2.52 | -2.1598 | -2.3289 | 2.1081 | 2.268 | 2.0038 | -2.1606 | -1.8294 | 1.9726 | -1.6385 | -1.7667 | 2.3424 | 2.52 | 2.2264 | -2.4006 | -2.0327 | 2.1918 | -1.8205 | -1.963 | 2.3424 | 2.52 | 2.2264 | -2.4006 | -2.0327 | 2.1918 | -1.8205 | -1.963 | 3.381 | 1.6903 | 3.381 | -1.6903 | 3.927 | 1.4895 | 3.927 | -1.4895 | 3.927 | 1.4895 | 3.927 | -1.4895 | 3.213 | 1.7402 | 3.213 | -1.7402 | 3.717 | 1.6677 | 3.717 | -1.6677 | 3.717 | 1.6677 | 3.717 | -1.6677 | 2.793 | 1.9424 | 2.793 | -1.9424 | 3.381 | 1.6903 | 3.381 | -1.6903 | 3.381 | 1.6903 | 3.381 | -1.6903
| 2.2765 | 2.268 | 2.2164 | -2.268 | -2.0601 | 2.161 | -1.8653 | -1.9567 | 2.5295 | 2.52 | 2.4626 | -2.52 | -2.289 | 2.4012 | -2.0725 | -2.1741 | 2.5615 | 2.52 | 2.4993 | -2.52 | -2.4741 | 2.52 | -2.2678 | -2.3789 | 2.2357 | 2.268 | 2.1764 | -2.268 | -1.9927 | 2.0903 | -1.796 | -1.884 | 2.4841 | 2.52 | 2.4182 | -2.52 | -2.2141 | 2.3226 | -1.9955 | -2.0933 | 2.5169 | 2.52 | 2.452 | -2.52 | -2.4293 | 2.52 | -2.1937 | -2.3012 | 2.1529 | 2.2584 | 2.0407 | -2.1407 | -1.8547 | 1.9455 | -1.6639 | -1.7454 | 2.3921 | 2.5093 | 2.2675 | -2.3786 | -2.0607 | 2.1617 | -1.8488 | -1.9394 | 2.3921 | 2.5093 | 2.2675 | -2.3786 | -2.0607 | 2.1617 | -1.8488 | -1.9394 | 3.402 | 1.6477 | 3.402 | -1.6477 | 3.948 | 1.4329 | 3.948 | -1.4329 | 3.948 | 1.4329 | 3.948 | -1.4329 | 3.234 | 1.7009 | 3.234 | -1.7009 | 3.738 | 1.6201 | 3.738 | -1.6201 | 3.738 | 1.6201 | 3.738 | -1.6201 | 2.814 | 1.9118 | 2.814 | -1.9118 | 3.402 | 1.6477 | 3.402 | -1.6477 | 3.402 | 1.6477 | 3.402 | -1.6477
| 2.3272 | 2.268 | 2.2664 | -2.268 | -2.0961 | 2.1384 | -1.8946 | -1.9328 | 2.5858 | 2.52 | 2.5182 | -2.52 | -2.329 | 2.376 | -2.1051 | -2.1476 | 2.6187 | 2.52 | 2.5563 | -2.52 | -2.527 | 2.52 | -2.3077 | -2.3544 | 2.285 | 2.268 | 2.2249 | -2.268 | -2.0234 | 2.0643 | -1.8235 | -1.8604 | 2.5389 | 2.52 | 2.4721 | -2.52 | -2.2483 | 2.2937 | -2.0261 | -2.0671 | 2.5727 | 2.52 | 2.507 | -2.52 | -2.4731 | 2.52 | -2.2275 | -2.2726 | 2.198 | 2.2424 | 2.0779 | -2.1199 | -1.8799 | 1.9178 | -1.6894 | -1.7235 | 2.4422 | 2.4916 | 2.3088 | -2.3554 | -2.0887 | 2.1309 | -1.8771 | -1.915 | 2.4422 | 2.4916 | 2.3088 | -2.3554 | -2.0887 | 2.1309 | -1.8771 | -1.915 | 3.423 | 1.6036 | 3.423 | -1.6036 | 3.969 | 1.3737 | 3.969 | -1.3737 | 3.969 | 1.3737 | 3.969 | -1.3737 | 3.255 | 1.6603 | 3.255 | -1.6603 | 3.759 | 1.5708 | 3.759 | -1.5708 | 3.759 | 1.5708 | 3.759 | -1.5708 | 2.835 | 1.8805 | 2.835 | -1.8805 | 3.423 | 1.6036 | 3.423 | -1.6036 | 3.423 | 1.6036 | 3.423 | -1.6036
| 2.3724 | 2.268 | 2.3092 | -2.268 | -2.1243 | 2.107 | -1.9237 | -1.908 | 2.636 | 2.52 | 2.5658 | -2.52 | -2.3604 | 2.3411 | -2.1374 | -2.12 | 2.6708 | 2.52 | 2.6089 | -2.52 | -2.5663 | 2.52 | -2.3435 | -2.3243 | 2.325 | 2.268 | 2.2623 | -2.2438 | -2.0501 | 2.0333 | -1.8516 | -1.8365 | 2.5833 | 2.52 | 2.5137 | -2.4931 | -2.2778 | 2.2592 | -2.0573 | -2.0405 | 2.6199 | 2.52 | 2.5538 | -2.52 | -2.5056 | 2.4852 | -2.2617 | -2.2433 | 2.2318 | 2.2136 | 2.1133 | -2.0961 | -1.9049 | 1.8893 | -1.7156 | -1.7016 | 2.4798 | 2.4595 | 2.3482 | -2.329 | -2.1165 | 2.0992 | -1.9062 | -1.8906 | 2.4798 | 2.4595 | 2.3482 | -2.329 | -2.1165 | 2.0992 | -1.9062 | -1.8906 | 3.444 | 1.558 | 3.444 | -1.558 | 3.99 | 1.3114 | 3.99 | -1.3114 | 3.99 | 1.3114 | 3.99 | -1.3114 | 3.276 | 1.6185 | 3.276 | -1.6185 | 3.78 | 1.5196 | 3.78 | -1.5196 | 3.78 | 1.5196 | 3.78 | -1.5196 | 2.856 | 1.8485 | 2.856 | -1.8485 | 3.444 | 1.558 | 3.444 | -1.558 | 3.444 | 1.558 | 3.444 | -1.558
| 2.4179 | 2.268 | 2.3524 | -2.2674 | -2.1525 | 2.0747 | -1.9529 | -1.8823 | 2.6866 | 2.52 | 2.6138 | -2.5193 | -2.3917 | 2.3053 | -2.1699 | -2.0915 | 2.7233 | 2.52 | 2.6619 | -2.52 | -2.6056 | 2.5114 | -2.3793 | -2.2933 | 2.3653 | 2.268 | 2.2999 | -2.2167 | -2.0766 | 2.0016 | -1.8797 | -1.8118 | 2.6281 | 2.52 | 2.5554 | -2.4631 | -2.3073 | 2.2239 | -2.0886 | -2.0131 | 2.6674 | 2.52 | 2.601 | -2.507 | -2.5381 | 2.4463 | -2.296 | -2.213 | 2.2656 | 2.1837 | 2.149 | -2.0713 | -1.9298 | 1.8601 | -1.7418 | -1.6789 | 2.5174 | 2.4264 | 2.3877 | -2.3014 | -2.1442 | 2.0667 | -1.9354 | -1.8654 | 2.5174 | 2.4264 | 2.3877 | -2.3014 | -2.1442 | 2.0667 | -1.9354 | -1.8654 | 3.465 | 1.5107 | 3.465 | -1.5107 | 4.011 | 1.2457 | 4.011 | -1.2457 | 4.011 | 1.2457 | 4.011 | -1.2457 | 3.297 | 1.5753 | 3.297 | -1.5753 | 3.801 | 1.4662 | 3.801 | -1.4662 | 3.801 | 1.4662 | 3.801 | -1.4662 | 2.877 | 1.8156 | 2.877 | -1.8156 | 3.465 | 1.5107 | 3.465 | -1.5107 | 3.465 | 1.5107 | 3.465 | -1.5107
| 2.4638 | 2.268 | 2.3959 | -2.2431 | -2.1807 | 2.0416 | -1.9822 | -1.8558 | 2.7376 | 2.52 | 2.6621 | -2.4923 | -2.423 | 2.2685 | -2.2024 | -2.062 | 2.7762 | 2.52 | 2.7154 | -2.52 | -2.645 | 2.4764 | -2.4151 | -2.2611 | 2.4057 | 2.2523 | 2.3376 | -2.1886 | -2.1031 | 1.969 | -1.9079 | -1.7863 | 2.673 | 2.5026 | 2.5974 | -2.4317 | -2.3368 | 2.1878 | -2.1199 | -1.9847 | 2.7151 | 2.52 | 2.6486 | -2.4797 | -2.5705 | 2.4065 | -2.3303 | -2.1817 | 2.2995 | 2.1529 | 2.1847 | -2.0454 | -1.9547 | 1.8301 | -1.7682 | -1.6554 | 2.555 | 2.3921 | 2.4275 | -2.2727 | -2.1719 | 2.0334 | -1.9646 | -1.8393 | 2.555 | 2.3921 | 2.4275 | -2.2727 | -2.1719 | 2.0334 | -1.9646 | -1.8393 | 3.486 | 1.4616 | 3.486 | -1.4616 | 4.032 | 1.176 | 4.032 | -1.176 | 4.032 | 1.176 | 4.032 | -1.176 | 3.318 | 1.5306 | 3.318 | -1.5306 | 3.822 | 1.4106 | 3.822 | -1.4106 | 3.822 | 1.4106 | 3.822 | -1.4106 | 2.898 | 1.7819 | 2.898 | -1.7819 | 3.486 | 1.4616 | 3.486 | -1.4616 | 3.486 | 1.4616 | 3.486 | -1.4616
| 2.51 | 2.268 | 2.4396 | -2.2174 | -2.2088 | 2.0076 | -2.0115 | -1.8283 | 2.7889 | 2.52 | 2.7107 | -2.4638 | -2.4542 | 2.2307 | -2.235 | -2.0315 | 2.8296 | 2.52 | 2.7694 | -2.5172 | -2.6845 | 2.4401 | -2.4511 | -2.2279 | 2.4464 | 2.2236 | 2.3755 | -2.1592 | -2.1295 | 1.9356 | -1.9362 | -1.7598 | 2.7182 | 2.4707 | 2.6395 | -2.3991 | -2.3661 | 2.1507 | -2.1513 | -1.9554 | 2.7632 | 2.5115 | 2.6964 | -2.4508 | -2.6028 | 2.3657 | -2.3647 | -2.1494 | 2.3335 | 2.121 | 2.2207 | -2.0184 | -1.9796 | 1.7993 | -1.7945 | -1.6311 | 2.5928 | 2.3567 | 2.4674 | -2.2427 | -2.1995 | 1.9992 | -1.9939 | -1.8123 | 2.5928 | 2.3567 | 2.4674 | -2.2427 | -2.1995 | 1.9992 | -1.9939 | -1.8123 | 3.507 | 1.4104 | 3.507 | -1.4104 | 4.053 | 1.1014 | 4.053 | -1.1014 | 4.053 | 1.1014 | 4.053 | -1.1014 | 3.339 | 1.4842 | 3.339 | -1.4842 | 3.843 | 1.3523 | 3.843 | -1.3523 | 3.843 | 1.3523 | 3.843 | -1.3523 | 2.919 | 1.7473 | 2.919 | -1.7473 | 3.507 | 1.4104 | 3.507 | -1.4104 | 3.507 | 1.4104 | 3.507 | -1.4104
| 2.5566 | 2.2547 | 2.4837 | -2.1904 | -2.2369 | 1.9727 | -2.0409 | -1.7999 | 2.8406 | 2.5052 | 2.7596 | -2.4338 | -2.4854 | 2.1919 | -2.2677 | -1.9999 | 2.8834 | 2.52 | 2.8238 | -2.4904 | -2.7241 | 2.4025 | -2.4871 | -2.1934 | 2.4873 | 2.1936 | 2.4136 | -2.1286 | -2.1559 | 1.9013 | -1.9645 | -1.7325 | 2.7636 | 2.4373 | 2.6818 | -2.3651 | -2.3954 | 2.1126 | -2.1828 | -1.925 | 2.8115 | 2.4795 | 2.7445 | -2.4204 | -2.635 | 2.3238 | -2.3992 | -2.1159 | 2.3675 | 2.088 | 2.2568 | -1.9903 | -2.0044 | 1.7677 | -1.821 | -1.6059 | 2.6306 | 2.32 | 2.5075 | -2.2114 | -2.2271 | 1.9641 | -2.0233 | -1.7844 | 2.6306 | 2.32 | 2.5075 | -2.2114 | -2.2271 | 1.9641 | -2.0233 | -1.7844 | 3.528 | 1.3571 | 3.528 | -1.3571 | 4.074 | 1.021 | 4.074 | -1.021 | 4.074 | 1.021 | 4.074 | -1.021 | 3.36 | 1.436 | 3.36 | -1.436 | 3.864 | 1.2911 | 3.864 | -1.2911 | 3.864 | 1.2911 | 3.864 | -1.2911 | 2.94 | 1.7117 | 2.94 | -1.7117 | 3.528 | 1.3571 | 3.528 | -1.3571 | 3.528 | 1.3571 | 3.528 | -1.3571
| 2.6035 | 2.2264 | 2.528 | -2.1619 | -2.2649 | 1.9368 | -2.0703 | -1.7705 | 2.8927 | 2.4737 | 2.8089 | -2.4021 | -2.5165 | 2.152 | -2.3004 | -1.9672 | 2.9375 | 2.5121 | 2.8787 | -2.4617 | -2.7638 | 2.3635 | -2.5232 | -2.1578 | 2.5284 | 2.1622 | 2.4518 | -2.0967 | -2.1822 | 1.8661 | -1.9929 | -1.7042 | 2.8093 | 2.4024 | 2.7243 | -2.3297 | -2.4246 | 2.0735 | -2.2143 | -1.8936 | 2.8601 | 2.4459 | 2.793 | -2.3885 | -2.6671 | 2.2808 | -2.4337 | -2.0812 | 2.4017 | 2.0538 | 2.293 | -1.9609 | -2.0291 | 1.7352 | -1.8475 | -1.5799 | 2.6685 | 2.282 | 2.5478 | -2.1788 | -2.2546 | 1.928 | -2.0527 | -1.7554 | 2.6685 | 2.282 | 2.5478 | -2.1788 | -2.2546 | 1.928 | -2.0527 | -1.7554 | 3.549 | 1.3012 | 3.549 | -1.3012 | 4.095 | 0.93326 | 4.095 | -0.93326 | 4.095 | 0.93326 | 4.095 | -0.93326 | 3.381 | 1.3858 | 3.381 | -1.3858 | 3.885 | 1.2265 | 3.885 | -1.2265 | 3.885 | 1.2265 | 3.885 | -1.2265 | 2.961 | 1.6751 | 2.961 | -1.6751 | 3.549 | 1.3012 | 3.549 | -1.3012 | 3.549 | 1.3012 | 3.549 | -1.3012
| 2.6507 | 2.1964 | 2.5726 | -2.1318 | -2.2928 | 1.8999 | -2.0998 | -1.74 | 2.9452 | 2.4405 | 2.8585 | -2.3686 | -2.5476 | 2.111 | -2.3332 | -1.9333 | 2.9921 | 2.4794 | 2.934 | -2.4312 | -2.8024 | 2.3221 | -2.5594 | -2.1208 | 2.5697 | 2.1293 | 2.4902 | -2.0635 | -2.2084 | 1.83 | -2.0213 | -1.6749 | 2.8552 | 2.3659 | 2.7669 | -2.2927 | -2.4538 | 2.0333 | -2.2459 | -1.861 | 2.9091 | 2.4105 | 2.8417 | -2.3548 | -2.6992 | 2.2366 | -2.4683 | -2.0453 | 2.4358 | 2.0184 | 2.3294 | -1.9302 | -2.0538 | 1.7018 | -1.874 | -1.5529 | 2.7065 | 2.2427 | 2.5883 | -2.1447 | -2.282 | 1.8909 | -2.0822 | -1.7254 | 2.7065 | 2.2427 | 2.5883 | -2.1447 | -2.282 | 1.8909 | -2.0822 | -1.7254 | 3.57 | 1.2424 | 3.57 | -1.2424 | 4.116 | 0.83579 | 4.116 | -0.83579 | 4.116 | 0.83579 | 4.116 | -0.83579 | 3.402 | 1.3335 | 3.402 | -1.3335 | 3.906 | 1.1579 | 3.906 | -1.1579 | 3.906 | 1.1579 | 3.906 | -1.1579 | 2.982 | 1.6375 | 2.982 | -1.6375 | 3.57 | 1.2424 | 3.57 | -1.2424 | 3.57 | 1.2424 | 3.57 | -1.2424
| 2.6982 | 2.1647 | 2.6176 | -2.1 | -2.3208 | 1.8619 | -2.1294 | -1.7084 | 2.998 | 2.4053 | 2.9084 | -2.3334 | -2.5786 | 2.0688 | -2.366 | -1.8982 | 3.0471 | 2.4447 | 2.9898 | -2.3986 | -2.8365 | 2.2757 | -2.5957 | -2.0825 | 2.6112 | 2.0949 | 2.5288 | -2.0288 | -2.2346 | 1.7928 | -2.0498 | -1.6445 | 2.9013 | 2.3276 | 2.8097 | -2.2542 | -2.4829 | 1.992 | -2.2775 | -1.8272 | 2.9583 | 2.3734 | 2.8908 | -2.3193 | -2.7312 | 2.1912 | -2.503 | -2.0081 | 2.4701 | 1.9817 | 2.366 | -1.8982 | -2.0785 | 1.6675 | -1.9006 | -1.5248 | 2.7445 | 2.2019 | 2.6289 | -2.1091 | -2.3094 | 1.8528 | -2.1118 | -1.6943 | 2.7445 | 2.2019 | 2.6289 | -2.1091 | -2.3094 | 1.8528 | -2.1118 | -1.6943 | 3.591 | 1.1803 | 3.591 | -1.1803 | 4.137 | 0.72473 | 4.137 | -0.72473 | 4.137 | 0.72473 | 4.137 | -0.72473 | 3.423 | 1.2786 | 3.423 | -1.2786 | 3.927 | 1.0845 | 3.927 | -1.0845 | 3.927 | 1.0845 | 3.927 | -1.0845 | 3.003 | 1.5986 | 3.003 | -1.5986 | 3.591 | 1.1803 | 3.591 | -1.1803 | 3.591 | 1.1803 | 3.591 | -1.1803
| 2.7461 | 2.1312 | 2.6628 | -2.0666 | -2.3486 | 1.8227 | -2.159 | -1.6756 | 3.0513 | 2.368 | 2.9587 | -2.2962 | -2.6096 | 2.0253 | -2.3989 | -1.8618 | 3.1026 | 2.4079 | 3.046 | -2.364 | -2.8705 | 2.2278 | -2.632 | -2.0427 | 2.6529 | 2.0588 | 2.5675 | -1.9926 | -2.2607 | 1.7545 | -2.0783 | -1.6129 | 2.9476 | 2.2876 | 2.8527 | -2.214 | -2.5119 | 1.9494 | -2.3092 | -1.7922 | 3.0078 | 2.3343 | 2.9402 | -2.2819 | -2.7631 | 2.1444 | -2.5378 | -1.9695 | 2.5044 | 1.9436 | 2.4028 | -1.8648 | -2.103 | 1.6321 | -1.9273 | -1.4957 | 2.7826 | 2.1596 | 2.6698 | -2.072 | -2.3367 | 1.8135 | -2.1414 | -1.6619 | 2.7826 | 2.1596 | 2.6698 | -2.072 | -2.3367 | 1.8135 | -2.1414 | -1.6619 | 3.612 | 1.1144 | 3.612 | -1.1144 | 4.158 | 0.59248 | 4.158 | -0.59248 | 4.158 | 0.59248 | 4.158 | -0.59248 | 3.444 | 1.2209 | 3.444 | -1.2209 | 3.948 | 1.0054 | 3.948 | -1.0054 | 3.948 | 1.0054 | 3.948 | -1.0054 | 3.024 | 1.5585 | 3.024 | -1.5585 | 3.612 | 1.1144 | 3.612 | -1.1144 | 3.612 | 1.1144 | 3.612 | -1.1144
| 2.7944 | 2.0958 | 2.7084 | -2.0313 | -2.3764 | 1.7823 | -2.1887 | -1.6415 | 3.1049 | 2.3286 | 3.0093 | -2.257 | -2.6405 | 1.9804 | -2.4319 | -1.8239 | 3.1584 | 2.3688 | 3.1027 | -2.327 | -2.9045 | 2.1784 | -2.6685 | -2.0013 | 2.6948 | 2.0211 | 2.6063 | -1.9548 | -2.2867 | 1.715 | -2.1069 | -1.5802 | 2.9942 | 2.2457 | 2.8959 | -2.1719 | -2.5408 | 1.9056 | -2.341 | -1.7558 | 3.0576 | 2.2932 | 2.9899 | -2.2424 | -2.7949 | 2.0962 | -2.5726 | -1.9294 | 2.5387 | 1.9041 | 2.4397 | -1.8298 | -2.1276 | 1.5957 | -1.954 | -1.4655 | 2.8208 | 2.1156 | 2.7108 | -2.0331 | -2.364 | 1.773 | -2.1711 | -1.6284 | 2.8208 | 2.1156 | 2.7108 | -2.0331 | -2.364 | 1.773 | -2.1711 | -1.6284 | 3.633 | 1.0439 | 3.633 | -1.0439 | 4.179 | 0.41947 | 4.179 | -0.41947 | 4.179 | 0.41947 | 4.179 | -0.41947 | 3.465 | 1.16 | 3.465 | -1.16 | 3.969 | 0.91897 | 3.969 | -0.91897 | 3.969 | 0.91897 | 3.969 | -0.91897 | 3.045 | 1.5171 | 3.045 | -1.5171 | 3.633 | 1.0439 | 3.633 | -1.0439 | 3.633 | 1.0439 | 3.633 | -1.0439
| 2.8322 | 2.0505 | 2.7494 | -1.9905 | -2.4038 | 1.7403 | -2.2199 | -1.6072 | 3.1469 | 2.2783 | 3.0549 | -2.2117 | -2.6709 | 1.9337 | -2.4665 | -1.7857 | 3.1979 | 2.3152 | 3.1471 | -2.2785 | -2.938 | 2.1271 | -2.7064 | -1.9594 | 2.7324 | 1.9782 | 2.6472 | -1.9165 | -2.3131 | 1.6746 | -2.1368 | -1.547 | 3.036 | 2.198 | 2.9413 | -2.1295 | -2.5701 | 1.8607 | -2.3743 | -1.7189 | 3.0958 | 2.2413 | 3.0341 | -2.1967 | -2.8271 | 2.0468 | -2.6094 | -1.8892 | 2.5737 | 1.8633 | 2.4781 | -1.7941 | -2.1522 | 1.5582 | -1.9821 | -1.435 | 2.8596 | 2.0703 | 2.7534 | -1.9935 | -2.3913 | 1.7313 | -2.2023 | -1.5945 | 2.8596 | 2.0703 | 2.7534 | -1.9935 | -2.3913 | 1.7313 | -2.2023 | -1.5945 | 3.654 | 0.96782 | 3.654 | -0.96782 | 4.2 | 0 | 4.2 | 0 | 4.2 | 0 | 4.2 | 0 | 3.486 | 1.0952 | 3.486 | -1.0952 | 3.99 | 0.82303 | 3.99 | -0.82303 | 3.99 | 0.82303 | 3.99 | -0.82303 | 3.066 | 1.4742 | 3.066 | -1.4742 | 3.654 | 0.96782 | 3.654 | -0.96782 | 3.654 | 0.96782 | 3.654 | -0.96782
| 2.87 | 2.0033 | 2.7907 | -1.9479 | -2.4311 | 1.6969 | -2.2511 | -1.5713 | 3.1889 | 2.2259 | 3.1007 | -2.1643 | -2.7012 | 1.8855 | -2.5012 | -1.7459 | 3.2374 | 2.2597 | 3.1917 | -2.2278 | -2.9713 | 2.074 | -2.7444 | -1.9156 | 2.7701 | 1.9335 | 2.6883 | -1.8764 | -2.3394 | 1.6329 | -2.1669 | -1.5125 | 3.0779 | 2.1484 | 2.987 | -2.0849 | -2.5993 | 1.8143 | -2.4076 | -1.6805 | 3.134 | 2.1876 | 3.0785 | -2.1488 | -2.8593 | 1.9958 | -2.6464 | -1.8472 | 2.6087 | 1.8209 | 2.5167 | -1.7567 | -2.1768 | 1.5194 | -2.0103 | -1.4032 | 2.8986 | 2.0232 | 2.7963 | -1.9519 | -2.4186 | 1.6882 | -2.2337 | -1.5591 | 2.8986 | 2.0232 | 2.7963 | -1.9519 | -2.4186 | 1.6882 | -2.2337 | -1.5591 | 3.675 | 0.88475 | 3.675 | -0.88475 | [8 empty] | 3.507 | 1.026 | 3.507 | -1.026 | 4.011 | 0.71369 | 4.011 | -0.71369 | 4.011 | 0.71369 | 4.011 | -0.71369 | 3.087 | 1.4297 | 3.087 | -1.4297 | 3.675 | 0.88475 | 3.675 | -0.88475 | 3.675 | 0.88475 | 3.675 | -0.88475
| 2.908 | 1.9542 | 2.8321 | -1.9032 | -2.4583 | 1.652 | -2.2825 | -1.5338 | 3.2311 | 2.1713 | 3.1468 | -2.1146 | -2.7315 | 1.8356 | -2.5361 | -1.7043 | 3.2768 | 2.202 | 3.2364 | -2.1749 | -3.0046 | 2.0191 | -2.7826 | -1.8699 | 2.8079 | 1.8869 | 2.7295 | -1.8343 | -2.3657 | 1.5897 | -2.197 | -1.4764 | 3.1199 | 2.0966 | 3.0328 | -2.0381 | -2.6285 | 1.7664 | -2.4411 | -1.6404 | 3.1723 | 2.1318 | 3.1231 | -2.0987 | -2.8914 | 1.943 | -2.6834 | -1.8033 | 2.6438 | 1.7766 | 2.5555 | -1.7173 | -2.2013 | 1.4793 | -2.0386 | -1.3699 | 2.9376 | 1.974 | 2.8395 | -1.9081 | -2.4459 | 1.6436 | -2.2651 | -1.5221 | 2.9376 | 1.974 | 2.8395 | -1.9081 | -2.4459 | 1.6436 | -2.2651 | -1.5221 | 3.696 | 0.79245 | 3.696 | -0.79245 | [8 empty] | 3.528 | 0.95128 | 3.528 | -0.95128 | 4.032 | 0.58348 | 4.032 | -0.58348 | 4.032 | 0.58348 | 4.032 | -0.58348 | 3.108 | 1.3835 | 3.108 | -1.3835 | 3.696 | 0.79245 | 3.696 | -0.79245 | 3.696 | 0.79245 | 3.696 | -0.79245
| 2.946 | 1.9029 | 2.8737 | -1.8562 | -2.4855 | 1.6055 | -2.3139 | -1.4946 | 3.2733 | 2.1143 | 3.193 | -2.0625 | -2.7617 | 1.7839 | -2.571 | -1.6607 | 3.3163 | 2.1421 | 3.2812 | -2.1195 | -3.0378 | 1.9622 | -2.8209 | -1.8221 | 2.8458 | 1.8382 | 2.771 | -1.7899 | -2.3919 | 1.545 | -2.2272 | -1.4386 | 3.162 | 2.0424 | 3.0789 | -1.9888 | -2.6576 | 1.7167 | -2.4747 | -1.5985 | 3.2105 | 2.0738 | 3.1678 | -2.0462 | -2.9234 | 1.8883 | -2.7206 | -1.7574 | 2.679 | 1.7304 | 2.5945 | -1.6759 | -2.2257 | 1.4377 | -2.0669 | -1.3351 | 2.9766 | 1.9227 | 2.8828 | -1.8621 | -2.473 | 1.5974 | -2.2966 | -1.4834 | 2.9766 | 1.9227 | 2.8828 | -1.8621 | -2.473 | 1.5974 | -2.2966 | -1.4834 | 3.717 | 0.68725 | 3.717 | -0.68725 | [8 empty] | 3.549 | 0.86966 | 3.549 | -0.86966 | 4.053 | 0.41312 | 4.053 | -0.41312 | 4.053 | 0.41312 | 4.053 | -0.41312 | 3.129 | 1.3353 | 3.129 | -1.3353 | 3.717 | 0.68725 | 3.717 | -0.68725 | 3.717 | 0.68725 | 3.717 | -0.68725
| 2.984 | 1.8493 | 2.9155 | -1.8069 | -2.5126 | 1.5572 | -2.3454 | -1.4536 | 3.3156 | 2.0548 | 3.2394 | -2.0076 | -2.7918 | 1.7302 | -2.606 | -1.6151 | 3.3558 | 2.0797 | 3.3262 | -2.0614 | -3.071 | 1.9032 | -2.8592 | -1.772 | 2.8838 | 1.7872 | 2.8127 | -1.7432 | -2.418 | 1.4986 | -2.2575 | -1.3991 | 3.2042 | 1.9858 | 3.1252 | -1.9368 | -2.6867 | 1.6651 | -2.5083 | -1.5545 | 3.2487 | 2.0134 | 3.2127 | -1.9911 | -2.9554 | 1.8316 | -2.7579 | -1.7092 | 2.7142 | 1.6821 | 2.6337 | -1.6322 | -2.2502 | 1.3945 | -2.0954 | -1.2986 | 3.0158 | 1.869 | 2.9263 | -1.8136 | -2.5002 | 1.5495 | -2.3282 | -1.4429 | 3.0158 | 1.869 | 2.9263 | -1.8136 | -2.5002 | 1.5495 | -2.3282 | -1.4429 | 3.738 | 0.56192 | 3.738 | -0.56192 | [8 empty] | 3.57 | 0.77898 | 3.57 | -0.77898 | 4.074 | 0 | 4.074 | 0 | 4.074 | 0 | 4.074 | 0 | 3.15 | 1.285 | 3.15 | -1.285 | 3.738 | 0.56192 | 3.738 | -0.56192 | 3.738 | 0.56192 | 3.738 | -0.56192
| 3.0222 | 1.7933 | 2.9574 | -1.7548 | -2.5397 | 1.507 | -2.3771 | -1.4105 | 3.358 | 1.9925 | 3.286 | -1.9498 | -2.8219 | 1.6744 | -2.6412 | -1.5672 | 3.3953 | 2.0146 | 3.3713 | -2.0004 | -3.104 | 1.8418 | -2.8977 | -1.7194 | 2.9218 | 1.7337 | 2.8546 | -1.6938 | -2.4441 | 1.4502 | -2.2879 | -1.3575 | 3.2465 | 1.9264 | 3.1718 | -1.882 | -2.7157 | 1.6114 | -2.5421 | -1.5084 | 3.2869 | 1.9503 | 3.2578 | -1.9331 | -2.9872 | 1.7725 | -2.7954 | -1.6587 | 2.7496 | 1.6315 | 2.6731 | -1.5861 | -2.2745 | 1.3496 | -2.1239 | -1.2603 | 3.0551 | 1.8128 | 2.9701 | -1.7624 | -2.5272 | 1.4996 | -2.3599 | -1.4003 | 3.0551 | 1.8128 | 2.9701 | -1.7624 | -2.5272 | 1.4996 | -2.3599 | -1.4003 | 3.759 | 0.39789 | 3.759 | -0.39789 | [8 empty] | 3.591 | 0.6756 | 3.591 | -0.6756 | [8 empty] | 3.171 | 1.2322 | 3.171 | -1.2322 | 3.759 | 0.39789 | 3.759 | -0.39789 | 3.759 | 0.39789 | 3.759 | -0.39789
| 3.0604 | 1.7344 | 2.9996 | -1.6999 | -2.5667 | 1.4546 | -2.4088 | -1.3651 | 3.4005 | 1.9271 | 3.3329 | -1.8888 | -2.8519 | 1.6162 | -2.6764 | -1.5168 | 3.4348 | 1.9466 | 3.4166 | -1.9363 | -3.1371 | 1.7778 | -2.9364 | -1.6641 | 2.96 | 1.6775 | 2.8967 | -1.6416 | -2.4701 | 1.3999 | -2.3184 | -1.3139 | 3.2889 | 1.8639 | 3.2185 | -1.824 | -2.7446 | 1.5554 | -2.576 | -1.4599 | 3.3251 | 1.8844 | 3.3031 | -1.8719 | -3.0191 | 1.711 | -2.8329 | -1.6055 | 2.785 | 1.5783 | 2.7127 | -1.5373 | -2.2988 | 1.3028 | -2.1525 | -1.2199 | 3.0944 | 1.7537 | 3.0141 | -1.7082 | -2.5543 | 1.4476 | -2.3917 | -1.3554 | 3.0944 | 1.7537 | 3.0141 | -1.7082 | -2.5543 | 1.4476 | -2.3917 | -1.3554 | 3.78 | 0 | 3.78 | 0 | [8 empty] | 3.612 | 0.55242 | 3.612 | -0.55242 | [8 empty] | 3.192 | 1.1767 | 3.192 | -1.1767 | 3.78 | 0 | 3.78 | 0 | 3.78 | 0 | 3.78 | 0
| 3.0987 | 1.6725 | 3.0419 | -1.6418 | -2.5936 | 1.3999 | -2.4406 | -1.3173 | 3.443 | 1.8583 | 3.3799 | -1.8243 | -2.8818 | 1.5554 | -2.7118 | -1.4637 | 3.4742 | 1.8752 | 3.462 | -1.8686 | -3.17 | 1.711 | -2.9751 | -1.6058 | 2.9983 | 1.6183 | 2.939 | -1.5863 | -2.4961 | 1.3473 | -2.3489 | -1.2678 | 3.3314 | 1.7981 | 3.2655 | -1.7625 | -2.7735 | 1.497 | -2.6099 | -1.4087 | 3.3634 | 1.8153 | 3.3485 | -1.8073 | -3.0508 | 1.6467 | -2.8706 | -1.5494 | 2.8205 | 1.5223 | 2.7525 | -1.4856 | -2.3231 | 1.2539 | -2.1813 | -1.1773 | 3.1339 | 1.6915 | 3.0583 | -1.6507 | -2.5812 | 1.3932 | -2.4236 | -1.3081 | 3.1339 | 1.6915 | 3.0583 | -1.6507 | -2.5812 | 1.3932 | -2.4236 | -1.3081 | [12 empty] | 3.633 | 0.39119 | 3.633 | -0.39119 | [8 empty] | 3.213 | 1.1181 | 3.213 | -1.1181
| 3.1371 | 1.6072 | 3.0844 | -1.5802 | -2.6205 | 1.3425 | -2.4725 | -1.2667 | 3.4856 | 1.7857 | 3.4271 | -1.7558 | -2.9117 | 1.4917 | -2.7472 | -1.4074 | 3.5137 | 1.8001 | 3.5075 | -1.797 | -3.2028 | 1.6409 | -3.0139 | -1.5441 | 3.0367 | 1.5557 | 2.9815 | -1.5275 | -2.5221 | 1.2921 | -2.3796 | -1.2191 | 3.3741 | 1.7286 | 3.3127 | -1.6972 | -2.8023 | 1.4357 | -2.644 | -1.3545 | 3.4016 | 1.7427 | 3.394 | -1.7388 | -3.0825 | 1.5792 | -2.9083 | -1.49 | 2.856 | 1.4632 | 2.7924 | -1.4306 | -2.3473 | 1.2026 | -2.2101 | -1.1323 | 3.1734 | 1.6258 | 3.1027 | -1.5896 | -2.6082 | 1.3362 | -2.4556 | -1.2581 | 3.1734 | 1.6258 | 3.1027 | -1.5896 | -2.6082 | 1.3362 | -2.4556 | -1.2581 | [12 empty] | 3.654 | 0 | 3.654 | 0 | [8 empty] | 3.234 | 1.0559 | 3.234 | -1.0559
| 3.1755 | 1.538 | 3.1271 | -1.5145 | -2.6473 | 1.2822 | -2.5045 | -1.213 | 3.5283 | 1.7088 | 3.4745 | -1.6828 | -2.9415 | 1.4246 | -2.7828 | -1.3478 | 3.5532 | 1.7209 | 3.5532 | -1.7209 | -3.2356 | 1.5671 | -3.0529 | -1.4786 | 3.0751 | 1.4894 | 3.0242 | -1.4647 | -2.5479 | 1.234 | -2.4103 | -1.1674 | 3.4168 | 1.6548 | 3.3602 | -1.6274 | -2.831 | 1.3711 | -2.6781 | -1.2971 | 3.4398 | 1.666 | 3.4398 | -1.666 | -3.1142 | 1.5083 | -2.9459 | -1.4268 | 2.8917 | 1.4005 | 2.8326 | -1.3719 | -2.3715 | 1.1486 | -2.239 | -1.0844 | 3.213 | 1.5561 | 3.1473 | -1.5243 | -2.635 | 1.2762 | -2.4878 | -1.2049 | 3.213 | 1.5561 | 3.1473 | -1.5243 | -2.635 | 1.2762 | -2.4878 | -1.2049 | [24 empty] | 3.255 | 0.98923 | 3.255 | -0.98923
| 3.2138 | 1.4642 | 3.1704 | -1.4445 | -2.6711 | 1.217 | -2.5381 | -1.1564 | 3.5709 | 1.6269 | 3.5227 | -1.605 | -2.9679 | 1.3522 | -2.8201 | -1.2849 | 3.5927 | 1.6369 | 3.5927 | -1.6369 | -3.2647 | 1.4875 | -3.0953 | -1.4103 | 3.1135 | 1.4185 | 3.066 | -1.3969 | -2.5709 | 1.1713 | -2.4429 | -1.113 | 3.4594 | 1.5762 | 3.4066 | -1.5521 | -2.8566 | 1.3015 | -2.7143 | -1.2367 | 3.478 | 1.5846 | 3.478 | -1.5846 | -3.1422 | 1.4316 | -2.9857 | -1.3603 | 2.9238 | 1.3321 | 2.8733 | -1.3091 | -2.3925 | 1.09 | -2.2693 | -1.0339 | 3.2487 | 1.4802 | 3.1925 | -1.4546 | -2.6583 | 1.2112 | -2.5215 | -1.1488 | 3.2487 | 1.4802 | 3.1925 | -1.4546 | -2.6583 | 1.2112 | -2.5215 | -1.1488 | [24 empty] | 3.276 | 0.91729 | 3.276 | -0.91729
| 3.2522 | 1.3854 | 3.214 | -1.3692 | -2.6948 | 1.148 | -2.5719 | -1.0956 | 3.6135 | 1.5394 | 3.5711 | -1.5213 | -2.9943 | 1.2755 | -2.8576 | -1.2173 | 3.6322 | 1.5473 | 3.6322 | -1.5473 | -3.2937 | 1.4031 | -3.1379 | -1.3368 | 3.1519 | 1.3427 | 3.1079 | -1.324 | -2.5938 | 1.105 | -2.4756 | -1.0546 | 3.5021 | 1.4919 | 3.4533 | -1.4711 | -2.882 | 1.2277 | -2.7506 | -1.1718 | 3.5162 | 1.4979 | 3.5162 | -1.4979 | -3.1702 | 1.3505 | -3.0257 | -1.2889 | 2.956 | 1.2592 | 2.9142 | -1.2414 | -2.4133 | 1.0281 | -2.2998 | -0.97971 | 3.2844 | 1.3991 | 3.238 | -1.3794 | -2.6814 | 1.1423 | -2.5553 | -1.0886 | 3.2844 | 1.3991 | 3.238 | -1.3794 | -2.6814 | 1.1423 | -2.5553 | -1.0886 | [24 empty] | 3.297 | 0.83869 | 3.297 | -0.83869
| 3.2906 | 1.3005 | 3.2577 | -1.2875 | -2.7184 | 1.0744 | -2.6057 | -1.0298 | 3.6563 | 1.445 | 3.6197 | -1.4306 | -3.0204 | 1.1938 | -2.8952 | -1.1443 | 3.6716 | 1.4511 | 3.6716 | -1.4511 | -3.3225 | 1.3131 | -3.1807 | -1.2571 | 3.1905 | 1.261 | 3.1501 | -1.245 | -2.6165 | 1.0341 | -2.5084 | -0.99137 | 3.545 | 1.4011 | 3.5001 | -1.3833 | -2.9073 | 1.149 | -2.7871 | -1.1015 | 3.5545 | 1.4048 | 3.5545 | -1.4048 | -3.198 | 1.2639 | -3.0658 | -1.2117 | 2.9881 | 1.181 | 2.9553 | -1.168 | -2.434 | 0.96199 | -2.3304 | -0.92103 | 3.3201 | 1.3122 | 3.2836 | -1.2978 | -2.7045 | 1.0689 | -2.5893 | -1.0234 | 3.3201 | 1.3122 | 3.2836 | -1.2978 | -2.7045 | 1.0689 | -2.5893 | -1.0234 | [24 empty] | 3.318 | 0.75132 | 3.318 | -0.75132
| 3.3291 | 1.2083 | 3.3017 | -1.1984 | -2.7418 | 0.99515 | -2.6397 | -0.95809 | 3.699 | 1.3426 | 3.6685 | -1.3315 | -3.0465 | 1.1057 | -2.933 | -1.0645 | 3.7111 | 1.347 | 3.7111 | -1.347 | -3.3511 | 1.2163 | -3.2237 | -1.1701 | 3.2291 | 1.172 | 3.1924 | -1.1587 | -2.6392 | 0.95789 | -2.5413 | -0.92238 | 3.5879 | 1.3022 | 3.5471 | -1.2874 | -2.9324 | 1.0643 | -2.8237 | -1.0249 | 3.5927 | 1.304 | 3.5927 | -1.304 | -3.2257 | 1.1708 | -3.1061 | -1.1273 | 3.0202 | 1.0962 | 2.9966 | -1.0876 | -2.4546 | 0.89091 | -2.3611 | -0.85697 | 3.3558 | 1.218 | 3.3295 | -1.2085 | -2.7274 | 0.9899 | -2.6234 | -0.95218 | 3.3558 | 1.218 | 3.3295 | -1.2085 | -2.7274 | 0.9899 | -2.6234 | -0.95218 | [24 empty] | 3.339 | 0.65168 | 3.339 | -0.65168
| 3.3677 | 1.1069 | 3.3458 | -1.0997 | -2.7652 | 0.90886 | -2.6738 | -0.87885 | 3.7419 | 1.2299 | 3.7176 | -1.2219 | -3.0724 | 1.0098 | -2.9709 | -0.9765 | 3.7506 | 1.2328 | 3.7506 | -1.2328 | -3.3796 | 1.1108 | -3.2669 | -1.0738 | 3.2678 | 1.0741 | 3.2349 | -1.0633 | -2.6617 | 0.87486 | -2.5744 | -0.84616 | 3.6309 | 1.1934 | 3.5944 | -1.1814 | -2.9574 | 0.97206 | -2.8604 | -0.94018 | 3.6309 | 1.1934 | 3.6309 | -1.1934 | -3.2532 | 1.0693 | -3.1465 | -1.0342 | 3.0524 | 1.0033 | 3.0381 | -0.99856 | -2.4751 | 0.81353 | -2.3919 | -0.78619 | 3.3915 | 1.1147 | 3.3756 | -1.1095 | -2.7501 | 0.90392 | -2.6577 | -0.87354 | 3.3915 | 1.1147 | 3.3756 | -1.1095 | -2.7501 | 0.90392 | -2.6577 | -0.87354 | [24 empty] | 3.36 | 0.53292 | 3.36 | -0.53292
| 3.4048 | 0.99305 | 3.387 | -0.98789 | -2.7865 | 0.81273 | -2.7127 | -0.7912 | 3.7831 | 1.1034 | 3.7634 | -1.0977 | -3.0961 | 0.90303 | -3.0141 | -0.87911 | 3.7901 | 1.1054 | 3.7901 | -1.1054 | -3.4057 | 0.99334 | -3.3155 | -0.96702 | 3.3022 | 0.96314 | 3.2756 | -0.95539 | -2.6823 | 0.78234 | -2.6117 | -0.76175 | 3.6691 | 1.0702 | 3.6396 | -1.0615 | -2.9803 | 0.86926 | -2.9019 | -0.84639 | 3.6691 | 1.0702 | 3.6691 | -1.0702 | -3.2784 | 0.95619 | -3.1921 | -0.93103 | 3.0845 | 0.89964 | 3.0729 | -0.89627 | -2.4944 | 0.72754 | -2.4272 | -0.70793 | 3.4272 | 0.9996 | 3.4144 | -0.99585 | -2.7716 | 0.80838 | -2.6969 | -0.78659 | 3.4272 | 0.9996 | 3.4144 | -0.99585 | -2.7716 | 0.80838 | -2.6969 | -0.78659 | [24 empty] | 3.381 | 0.37742 | 3.381 | -0.37742
| 3.4418 | 0.8626 | 3.4284 | -0.85924 | -2.8077 | 0.70367 | -2.7517 | -0.68965 | 3.8242 | 0.95844 | 3.8093 | -0.95471 | -3.1196 | 0.78186 | -3.0575 | -0.76628 | 3.8296 | 0.95978 | 3.8296 | -0.95978 | -3.4316 | 0.86004 | -3.3632 | -0.84291 | 3.3366 | 0.83623 | 3.3165 | -0.83118 | -2.7027 | 0.67737 | -2.6492 | -0.66396 | 3.7073 | 0.92915 | 3.685 | -0.92354 | -3.003 | 0.75263 | -2.9436 | -0.73774 | 3.7073 | 0.92915 | 3.7073 | -0.92915 | -3.3033 | 0.8279 | -3.238 | -0.81151 | 3.1166 | 0.7811 | 3.1079 | -0.7789 | -2.5136 | 0.62997 | -2.4627 | -0.6172 | 3.4629 | 0.86788 | 3.4532 | -0.86545 | -2.7929 | 0.69997 | -2.7363 | -0.68578 | 3.4629 | 0.86788 | 3.4532 | -0.86545 | -2.7929 | 0.69997 | -2.7363 | -0.68578 | [24 empty] | 3.402 | 0 | 3.402 | 0
| 3.4789 | 0.70642 | 3.4699 | -0.70459 | -2.8287 | 0.57439 | -2.791 | -0.56674 | 3.8655 | 0.78491 | 3.8554 | -0.78287 | -3.143 | 0.63821 | -3.1011 | -0.62971 | 3.869 | 0.78564 | 3.869 | -0.78564 | -3.4573 | 0.70204 | -3.4112 | -0.69268 | 3.371 | 0.68451 | 3.3574 | -0.68176 | -2.723 | 0.55293 | -2.687 | -0.54562 | 3.7456 | 0.76057 | 3.7305 | -0.75751 | -3.0256 | 0.61437 | -2.9856 | -0.60624 | 3.7456 | 0.76057 | 3.7456 | -0.76057 | -3.3281 | 0.67581 | -3.2841 | -0.66687 | 3.1487 | 0.63938 | 3.1428 | -0.63818 | -2.5327 | 0.51428 | -2.4983 | -0.50731 | 3.4986 | 0.71042 | 3.492 | -0.70909 | -2.8141 | 0.57142 | -2.7759 | -0.56367 | 3.4986 | 0.71042 | 3.492 | -0.70909 | -2.8141 | 0.57142 | -2.7759 | -0.56367
| 3.516 | 0.50101 | 3.5115 | -0.50036 | -2.8496 | 0.40604 | -2.8305 | -0.40333 | 3.9067 | 0.55668 | 3.9016 | -0.55595 | -3.1662 | 0.45116 | -3.145 | -0.44814 | 3.9085 | 0.55693 | 3.9085 | -0.55693 | -3.4828 | 0.49627 | -3.4595 | -0.49296 | 3.4054 | 0.48524 | 3.3985 | -0.48427 | -2.7432 | 0.39088 | -2.725 | -0.38829 | 3.7838 | 0.53916 | 3.7762 | -0.53807 | -3.048 | 0.43431 | -3.0277 | -0.43143 | 3.7838 | 0.53916 | 3.7838 | -0.53916 | -3.3527 | 0.47774 | -3.3305 | -0.47457 | 3.1809 | 0.45325 | 3.1779 | -0.45282 | -2.5515 | 0.36358 | -2.5342 | -0.36111 | 3.5343 | 0.50361 | 3.531 | -0.50314 | -2.8351 | 0.40397 | -2.8158 | -0.40123 | 3.5343 | 0.50361 | 3.531 | -0.50314 | -2.8351 | 0.40397 | -2.8158 | -0.40123
| 3.5532 | 0 | 3.5532 | 0 | -2.8703 | 0 | -2.8703 | 0 | 3.948 | 0 | 3.948 | 0 | -3.1892 | 0 | -3.1892 | 0 | 3.948 | 0 | 3.948 | 0 | -3.5081 | 0 | -3.5081 | 0 | 3.4398 | 0 | 3.4398 | 0 | -2.7631 | 0 | -2.7631 | 0 | 3.822 | 0 | 3.822 | 0 | -3.0702 | 0 | -3.0702 | 0 | 3.822 | 0 | 3.822 | 0 | -3.3772 | 0 | -3.3772 | 0 | 3.213 | 0 | 3.213 | 0 | -2.5703 | 0 | -2.5703 | 0 | 3.57 | 0 | 3.57 | 0 | -2.8559 | 0 | -2.8559 | 0 | 3.57 | 0 | 3.57 | 0 | -2.8559 | 0 | -2.8559 | 0
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Category always has to be defined in the first column belonging to a new category. Every profile defined in this sheet must have a corresponging category assigned. This is used for the labelling of the output data generated by the test script.
Note on BW4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Base kVA
Note on CI7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Derating 0.87=0.9-(0.9-0.81)/(50-35)*(40-35)
Note on CK7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Derating 0.87=0.9-(0.9-0.81)/(50-35)*(40-35)
Note on CM7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Derating 0.97==1-(1-0.9)/(50-35)*(40-35)
Note on CO7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Derating 0.97==1-(1-0.9)/(50-35)*(40-35)
Note on CQ7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Derating 0.97==1-(1-0.9)/(50-35)*(40-35)
Note on CS7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Derating 0.97==1-(1-0.9)/(50-35)*(40-35)

## TestTypes
layers (optional) | Layer 1 | Layer 2
Test Type
Steady_State | 0 | 1
F_profile | 0 | 1
ANG_profile | 0 | 1
V_profile | 0 | 1
V_stp_profile | 0 | 1
Q_stp_profile | 0 | 1
PF_stp_profile | 0 | 1
P_stp_profile | 0 | 0
ORT | 0 | 0
Fault | 4 | 0
Fault_TOV | 0 | 0
Multifault_random | 0 | 1
Multifault | 0 | 1
P_prim_lim_profile | 0 | 0
Auxiliary_profile | 0 | 0
Note on A5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Angle change profile is defined as a step profile and not as a linear interpolated profile. The reason is that the profile cannot be programmes into a test source but rather needs to be written vie the PSS/E API. A step profile limits the number or changes that need to be made during runtime.
Note on A11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Oscillatory rejection test
Note on A12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: inductive or ohmic fault, different types. to be specified by residual voltage at POC+X/R or resistance+reactcance or Impedance+X/R ratio.
Note on A13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: capacitive fault to increase voltage

## Bus Lib
Num | Bus_num_PSSE | Bus_name_PSSE | Bus_name_full |  | Bus_name_PSSE | Bus_name_full
1 | 0 | N/A | N/A |  | 2LSMORE_330A | Lismore 330kV_A
1 | 250490 | LSM_330 | Lismore 330kV_A |  | 2LISMOR_132A | Lismore 132kV_2
2 | 250040 | LSM_132_B | Lismore 132kV_2 |  | 2_COFFS_132D | Coffs Harbour 132kV
3 | 226843 | COFF_132 | Coffs Harbour 132kV |  | 2GRAFTN_132C | Graffton East 132kV
4 | 236942 | GRAF_132 | Graffton East 132kV |  | 2KOLKHN_132B | Koolkhan 132kV
5 | 245641 | KOLK_132 | Koolkhan 132kV |  | 2KOLKHN__66B | Koolkhan 66kV
6 | 245631 | 2KOLKHN__66B | Koolkhan 66kV |  | 2MULUMB__DC2 | 2MULUMB__DC2
7 | 258402 | 2MULUMB__DC2 | 2MULUMB__DC2 |  | 2MULUMB__DC3 | 2MULUMB__DC3
8 | 258403 | 2MULUMB__DC3 | 2MULUMB__DC3 |  | 2DUNOON_132A | 2DUNOON_132A
9 | 232040 | 2DUNOON_132A | 2DUNOON_132A |  | 2CASN_T_132A | Casino 132kV
10 | 294840 | CASN_132 | Casino 132kV |  | 2BAYSWT_500A | Bayswater 500kV
11 | 215290 | 2BAYSWT_500A | Bayswater 500kV |  | 2WOLLAR_500A | Wollar 500kV
12 | 288090 | 2WOLLAR_500A | Wollar 500kV |  | 2MTPIPR_500A | Mt Piper 500kV
13 | 257690 | 2MTPIPR_500A | Mt Piper 500kV |  | 2TAMWTH_330A | Tamworth 330kV
14 | 275290 | 2TAMWTH_330A | Tamworth 330kV |  | 2TAMWTH_330B | Tamworth 330kV
15 | 275291 | 2TAMWTH_330B | Tamworth 330kV |  | 2TAMWTH_330C | Tamworth 330kV
16 | 275292 | 2TAMWTH_330C | Tamworth 330kV |  | 2ARMIDL_330A | Armidale 330kV
17 | 211690 | 2ARMIDL_330A | Armidale 330kV |  | 2ARMIDL_330B | Armidale 330kV
18 | 211691 | 2ARMIDL_330B | Armidale 330kV |  | 2ARMIDL_330C | Armidale 330kV
19 | 211692 | 2ARMIDL_330C | Armidale 330kV |  | 2ARMIDL_330D | Armidale 330kV
20 | 211693 | 2ARMIDL_330D | Armidale 330kV |  | 2ARMIDL_330E | Armidale 330kV
21 | 211694 | 2ARMIDL_330E | Armidale 330kV |  | 2DUMARQ_330A | Dumaresq 330kV
22 | 231690 | 2DUMARQ_330A | Dumaresq 330kV |  | 2DUMARQ_330B | Dumaresq 330kV
23 | 231691 | 2DUMARQ_330B | Dumaresq 330kV |  | 2DUMARQ_330C | Dumaresq 330kV
24 | 231692 | 2DUMARQ_330C | Dumaresq 330kV |  | 2DUMARQ_330D | Dumaresq 330kV
25 | 231693 | 2DUMARQ_330D | Dumaresq 330kV |  | 2DUMARQ_330E | Dumaresq 330kV
26 | 231694 | 2DUMARQ_330E | Dumaresq 330kV |  | 2MUSWLB_330A | Muswellbrook 330kV
27 | 260890 | 2MUSWLB_330A | Muswellbrook 330kV |  | 2_COFFS_330D | Coffs Harbour 330kV
28 | 226893 | COFF_330 | Coffs Harbour 330kV |  | 2LIDDEL_330A | Liddell 330kV
29 | 249290 | 2LIDDEL_330A | Liddell 330kV |  | 2SAPHIR_330A | Sapphire WF 330kV
30 | 270390 | 2SAPHIR_330A | Sapphire WF 330kV |  | 2LSMORE_330B | Lismore 330kV
31 | 250491 | LSM_330 | Lismore 330kV |  | 2TAMWTH_132A | Tamworth 132kV
32 | 275240 | 2TAMWTH_132A | Tamworth 132kV |  | 2GUNDAH_132B | Gunnedah 132kV
33 | 238441 | 2GUNDAH_132B | Gunnedah 132kV |  | 2NARABR_132A | Narrabri 132kV
34 | 261640 | 2NARABR_132A | Narrabri 132kV |  | 2BOGABR_132G | Boggabri East 132kV
35 | 209446 | 2BOGABR_132G | Boggabri East 132kV |  | 2BGNBRY_132A | Boggabri North 132kV
36 | 218640 | 2BGNBRY_132A | Boggabri North 132kV |  | 2NARABR_132A | Narrabri 132kV
37 | 261640 | 2NARABR_132A | Narrabri 132kV |  | 2_MOREE_132A | Moree 132kV
38 | 257240 | 2_MOREE_132A | Moree 132kV |  | 2INVERL_132A | Inverell 132kV
39 | 242040 | 2INVERL_132A | Inverell 132kV |  | 2WHITER_132A | White Rock 132kV
40 | 287040 | 2WHITER_132A | White Rock 132kV |  | 2GLENIN_132A | Glen Innes 132kV
41 | 235640 | 2GLENIN_132A | Glen Innes 132kV |  | 2ARMIDL_132A | Armidale 132kV
42 | 211640 | ARM_132 | Armidale 132kV |  | 2TENTFD_132B | Tenterfield 132kV
43 | 276041 | 2TENTFD_132B | Tenterfield 132kV |  | 2LSMORE___S1 | Lismore 132kV
44 | 250401 | LSM_132 | Lismore 132kV |  | Metz_SF_POC | Metz SF POC
45 | 800000 | MSF_132 | Metz SF POC |  | Gunnedah_SF_POC | Gunnedah SF POC
46 | 800001 | Gunnedah_SF_POC | Gunnedah SF POC |  | New_England_SF_POC | New England SF POC
47 | 800002 | New_England_SF_POC | New England SF POC |  | Tamworth_SF_POC | Tamworth SF POC
48 | 800003 | Tamworth_SF_POC | Tamworth SF POC |  | 2GUN_BO_132A | Gunnedah East
49 | 238740 | 2GUN_BO_132A | Gunnedah East |  | 2CASN_T_132A | Casino 132kV
50 | 294840 | 2CASN_T_132A | Casino 132kV |  | Summerville_SF_132kV | Summerville SF 132kV
51 | 273540 | SUM_POC | SUM_POC |  | SUM_POC_to | SUM_POC_to
52 | 273541 | SUM_HV | SUM_HV |  | SUM_POC_from | SUM_POC_from
53 | 273530 | SUM_MV | SUM_MV |  | SUM_HV | SUM_HV
54 | 273531 | SUM_MV_PV | SUM_MV_PV |  | SUM_MV | SUM_MV
55 | 273501 | SUM_LV_PV | SUM_LV_PV |  | SUM_MV_PV | SUM_MV_PV
56 | 273532 | SUM_MV_BESS | SUM_MV_BESS |  | SUM_LV_PV | SUM_LV_PV
57 | 273502 | SUM_LV_BESS | SUM_LV_BESS |  | SUM_MV_BESS | SUM_MV_BESS
58 | 2200 | GUNSF_POC | GUNSF_POC |  | SUM_LV_BESS | SUM_LV_BESS
59 | 2300 | GUNSF_MV2 | GUNSF_MV2
60 | 2400 | GUNSF_MV1 | GUNSF_MV1
61 | 2500 | GUNSF_GEN | GUNSF_GEN
62 | 106 | TAMSF_POC | TAMSF_POC
63 | 105 | TAMSF_BUS1 | TAMSF_BUS1
64 | 103 | TAMSF_BUS2 | TAMSF_BUS2
65 | 1031 | TAMSF_BUS3 | TAMSF_BUS3
66 | 1032 | TAMSF_BUS4 | TAMSF_BUS4
67 | 102 | TAMSF_BUS5 | TAMSF_BUS5
68 | 101 | TAMSF_BUS6 | TAMSF_BUS6
69 | 100 | TAMSF_GEN | TAMSF_GEN
70 | 249201 | LID_GEN1 | LID_GEN1
71 | 101502 | MSF_132 | Metz SF POC
72 | 460391 | 4BULICR_330B | Bulli Creek | QLD
73 | 460392 | 4BULICR_330C | Bulli Creek | QLD
74 | 231694 | 2DUMARQ_330E | Dumaresq | NSW
75 | 231692 | 2DUMARQ_330C | Dumaresq | NSW
76 | 585582 | 5SOUTEA_275C | SouthEast in SA | SA
77 | 333081 | 3HEYWOD_275B | Heywood | VIC
| 277690 | 2TOMAGO_330A | Tomago | Load to shed
Note on B73: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Only for LL

## MonitorBuses
bus_number | bus_name | bus_code
250490 | LSM_330 | Lismore 330kV_A | LSM_330 = 250490 # Lismore 330kV_A | LSM_330 = 250490 # Lismore 330kV_A
226893 | COFF_330 | Coffs Harbour 330kV | COFF_330 = 226893 # Coffs Harbour 330kV | COFF_330 = 226893 # Coffs Harbour 330kV
250401 | LSM_132 | Lismore 132kV | LSM_132 = 250401 # Lismore 132kV | LSM_132 = 250401 # Lismore 132kV
245641 | KOLK_132 | Koolkhan 132kV | KOLK_132 = 245641 # Koolkhan 132kV | KOLK_132 = 245641 # Koolkhan 132kV
226843 | COFF_132 | Coffs Harbour 132kV | COFF_132 = 226843 # Coffs Harbour 132kV | COFF_132 = 226843 # Coffs Harbour 132kV
250040 | LSM_132_B | Lismore 132kV_2 | LSM_132_B = 250040 # Lismore 132kV_2 | LSM_132_B = 250040 # Lismore 132kV_2
294840 | CASN_132 | Casino 132kV | CASN_132 = 294840 # Casino 132kV | CASN_132 = 294840 # Casino 132kV
211640 | ARM_132 | Armidale 132kV | ARM_132 = 211640 # Armidale 132kV | ARM_132 = 211640 # Armidale 132kV
273540 | SUM_POC | SUM_POC | SUM_POC = 273540 # SUM_POC | SUM_POC = 9910 # SUM_POC 132kV

## MonitorBranches
brch_from | brch_to | brch_id | brch_name | brch_code | brch_name | brch_code | brch_name
250491 | 226893 | 1 | LSM_330 - COFF_330 | LSM_330 - COFF_330 | LSM_330 - COFF_330 | Lismore 330kV - Coffs Harbour 330kV | 89-0
250490 | 250401 | 1 | LSM_330 - LSM_132 | LSM_330 - LSM_132 | LSM_330 - LSM_132 | Lismore 330kV_A - Lismore 132kV | LISMORE_1H
250490 | 250401 | 2 | LSM_330 - LSM_132 | LSM_330 - LSM_132 | LSM_330 - LSM_132 | Lismore 330kV_A - Lismore 132kV | LISMORE_2H
250401 | 250040 | 1 | LSM_132 - LSM_132_B | LSM_132 - LSM_132_B | LSM_132 - LSM_132_B | Lismore 132kV - Lismore 132kV_2 | 9U8-0
250401 | 250040 | 2 | LSM_132 - LSM_132_B | LSM_132 - LSM_132_B | LSM_132 - LSM_132_B | Lismore 132kV - Lismore 132kV_2 | 9U9-0
250401 | 250040 | 3 | LSM_132 - LSM_132_B | LSM_132 - LSM_132_B | LSM_132 - LSM_132_B | Lismore 132kV - Lismore 132kV_2 | 9W1-0
250401 | 294840 | 1 | LSM_132 - CASN_132 | LSM_132 - CASN_132 | LSM_132 - CASN_132 | Lismore 132kV - Casino 132kV | 96L/2-0
800000 | 245641 | 1 | MSF_132 - KOLK_132 | MSF_132 - KOLK_132 | MSF_132 - KOLK_132 | Metz SF POC - Koolkhan 132kV | 966-0
245641 | 236942 | 1 | KOLK_132 - GRAF_132 | KOLK_132 - GRAF_132 | KOLK_132 - GRAF_132 | Koolkhan 132kV - Graffton East 132kV | 9W0-0
273540 | 250401 | 1 | SUM_POC - LSM_132 | SUM_POC - LSM_132 | SUM_POC - LSM_132 | SUM_POC - Lismore 132kV | 967-1
273540 | 245641 | 1 | SUM_POC - KOLK_132 | SUM_POC - KOLK_132 | SUM_POC - KOLK_132 | SUM_POC - Koolkhan 132kV | 967-0
275291 | 249290 | 1 | 2TAMWTH_330B - 2LIDDEL_330A | 2TAMWTH_330B - 2LIDDEL_330A | 2TAMWTH_330B - 2LIDDEL_330A | Tamworth 330kV - Liddell 330kV
275292 | 260890 | 1 | 2TAMWTH_330B - 2LIDDEL_330A | 2TAMWTH_330C - 2MUSWLB_330A | 2TAMWTH_330C - 2MUSWLB_330A | Tamworth 330kV - Muswellbrook 330kV