## CATL_25C_0.9pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 25 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1490 |  | VDC
Nom. Battery Voltage** |  |  |  | 1291.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1159 |  | VDC |  | Please select:
AC Voltage |  |  |  | 0.9 |  | pu |  | Project plant specific |  |  | VArRtg: | 2172 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP @25°C, 1159Vdc min. battery voltage and 0.9pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 1954.8027 | 1954.8027 | 1954.8027 | 1954.8023 | 0 | 0 | 0 | 0 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8023
0.01 | 1954.8027 | 1954.8027 | 1954.8027 | 1954.8023 | 0.019548 | 0.019548 | -0.019548 | -0.019548 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8023
0.05 | 1968.282 | 1968.282 | 1968.282 | 1966.1729 | 98.4141 | 98.4141 | -98.4141 | -98.3086 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.1 | 1981.764 | 1981.764 | 1981.764 | 1977.5458 | 198.1764 | 198.1764 | -198.1764 | -197.7546 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.15 | 2021.1521 | 2021.1521 | 2021.1521 | 2009.4577 | 303.1728 | 303.1728 | -303.1728 | -301.4186 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.2 | 2060.5401 | 2060.5401 | 2060.5401 | 2041.3695 | 412.108 | 412.108 | -412.108 | -408.2739 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.25 | 2123.0365 | 2123.0365 | 2123.0365 | 2091.4544 | 530.7591 | 530.7591 | -530.7591 | -522.8636 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.3 | 2185.5328 | 2185.5328 | 2185.5328 | 2141.5392 | 655.6599 | 655.6599 | -655.6599 | -642.4618 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.35 | 2267.455 | 2267.455 | 2267.455 | 2206.9114 | 793.6093 | 793.6093 | -793.6093 | -772.419 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.4 | 2349.3772 | 2349.3772 | 2349.3772 | 2272.2836 | 939.7509 | 939.7509 | -939.7509 | -908.9134 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.45 | 2446.9783 | 2446.9783 | 2446.9783 | 2349.8213 | 1101.1402 | 1101.1402 | -1101.1402 | -1057.4196 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.5 | 2544.5793 | 2544.5793 | 2544.5793 | 2427.359 | 1272.2897 | 1272.2897 | -1272.2897 | -1213.6795 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.51 | 2566.5719 | 2566.5719 | 2566.5719 | 2445.9191 | 1308.9517 | 1308.9517 | -1308.9517 | -1247.4188 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.52 | 2588.5644 | 2588.5644 | 2588.5644 | 2464.4793 | 1346.0535 | 1346.0535 | -1346.0535 | -1281.5292 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.53 | 2610.5569 | 2610.5569 | 2610.5569 | 2483.0395 | 1383.5952 | 1383.5952 | -1383.5952 | -1316.0109 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.54 | 2632.5495 | 2632.5495 | 2632.5495 | 2501.5997 | 1421.5767 | 1421.5767 | -1421.5767 | -1350.8638 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.55 | 2654.542 | 2654.542 | 2654.542 | 2520.1599 | 1459.9981 | 1459.9981 | -1459.9981 | -1386.0879 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.56 | 2676.5345 | 2676.5345 | 2676.5345 | 2538.7201 | 1498.8593 | 1498.8593 | -1498.8593 | -1421.6832 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.57 | 2698.5271 | 2698.5271 | 2698.5271 | 2557.2802 | 1538.1604 | 1538.1604 | -1538.1604 | -1457.6497 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.58 | 2720.5196 | 2720.5196 | 2720.5196 | 2575.8404 | 1577.9014 | 1577.9014 | -1577.9014 | -1493.9874 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.59 | 2742.5121 | 2742.5121 | 2742.5121 | 2594.4006 | 1618.0822 | 1618.0822 | -1618.0822 | -1530.6964 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.6 | 2764.5047 | 2764.5047 | 2764.5047 | 2612.9608 | 1658.7028 | 1658.7028 | -1658.7028 | -1567.7765 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.61 | 2788.427 | 2788.427 | 2788.427 | 2633.8622 | 1700.9404 | 1700.9404 | -1700.9404 | -1606.656 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.62 | 2812.3493 | 2812.3493 | 2812.3493 | 2654.7637 | 1743.6565 | 1743.6565 | -1743.6565 | -1645.9535 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.63 | 2836.2715 | 2836.2715 | 2836.2715 | 2675.6651 | 1786.8511 | 1786.8511 | -1786.8511 | -1685.669 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.64 | 2860.1938 | 2860.1938 | 2860.1938 | 2696.5666 | 1830.5241 | 1830.5241 | -1830.5241 | -1725.8026 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.65 | 2884.1161 | 2884.1161 | 2884.1161 | 2717.468 | 1874.6755 | 1874.6755 | -1874.6755 | -1766.3542 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.66 | 2908.0384 | 2908.0384 | 2908.0384 | 2738.3695 | 1919.3054 | 1919.3054 | -1919.3054 | -1807.3239 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.67 | 2931.9607 | 2931.9607 | 2931.9607 | 2759.2709 | 1964.4137 | 1964.4137 | -1964.4137 | -1848.7115 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.68 | 2955.883 | 2955.883 | 2955.883 | 2780.1724 | 2010.0004 | 2010.0004 | -2010.0004 | -1890.5172 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.69 | 2979.8053 | 2979.8053 | 2979.8053 | 2801.0738 | 2056.0657 | 2056.0657 | -2056.0657 | -1932.7409 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.7 | 3003.7276 | 3003.7276 | 3003.7276 | 2821.9753 | 2102.6093 | 2102.6093 | -2102.6093 | -1975.3827 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.71 | 3029.1548 | 3029.1548 | 3025.2029 | 2833.6166 | 2150.6999 | 2150.6999 | -2147.8941 | -2011.8678 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.72 | 3054.5821 | 3054.5821 | 3046.6783 | 2845.2579 | 2199.2991 | 2199.2991 | -2193.6084 | -2048.5857 | 1954.8027 | -1954.8027 | 1954.8027 | -1954.8027
0.73 | 3080.0093 | 3080.0093 | 3068.1536 | 2856.8992 | 2248.4068 | 2248.4068 | -2239.7521 | -2085.5364 | 1954.8027 | -1954.8027 | 1954.8027 | -1952.5396
0.74 | 3105.4366 | 3105.4366 | 3089.6289 | 2868.5405 | 2298.023 | 2298.023 | -2286.3254 | -2122.7199 | 1954.8027 | -1954.8027 | 1954.8027 | -1929.4
0.75 | 3130.8638 | 3130.8638 | 3111.1043 | 2880.1818 | 2348.1478 | 2348.1478 | -2333.3282 | -2160.1363 | 1954.8027 | -1954.8027 | 1954.8027 | -1905.0612
0.76 | 3156.291 | 3156.291 | 3132.5796 | 2891.8231 | 2398.7812 | 2398.7812 | -2380.7605 | -2197.7855 | 1954.8027 | -1954.8027 | 1954.8027 | -1879.4625
0.77 | 3181.7183 | 3181.7183 | 3154.055 | 2903.4644 | 2449.9231 | 2449.9231 | -2428.6223 | -2235.6676 | 1954.8027 | -1954.8027 | 1954.8027 | -1852.5377
0.78 | 3207.1455 | 3207.1455 | 3175.5303 | 2915.1057 | 2501.5735 | 2501.5735 | -2476.9136 | -2273.7824 | 1954.8027 | -1954.8027 | 1954.8027 | -1824.2134
0.79 | 3232.5728 | 3232.5728 | 3197.0056 | 2926.747 | 2553.7325 | 2553.7325 | -2525.6345 | -2312.1301 | 1954.8027 | -1954.8027 | 1954.8027 | -1794.4086
0.8 | 3258 | 3258 | 3218.481 | 2938.3883 | 2606.4 | 2606.4 | -2574.7848 | -2350.7106 | 1954.8 | -1954.8 | 1931.0886 | -1763.033
0.81 | 3258 | 3258 | 3214.1282 | 2943.5507 | 2638.98 | 2638.98 | -2603.4438 | -2384.2761 | 1910.5885 | -1910.5885 | 1884.8608 | -1726.1861
0.82 | 3258 | 3258 | 3209.7754 | 2948.7132 | 2671.56 | 2671.56 | -2632.0158 | -2417.9448 | 1864.7604 | -1864.7604 | 1837.1583 | -1687.7359
0.83 | 3258 | 3258 | 3205.4226 | 2953.8757 | 2704.14 | 2704.14 | -2660.5007 | -2451.7168 | 1817.1931 | -1817.1931 | 1787.8674 | -1647.5637
0.84 | 3258 | 3258 | 3201.0698 | 2959.0382 | 2736.72 | 2736.72 | -2688.8986 | -2485.5921 | 1767.7465 | -1767.7465 | 1736.8569 | -1605.5339
0.85 | 3258 | 3258 | 3196.717 | 2964.2007 | 2769.3 | 2769.3 | -2717.2094 | -2519.5706 | 1716.258 | -1716.258 | 1683.9752 | -1561.4896
0.86 | 3258 | 3258 | 3192.3642 | 2969.3631 | 2801.88 | 2801.88 | -2745.4332 | -2553.6523 | 1662.538 | -1662.538 | 1629.0444 | -1515.2483
0.87 | 3258 | 3258 | 3188.0114 | 2974.5256 | 2834.46 | 2834.46 | -2773.5699 | -2587.8373 | 1606.3625 | -1606.3625 | 1571.8545 | -1466.595
0.88 | 3258 | 3258 | 3183.6586 | 2979.6881 | 2867.04 | 2867.04 | -2801.6195 | -2622.1255 | 1547.4643 | -1547.4643 | 1512.154 | -1415.2734
0.89 | 3258 | 3258 | 3179.3058 | 2984.8506 | 2899.62 | 2899.62 | -2829.5821 | -2656.517 | 1485.5194 | -1485.5194 | 1449.6379 | -1360.974
0.9 | 3258 | 3258 | 3174.953 | 2990.0131 | 2932.2 | 2932.2 | -2857.4577 | -2691.0118 | 1420.1293 | -1420.1293 | 1383.9299 | -1303.3165
0.91 | 3258 | 3258 | 3168.8697 | 2996.3762 | 2964.78 | 2964.78 | -2883.6714 | -2726.7023 | 1350.7937 | -1350.7937 | 1313.8395 | -1242.3223
0.92 | 3258 | 3258 | 3162.7864 | 3002.7393 | 2997.36 | 2997.36 | -2909.7635 | -2762.5202 | 1276.87 | -1276.87 | 1239.5541 | -1176.8287
0.93 | 3258 | 3258 | 3156.7032 | 3009.1024 | 3029.94 | 3029.94 | -2935.7339 | -2798.4653 | 1197.5089 | -1197.5089 | 1160.2763 | -1106.0242
0.94 | 3258 | 3258 | 3150.6199 | 3015.4655 | 3062.52 | 3062.52 | -2961.5827 | -2834.5376 | 1111.5463 | -1111.5463 | 1074.911 | -1028.7998
0.95 | 3258 | 3258 | 3144.5366 | 3021.8287 | 3095.1 | 3095.1 | -2987.3098 | -2870.7372 | 1017.3102 | -1017.3102 | 981.8812 | -943.5657
0.96 | 3258 | 3258 | 3132.4254 | 3034.259 | 3127.68 | 3127.68 | -3007.1284 | -2912.8887 | 912.24 | -912.24 | 877.0791 | -849.5925
0.97 | 3258 | 3258 | 3120.3142 | 3046.6894 | 3160.26 | 3160.26 | -3026.7048 | -2955.2887 | 792.0358 | -792.0358 | 758.5637 | -740.6652
0.98 | 3258 | 3258 | 3108.203 | 3059.1198 | 3192.84 | 3192.84 | -3046.0389 | -2997.9374 | 648.3338 | -648.3338 | 618.5246 | -608.7572
0.99 | 3258 | 3258 | 3096.0918 | 3071.5502 | 3225.42 | 3225.42 | -3065.1308 | -3040.8347 | 459.5975 | -459.5975 | 436.7575 | -433.2955
1 | 3258 | 3258 | 3083.9806 | 3083.9806 | 3258 | 3258 | -3083.9806 | -3083.9806 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_25C_1.0pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 25 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1490 |  | VDC
Nom. Battery Voltage** |  |  |  | 1291.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1159 |  | VDC |  | Please select:
AC Voltage |  |  |  | 1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2172 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP @25°C, 1159Vdc min. battery voltage and 1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2172.003 | 2172.003 | 2172.003 | 2172.0025 | 0 | 0 | 0 | 0 | 2172.003 | -2172.003 | 2172.003 | -2172.0025
0.01 | 2172.003 | 2172.003 | 2172.003 | 2172.0025 | 0.02172 | 0.02172 | -0.02172 | -0.02172 | 2172.003 | -2172.003 | 2172.003 | -2172.0025
0.05 | 2186.98 | 2186.98 | 2186.98 | 2184.6366 | 109.349 | 109.349 | -109.349 | -109.2318 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.1 | 2201.96 | 2201.96 | 2201.96 | 2197.2732 | 220.196 | 220.196 | -220.196 | -219.7273 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.15 | 2245.7245 | 2245.7245 | 2245.7245 | 2232.7307 | 336.8587 | 336.8587 | -336.8587 | -334.9096 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.2 | 2289.489 | 2289.489 | 2289.489 | 2268.1883 | 457.8978 | 457.8978 | -457.8978 | -453.6377 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.25 | 2358.9294 | 2358.9294 | 2358.9294 | 2323.8382 | 589.7324 | 589.7324 | -589.7324 | -580.9595 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.3 | 2428.3698 | 2428.3698 | 2428.3698 | 2379.488 | 728.5109 | 728.5109 | -728.5109 | -713.8464 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.35 | 2519.3945 | 2519.3945 | 2519.3945 | 2452.1238 | 881.7881 | 881.7881 | -881.7881 | -858.2433 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.4 | 2610.4191 | 2610.4191 | 2610.4191 | 2524.7595 | 1044.1676 | 1044.1676 | -1044.1676 | -1009.9038 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.45 | 2718.8648 | 2718.8648 | 2718.8648 | 2610.9125 | 1223.4891 | 1223.4891 | -1223.4891 | -1174.9106 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.5 | 2827.3104 | 2827.3104 | 2827.3104 | 2697.0655 | 1413.6552 | 1413.6552 | -1413.6552 | -1348.5328 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.51 | 2851.7465 | 2851.7465 | 2851.7465 | 2717.6879 | 1454.3907 | 1454.3907 | -1454.3907 | -1386.0208 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.52 | 2876.1827 | 2876.1827 | 2876.1827 | 2738.3104 | 1495.615 | 1495.615 | -1495.615 | -1423.9214 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.53 | 2900.6188 | 2900.6188 | 2900.6188 | 2758.9328 | 1537.328 | 1537.328 | -1537.328 | -1462.2344 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.54 | 2925.055 | 2925.055 | 2925.055 | 2779.5552 | 1579.5297 | 1579.5297 | -1579.5297 | -1500.9598 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.55 | 2949.4911 | 2949.4911 | 2949.4911 | 2800.1776 | 1622.2201 | 1622.2201 | -1622.2201 | -1540.0977 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.56 | 2973.9273 | 2973.9273 | 2973.9273 | 2820.8001 | 1665.3993 | 1665.3993 | -1665.3993 | -1579.648 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.57 | 2998.3634 | 2998.3634 | 2998.3634 | 2841.4225 | 1709.0671 | 1709.0671 | -1709.0671 | -1619.6108 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.58 | 3022.7996 | 3022.7996 | 3022.7996 | 2862.0449 | 1753.2237 | 1753.2237 | -1753.2237 | -1659.9861 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.59 | 3047.2357 | 3047.2357 | 3047.2357 | 2882.6673 | 1797.8691 | 1797.8691 | -1797.8691 | -1700.7737 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.6 | 3071.6719 | 3071.6719 | 3071.6719 | 2903.2898 | 1843.0031 | 1843.0031 | -1843.0031 | -1741.9739 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.61 | 3098.2522 | 3098.2522 | 3098.2522 | 2926.5136 | 1889.9338 | 1889.9338 | -1889.9338 | -1785.1733 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.62 | 3124.8325 | 3124.8325 | 3124.8325 | 2949.7374 | 1937.3962 | 1937.3962 | -1937.3962 | -1828.8372 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.63 | 3151.4128 | 3151.4128 | 3151.4128 | 2972.9613 | 1985.3901 | 1985.3901 | -1985.3901 | -1872.9656 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.64 | 3177.9932 | 3177.9932 | 3177.9932 | 2996.1851 | 2033.9156 | 2033.9156 | -2033.9156 | -1917.5585 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.65 | 3204.5735 | 3204.5735 | 3204.5735 | 3019.4089 | 2082.9728 | 2082.9728 | -2082.9728 | -1962.6158 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.66 | 3231.1538 | 3231.1538 | 3231.1538 | 3042.6328 | 2132.5615 | 2132.5615 | -2132.5615 | -2008.1376 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.67 | 3257.7341 | 3257.7341 | 3257.7341 | 3065.8566 | 2182.6819 | 2182.6819 | -2182.6819 | -2054.1239 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.68 | 3284.3144 | 3284.3144 | 3284.3144 | 3089.0804 | 2233.3338 | 2233.3338 | -2233.3338 | -2100.5747 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.69 | 3310.8948 | 3310.8948 | 3310.8948 | 3112.3042 | 2284.5174 | 2284.5174 | -2284.5174 | -2147.4899 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.7 | 3337.4751 | 3337.4751 | 3337.4751 | 3135.5281 | 2336.2326 | 2336.2326 | -2336.2326 | -2194.8697 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.71 | 3365.7276 | 3365.7276 | 3361.3366 | 3148.4629 | 2389.6666 | 2389.6666 | -2386.549 | -2235.4086 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.72 | 3393.9801 | 3393.9801 | 3385.1981 | 3161.3976 | 2443.6657 | 2443.6657 | -2437.3426 | -2276.2063 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.73 | 3422.2326 | 3422.2326 | 3409.0596 | 3174.3324 | 2498.2298 | 2498.2298 | -2488.6135 | -2317.2627 | 2172.003 | -2172.003 | 2172.003 | -2169.4884
0.74 | 3450.4851 | 3450.4851 | 3432.9211 | 3187.2672 | 2553.3589 | 2553.3589 | -2540.3616 | -2358.5777 | 2172.003 | -2172.003 | 2172.003 | -2143.7778
0.75 | 3478.7375 | 3478.7375 | 3456.7825 | 3200.202 | 2609.0532 | 2609.0532 | -2592.5869 | -2400.1515 | 2172.003 | -2172.003 | 2172.003 | -2116.7346
0.76 | 3506.99 | 3506.99 | 3480.644 | 3213.1367 | 2665.3124 | 2665.3124 | -2645.2895 | -2441.9839 | 2172.003 | -2172.003 | 2172.003 | -2088.2917
0.77 | 3535.2425 | 3535.2425 | 3504.5055 | 3226.0715 | 2722.1367 | 2722.1367 | -2698.4692 | -2484.0751 | 2172.003 | -2172.003 | 2172.003 | -2058.3752
0.78 | 3563.495 | 3563.495 | 3528.367 | 3239.0063 | 2779.5261 | 2779.5261 | -2752.1263 | -2526.4249 | 2172.003 | -2172.003 | 2172.003 | -2026.9038
0.79 | 3591.7475 | 3591.7475 | 3552.2285 | 3251.9411 | 2837.4805 | 2837.4805 | -2806.2605 | -2569.0334 | 2172.003 | -2172.003 | 2172.003 | -1993.7873
0.8 | 3620 | 3620 | 3576.09 | 3264.8759 | 2896 | 2896 | -2860.872 | -2611.9007 | 2172 | -2172 | 2145.654 | -1958.9255
0.81 | 3620 | 3620 | 3571.2535 | 3270.6119 | 2932.2 | 2932.2 | -2892.7154 | -2649.1957 | 2122.8762 | -2122.8762 | 2094.2898 | -1917.9846
0.82 | 3620 | 3620 | 3566.4171 | 3276.348 | 2968.4 | 2968.4 | -2924.462 | -2686.6054 | 2071.9559 | -2071.9559 | 2041.287 | -1875.2621
0.83 | 3620 | 3620 | 3561.5806 | 3282.0841 | 3004.6 | 3004.6 | -2956.1119 | -2724.1298 | 2019.1035 | -2019.1035 | 1986.5193 | -1830.6264
0.84 | 3620 | 3620 | 3556.7442 | 3287.8202 | 3040.8 | 3040.8 | -2987.6651 | -2761.769 | 1964.1628 | -1964.1628 | 1929.841 | -1783.9265
0.85 | 3620 | 3620 | 3551.9078 | 3293.5563 | 3077 | 3077 | -3019.1216 | -2799.5228 | 1906.9533 | -1906.9533 | 1871.0835 | -1734.9884
0.86 | 3620 | 3620 | 3547.0713 | 3299.2924 | 3113.2 | 3113.2 | -3050.4813 | -2837.3914 | 1847.2644 | -1847.2644 | 1810.0493 | -1683.6092
0.87 | 3620 | 3620 | 3542.2349 | 3305.0285 | 3149.4 | 3149.4 | -3081.7443 | -2875.3748 | 1784.8472 | -1784.8472 | 1746.505 | -1629.55
0.88 | 3620 | 3620 | 3537.3984 | 3310.7646 | 3185.6 | 3185.6 | -3112.9106 | -2913.4728 | 1719.4047 | -1719.4047 | 1680.1712 | -1572.526
0.89 | 3620 | 3620 | 3532.562 | 3316.5006 | 3221.8 | 3221.8 | -3143.9802 | -2951.6856 | 1650.5771 | -1650.5771 | 1610.7088 | -1512.1934
0.9 | 3620 | 3620 | 3527.7255 | 3322.2367 | 3258 | 3258 | -3174.953 | -2990.0131 | 1577.9214 | -1577.9214 | 1537.6999 | -1448.1294
0.91 | 3620 | 3620 | 3520.9663 | 3329.3069 | 3294.2 | 3294.2 | -3204.0794 | -3029.6692 | 1500.8819 | -1500.8819 | 1459.8217 | -1380.3581
0.92 | 3620 | 3620 | 3514.2071 | 3336.377 | 3330.4 | 3330.4 | -3233.0706 | -3069.4668 | 1418.7445 | -1418.7445 | 1377.2823 | -1307.5874
0.93 | 3620 | 3620 | 3507.448 | 3343.4471 | 3366.6 | 3366.6 | -3261.9266 | -3109.4058 | 1330.5655 | -1330.5655 | 1289.1959 | -1228.9158
0.94 | 3620 | 3620 | 3500.6888 | 3350.5173 | 3402.8 | 3402.8 | -3290.6474 | -3149.4862 | 1235.0515 | -1235.0515 | 1194.3455 | -1143.1109
0.95 | 3620 | 3620 | 3493.9296 | 3357.5874 | 3439 | 3439 | -3319.2331 | -3189.708 | 1130.3446 | -1130.3446 | 1090.9792 | -1048.4063
0.96 | 3620 | 3620 | 3480.4727 | 3371.3989 | 3475.2 | 3475.2 | -3341.2538 | -3236.543 | 1013.6 | -1013.6 | 974.5323 | -943.9917
0.97 | 3620 | 3620 | 3467.0158 | 3385.2105 | 3511.4 | 3511.4 | -3363.0053 | -3283.6542 | 880.0398 | -880.0398 | 842.8486 | -822.9613
0.98 | 3620 | 3620 | 3453.5589 | 3399.022 | 3547.6 | 3547.6 | -3384.4877 | -3331.0416 | 720.3709 | -720.3709 | 687.2495 | -676.3968
0.99 | 3620 | 3620 | 3440.102 | 3412.8335 | 3583.8 | 3583.8 | -3405.7009 | -3378.7052 | 510.6638 | -510.6638 | 485.2861 | -481.4394
1 | 3620 | 3620 | 3426.6451 | 3426.6451 | 3620 | 3620 | -3426.6451 | -3426.6451 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_25C_1.1pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 25 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1490 |  | VDC
Nom. Battery Voltage** |  |  |  | 1291.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1159 |  | VDC |  | Please select:
AC Voltage |  |  |  | 1.1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2172 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP @25°C, 1159Vdc min. battery voltage and 1.1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2172.003 | 2172.003 | 2172.003 | 2172.003 | 0 | 0 | 0 | 0 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.01 | 2172.003 | 2172.003 | 2172.003 | 2172.003 | 0.02172 | 0.02172 | -0.02172 | -0.02172 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.05 | 2186.98 | 2186.98 | 2186.98 | 2186.98 | 109.349 | 109.349 | -109.349 | -109.349 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.1 | 2201.96 | 2201.96 | 2201.96 | 2201.96 | 220.196 | 220.196 | -220.196 | -220.196 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.15 | 2245.7245 | 2245.7245 | 2245.7245 | 2244.6232 | 336.8587 | 336.8587 | -336.8587 | -336.6935 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.2 | 2289.489 | 2289.489 | 2289.489 | 2287.2863 | 457.8978 | 457.8978 | -457.8978 | -457.4573 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.25 | 2358.9294 | 2358.9294 | 2358.9294 | 2352.8682 | 589.7324 | 589.7324 | -589.7324 | -588.2171 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.3 | 2428.3698 | 2428.3698 | 2428.3698 | 2418.4501 | 728.5109 | 728.5109 | -728.5109 | -725.535 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.35 | 2519.3945 | 2519.3945 | 2519.3945 | 2502.9902 | 881.7881 | 881.7881 | -881.7881 | -876.0466 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.4 | 2610.4191 | 2610.4191 | 2610.4191 | 2587.5302 | 1044.1676 | 1044.1676 | -1044.1676 | -1035.0121 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.45 | 2718.8648 | 2718.8648 | 2718.8648 | 2688.5166 | 1223.4891 | 1223.4891 | -1223.4891 | -1209.8325 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.5 | 2827.3104 | 2827.3104 | 2827.3104 | 2789.503 | 1413.6552 | 1413.6552 | -1413.6552 | -1394.7515 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.51 | 2851.7465 | 2851.7465 | 2851.7465 | 2813.3979 | 1454.3907 | 1454.3907 | -1454.3907 | -1434.833 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.52 | 2876.1827 | 2876.1827 | 2876.1827 | 2837.2929 | 1495.615 | 1495.615 | -1495.615 | -1475.3923 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.53 | 2900.6188 | 2900.6188 | 2900.6188 | 2861.1879 | 1537.328 | 1537.328 | -1537.328 | -1516.4296 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.54 | 2925.055 | 2925.055 | 2925.055 | 2885.0828 | 1579.5297 | 1579.5297 | -1579.5297 | -1557.9447 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.55 | 2949.4911 | 2949.4911 | 2949.4911 | 2908.9778 | 1622.2201 | 1622.2201 | -1622.2201 | -1599.9378 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.56 | 2973.9273 | 2973.9273 | 2973.9273 | 2932.8727 | 1665.3993 | 1665.3993 | -1665.3993 | -1642.4087 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.57 | 2998.3634 | 2998.3634 | 2998.3634 | 2956.7677 | 1709.0671 | 1709.0671 | -1709.0671 | -1685.3576 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.58 | 3022.7996 | 3022.7996 | 3022.7996 | 2980.6626 | 1753.2237 | 1753.2237 | -1753.2237 | -1728.7843 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.59 | 3047.2357 | 3047.2357 | 3047.2357 | 3004.5576 | 1797.8691 | 1797.8691 | -1797.8691 | -1772.689 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.6 | 3071.6719 | 3071.6719 | 3071.6719 | 3028.4525 | 1843.0031 | 1843.0031 | -1843.0031 | -1817.0715 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.61 | 3098.2522 | 3098.2522 | 3098.2522 | 3055.192 | 1889.9338 | 1889.9338 | -1889.9338 | -1863.6671 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.62 | 3124.8325 | 3124.8325 | 3124.8325 | 3081.9314 | 1937.3962 | 1937.3962 | -1937.3962 | -1910.7975 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.63 | 3151.4128 | 3151.4128 | 3151.4128 | 3108.6708 | 1985.3901 | 1985.3901 | -1985.3901 | -1958.4626 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.64 | 3177.9932 | 3177.9932 | 3177.9932 | 3135.4103 | 2033.9156 | 2033.9156 | -2033.9156 | -2006.6626 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.65 | 3204.5735 | 3204.5735 | 3204.5735 | 3162.1497 | 2082.9728 | 2082.9728 | -2082.9728 | -2055.3973 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.66 | 3231.1538 | 3231.1538 | 3231.1538 | 3188.8892 | 2132.5615 | 2132.5615 | -2132.5615 | -2104.6668 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.67 | 3257.7341 | 3257.7341 | 3257.7341 | 3215.6286 | 2182.6819 | 2182.6819 | -2182.6819 | -2154.4712 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.68 | 3284.3144 | 3284.3144 | 3284.3144 | 3242.368 | 2233.3338 | 2233.3338 | -2233.3338 | -2204.8103 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.69 | 3310.8948 | 3310.8948 | 3310.8948 | 3269.1075 | 2284.5174 | 2284.5174 | -2284.5174 | -2255.6841 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.7 | 3337.4751 | 3337.4751 | 3337.4751 | 3295.8469 | 2336.2326 | 2336.2326 | -2336.2326 | -2307.0928 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.71 | 3365.7276 | 3365.7276 | 3365.7276 | 3328.2622 | 2389.6666 | 2389.6666 | -2389.6666 | -2363.0662 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.72 | 3393.9801 | 3393.9801 | 3393.9801 | 3360.6775 | 2443.6657 | 2443.6657 | -2443.6657 | -2419.6878 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.73 | 3422.2326 | 3422.2326 | 3422.2326 | 3393.0928 | 2498.2298 | 2498.2298 | -2498.2298 | -2476.9578 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.74 | 3450.4851 | 3450.4851 | 3450.4851 | 3425.5081 | 2553.3589 | 2553.3589 | -2553.3589 | -2534.876 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.75 | 3478.7375 | 3478.7375 | 3478.7375 | 3457.9234 | 2609.0532 | 2609.0532 | -2609.0532 | -2593.4426 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.76 | 3506.99 | 3506.99 | 3506.99 | 3490.3388 | 2665.3124 | 2665.3124 | -2665.3124 | -2652.6575 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.77 | 3535.2425 | 3535.2425 | 3535.2425 | 3522.7541 | 2722.1367 | 2722.1367 | -2722.1367 | -2712.5206 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.78 | 3563.495 | 3563.495 | 3563.495 | 3555.1694 | 2779.5261 | 2779.5261 | -2779.5261 | -2773.0321 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.79 | 3591.7475 | 3591.7475 | 3591.7475 | 3577.1352 | 2837.4805 | 2837.4805 | -2837.4805 | -2825.9368 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.8 | 3620 | 3620 | 3620 | 3591.3634 | 2896 | 2896 | -2896 | -2873.0907 | 2172 | -2172 | 2172 | -2154.8181
0.81 | 3620 | 3620 | 3620 | 3597.6731 | 2932.2 | 2932.2 | -2932.2 | -2914.1152 | 2122.8762 | -2122.8762 | 2122.8762 | -2109.783
0.82 | 3620 | 3620 | 3620 | 3603.9828 | 2968.4 | 2968.4 | -2968.4 | -2955.2659 | 2071.9559 | -2071.9559 | 2071.9559 | -2062.7883
0.83 | 3620 | 3620 | 3620 | 3610.2925 | 3004.6 | 3004.6 | -3004.6 | -2996.5428 | 2019.1035 | -2019.1035 | 2019.1035 | -2013.689
0.84 | 3620 | 3620 | 3620 | 3616.6022 | 3040.8 | 3040.8 | -3040.8 | -3037.9459 | 1964.1628 | -1964.1628 | 1964.1628 | -1962.3192
0.85 | 3620 | 3620 | 3620 | 3620 | 3077 | 3077 | -3077 | -3077 | 1906.9533 | -1906.9533 | 1906.9533 | -1906.9533
0.86 | 3620 | 3620 | 3620 | 3620 | 3113.2 | 3113.2 | -3113.2 | -3113.2 | 1847.2644 | -1847.2644 | 1847.2644 | -1847.2644
0.87 | 3620 | 3620 | 3620 | 3620 | 3149.4 | 3149.4 | -3149.4 | -3149.4 | 1784.8472 | -1784.8472 | 1784.8472 | -1784.8472
0.88 | 3620 | 3620 | 3620 | 3620 | 3185.6 | 3185.6 | -3185.6 | -3185.6 | 1719.4047 | -1719.4047 | 1719.4047 | -1719.4047
0.89 | 3620 | 3620 | 3620 | 3620 | 3221.8 | 3221.8 | -3221.8 | -3221.8 | 1650.5771 | -1650.5771 | 1650.5771 | -1650.5771
0.9 | 3620 | 3620 | 3620 | 3620 | 3258 | 3258 | -3258 | -3258 | 1577.9214 | -1577.9214 | 1577.9214 | -1577.9214
0.91 | 3620 | 3620 | 3620 | 3620 | 3294.2 | 3294.2 | -3294.2 | -3294.2 | 1500.8819 | -1500.8819 | 1500.8819 | -1500.8819
0.92 | 3620 | 3620 | 3620 | 3620 | 3330.4 | 3330.4 | -3330.4 | -3330.4 | 1418.7445 | -1418.7445 | 1418.7445 | -1418.7445
0.93 | 3620 | 3620 | 3620 | 3620 | 3366.6 | 3366.6 | -3366.6 | -3366.6 | 1330.5655 | -1330.5655 | 1330.5655 | -1330.5655
0.94 | 3620 | 3620 | 3620 | 3620 | 3402.8 | 3402.8 | -3402.8 | -3402.8 | 1235.0515 | -1235.0515 | 1235.0515 | -1235.0515
0.95 | 3620 | 3620 | 3620 | 3620 | 3439 | 3439 | -3439 | -3439 | 1130.3446 | -1130.3446 | 1130.3446 | -1130.3446
0.96 | 3620 | 3620 | 3620 | 3620 | 3475.2 | 3475.2 | -3475.2 | -3475.2 | 1013.6 | -1013.6 | 1013.6 | -1013.6
0.97 | 3620 | 3620 | 3620 | 3620 | 3511.4 | 3511.4 | -3511.4 | -3511.4 | 880.0398 | -880.0398 | 880.0398 | -880.0398
0.98 | 3620 | 3620 | 3620 | 3620 | 3547.6 | 3547.6 | -3547.6 | -3547.6 | 720.3709 | -720.3709 | 720.3709 | -720.3709
0.99 | 3620 | 3620 | 3620 | 3620 | 3583.8 | 3583.8 | -3583.8 | -3583.8 | 510.6638 | -510.6638 | 510.6638 | -510.6638
1 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | -3620 | -3620 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_35C_0.9pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 35 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1490 |  | VDC
Nom. Battery Voltage** |  |  |  | 1291.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1159 |  | VDC |  | Please select:
AC Voltage |  |  |  | 0.9 |  | pu |  | Project plant specific |  |  | VArRtg: | 2172 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP @35°C, 1159Vdc min. battery voltage and 0.9pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 1954.8024 | 1954.8023 | 1954.8024 | 1954.802 | 0 | 0 | 0 | 0 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.802
0.01 | 1954.8024 | 1954.8023 | 1954.8024 | 1954.802 | 0.019548 | 0.019548 | -0.019548 | -0.019548 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.802
0.05 | 1966.7481 | 1966.4425 | 1966.7481 | 1964.6457 | 98.3374 | 98.3221 | -98.3374 | -98.2323 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.1 | 1978.6961 | 1978.0849 | 1978.6961 | 1974.4915 | 197.8696 | 197.8085 | -197.8696 | -197.4491 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.15 | 2013.6982 | 2013.0068 | 2013.6982 | 2002.329 | 302.0547 | 301.951 | -302.0547 | -300.3494 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.2 | 2048.7003 | 2047.9287 | 2048.7003 | 2030.1666 | 409.7401 | 409.5857 | -409.7401 | -406.0333 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.25 | 2104.5035 | 2104.1177 | 2104.5035 | 2073.8602 | 526.1259 | 526.0294 | -526.1259 | -518.4651 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.3 | 2160.3067 | 2160.3067 | 2160.3067 | 2117.5538 | 648.092 | 648.092 | -648.092 | -635.2661 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.35 | 2233.8826 | 2233.8826 | 2233.8826 | 2174.9345 | 781.8589 | 781.8589 | -781.8589 | -761.2271 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.4 | 2307.4585 | 2307.4585 | 2307.4585 | 2232.3151 | 922.9834 | 922.9834 | -922.9834 | -892.926 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.45 | 2395.6429 | 2395.6429 | 2395.6429 | 2300.5535 | 1078.0393 | 1078.0393 | -1078.0393 | -1035.2491 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.5 | 2483.8273 | 2483.8273 | 2483.8273 | 2368.7918 | 1241.9136 | 1241.9136 | -1241.9136 | -1184.3959 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.51 | 2503.8095 | 2503.8095 | 2503.0255 | 2385.29 | 1276.9429 | 1276.9429 | -1276.543 | -1216.4979 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.52 | 2523.7917 | 2523.7917 | 2522.2237 | 2401.7881 | 1312.3717 | 1312.3717 | -1311.5563 | -1248.9298 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.53 | 2543.774 | 2543.774 | 2541.4219 | 2418.2863 | 1348.2002 | 1348.2002 | -1346.9536 | -1281.6917 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.54 | 2563.7562 | 2563.7562 | 2560.6201 | 2434.7844 | 1384.4283 | 1384.4283 | -1382.7348 | -1314.7836 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.55 | 2583.7384 | 2583.7384 | 2579.8182 | 2451.2826 | 1421.0561 | 1421.0561 | -1418.9 | -1348.2054 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.56 | 2603.7206 | 2603.7206 | 2599.0164 | 2467.7808 | 1458.0836 | 1458.0836 | -1455.4492 | -1381.9572 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.57 | 2623.7029 | 2623.7029 | 2618.2146 | 2484.2789 | 1495.5106 | 1495.5106 | -1492.3823 | -1416.039 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.58 | 2643.6851 | 2643.6851 | 2637.4128 | 2500.7771 | 1533.3374 | 1533.3374 | -1529.6994 | -1450.4507 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.59 | 2663.6673 | 2663.6673 | 2656.611 | 2517.2753 | 1571.5637 | 1571.5637 | -1567.4005 | -1485.1924 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.6 | 2683.6495 | 2683.6495 | 2675.8092 | 2533.7734 | 1610.1897 | 1610.1897 | -1605.4855 | -1520.2641 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.61 | 2705.4928 | 2705.4928 | 2696.2582 | 2548.0097 | 1650.3506 | 1650.3506 | -1644.7175 | -1554.2859 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.62 | 2727.336 | 2727.336 | 2716.7072 | 2562.246 | 1690.9483 | 1690.9483 | -1684.3585 | -1588.5925 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.63 | 2749.1792 | 2749.1792 | 2737.1562 | 2576.4822 | 1731.9829 | 1731.9829 | -1724.4084 | -1623.1838 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.64 | 2771.0224 | 2771.0224 | 2757.6052 | 2590.7185 | 1773.4543 | 1773.4543 | -1764.8673 | -1658.0598 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.65 | 2792.8656 | 2792.8656 | 2778.0542 | 2604.9548 | 1815.3626 | 1815.3626 | -1805.7352 | -1693.2206 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.66 | 2814.7088 | 2814.7088 | 2798.5031 | 2619.191 | 1857.7078 | 1857.7078 | -1847.0121 | -1728.6661 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.67 | 2836.552 | 2836.552 | 2818.9521 | 2633.4273 | 1900.4899 | 1900.4899 | -1888.6979 | -1764.3963 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.68 | 2858.3952 | 2858.3952 | 2839.4011 | 2647.6636 | 1943.7088 | 1943.7088 | -1930.7928 | -1800.4112 | 1954.8024 | -1954.8023 | 1954.8024 | -1941.299
0.69 | 2880.2384 | 2880.2384 | 2859.8501 | 2661.8998 | 1987.3645 | 1987.3645 | -1973.2966 | -1836.7109 | 1954.8024 | -1954.8023 | 1954.8024 | -1926.708
0.7 | 2902.0816 | 2902.0816 | 2880.2991 | 2676.1361 | 2031.4572 | 2031.4572 | -2016.2094 | -1873.2953 | 1954.8024 | -1954.8023 | 1954.8024 | -1911.1434
0.71 | 2918.157 | 2918.157 | 2890.9977 | 2681.9228 | 2071.8914 | 2071.8914 | -2052.6083 | -1904.1652 | 1954.8024 | -1954.8023 | 1954.8024 | -1888.6145
0.72 | 2934.2323 | 2934.2323 | 2901.6962 | 2687.7096 | 2112.6472 | 2112.6472 | -2089.2213 | -1935.1509 | 1954.8024 | -1954.8023 | 1954.8024 | -1865.2007
0.73 | 2950.3076 | 2950.3076 | 2912.3948 | 2693.4963 | 2153.7245 | 2153.7245 | -2126.0482 | -1966.2523 | 1954.8024 | -1954.8023 | 1954.8024 | -1840.8623
0.74 | 2966.3829 | 2966.3829 | 2923.0934 | 2699.283 | 2195.1233 | 2195.1233 | -2163.0891 | -1997.4694 | 1954.8024 | -1954.8023 | 1954.8024 | -1815.5563
0.75 | 2982.4582 | 2982.4582 | 2933.7919 | 2705.0697 | 2236.8437 | 2236.8437 | -2200.3439 | -2028.8023 | 1954.8024 | -1954.8023 | 1940.5209 | -1789.2354
0.76 | 2998.5335 | 2998.5335 | 2944.4905 | 2710.8565 | 2278.8855 | 2278.8855 | -2237.8128 | -2060.2509 | 1948.8161 | -1948.8161 | 1913.6923 | -1761.8482
0.77 | 3014.6088 | 3014.6088 | 2955.189 | 2716.6432 | 2321.2488 | 2321.2488 | -2275.4956 | -2091.8153 | 1923.4527 | -1923.4527 | 1885.5403 | -1733.3376
0.78 | 3030.6842 | 3030.6842 | 2965.8876 | 2722.4299 | 2363.9336 | 2363.9336 | -2313.3923 | -2123.4953 | 1896.5401 | -1896.5401 | 1855.9917 | -1703.6409
0.79 | 3046.7595 | 3046.7595 | 2976.5862 | 2728.2166 | 2406.94 | 2406.94 | -2351.5031 | -2155.2912 | 1867.9891 | -1867.9891 | 1824.9653 | -1672.6883
0.8 | 3062.8348 | 3062.8348 | 2987.2847 | 2734.0034 | 2450.2678 | 2450.2678 | -2389.8278 | -2187.2027 | 1837.7009 | -1837.7009 | 1792.3708 | -1640.402
0.81 | 3062.8348 | 3062.8348 | 2983.1913 | 2738.6888 | 2480.8962 | 2480.8962 | -2416.385 | -2218.338 | 1796.1378 | -1796.1378 | 1749.4325 | -1606.049
0.82 | 3062.8348 | 3062.8348 | 2979.0979 | 2743.3743 | 2511.5245 | 2511.5245 | -2442.8603 | -2249.5669 | 1753.0549 | -1753.0549 | 1705.127 | -1570.2074
0.83 | 3062.8348 | 3062.8348 | 2975.0045 | 2748.0598 | 2542.1529 | 2542.1529 | -2469.2537 | -2280.8896 | 1708.3371 | -1708.3371 | 1659.3486 | -1532.7671
0.84 | 3062.8348 | 3062.8348 | 2970.9111 | 2752.7453 | 2572.7812 | 2572.7812 | -2495.5653 | -2312.306 | 1661.8525 | -1661.8525 | 1611.976 | -1493.6021
0.85 | 3062.8348 | 3062.8348 | 2966.8177 | 2757.4307 | 2603.4096 | 2603.4096 | -2521.795 | -2343.8161 | 1613.4483 | -1613.4483 | 1562.8682 | -1452.5668
0.86 | 3062.8348 | 3062.8348 | 2962.7243 | 2762.1162 | 2634.0379 | 2634.0379 | -2547.9429 | -2375.4199 | 1562.9463 | -1562.9463 | 1511.8605 | -1409.4914
0.87 | 3062.8348 | 3062.8348 | 2958.6309 | 2766.8017 | 2664.6663 | 2664.6663 | -2574.0089 | -2407.1175 | 1510.136 | -1510.136 | 1458.7581 | -1364.1763
0.88 | 3062.8348 | 3062.8348 | 2954.5375 | 2771.4871 | 2695.2946 | 2695.2946 | -2599.993 | -2438.9087 | 1454.7659 | -1454.7659 | 1403.3276 | -1316.3835
0.89 | 3062.8348 | 3062.8348 | 2950.4441 | 2776.1726 | 2725.923 | 2725.923 | -2625.8952 | -2470.7936 | 1396.5318 | -1396.5318 | 1345.286 | -1265.8251
0.9 | 3062.8348 | 3062.8348 | 2946.3507 | 2780.8581 | 2756.5513 | 2756.5513 | -2651.7156 | -2502.7723 | 1335.0587 | -1335.0587 | 1284.2845 | -1212.1479
0.91 | 3062.8348 | 3062.8348 | 2940.2248 | 2787.2103 | 2787.1797 | 2787.1797 | -2675.6045 | -2536.3614 | 1269.8766 | -1269.8766 | 1219.0414 | -1155.6004
0.92 | 3062.8348 | 3062.8348 | 2934.0989 | 2793.5625 | 2817.808 | 2817.808 | -2699.371 | -2570.0775 | 1200.3812 | -1200.3812 | 1149.9272 | -1094.8484
0.93 | 3062.8348 | 3062.8348 | 2927.973 | 2799.9147 | 2848.4363 | 2848.4363 | -2723.0148 | -2603.9206 | 1125.7741 | -1125.7741 | 1076.2043 | -1029.1353
0.94 | 3062.8348 | 3062.8348 | 2921.847 | 2806.2669 | 2879.0647 | 2879.0647 | -2746.5362 | -2637.8909 | 1044.9609 | -1044.9609 | 996.8595 | -957.4265
0.95 | 3062.8348 | 3062.8348 | 2915.7211 | 2812.6191 | 2909.693 | 2909.693 | -2769.9351 | -2671.9881 | 956.3699 | -956.3699 | 910.4336 | -878.24
0.96 | 3062.786 | 3062.786 | 2906.5317 | 2824.05 | 2940.2746 | 2940.2746 | -2790.2704 | -2711.088 | 857.5801 | -857.5801 | 813.8289 | -790.734
0.97 | 3062.7373 | 3062.7373 | 2897.3422 | 2835.481 | 2970.8551 | 2970.8551 | -2810.422 | -2750.4166 | 744.5665 | -744.5665 | 704.3581 | -689.3194
0.98 | 3062.6885 | 3062.6885 | 2888.1528 | 2846.912 | 3001.4347 | 3001.4347 | -2830.3897 | -2789.9737 | 609.4673 | -609.4673 | 574.7351 | -566.5283
0.99 | 3062.6397 | 3062.6397 | 2878.9633 | 2858.3429 | 3032.0134 | 3032.0134 | -2850.1737 | -2829.7595 | 432.0385 | -432.0385 | 406.1278 | -403.2189
1 | 3062.591 | 3062.591 | 2869.7739 | 2869.7739 | 3062.591 | 3062.591 | -2869.7739 | -2869.7739 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_35C_1.0pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 35 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1490 |  | VDC
Nom. Battery Voltage** |  |  |  | 1291.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1159 |  | VDC |  | Please select:
AC Voltage |  |  |  | 1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2172 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP @35°C, 1159Vdc min. battery voltage and 1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2172.0027 | 2172.0026 | 2172.0027 | 2172.0022 | 0 | 0 | 0 | 0 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0022
0.01 | 2172.0027 | 2172.0026 | 2172.0027 | 2172.0022 | 0.02172 | 0.02172 | -0.02172 | -0.02172 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0022
0.05 | 2185.2756 | 2184.9361 | 2185.2756 | 2182.9397 | 109.2638 | 109.2468 | -109.2638 | -109.147 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.1 | 2198.5512 | 2197.8721 | 2198.5512 | 2193.8794 | 219.8551 | 219.7872 | -219.8551 | -219.3879 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.15 | 2237.4425 | 2236.6742 | 2237.4425 | 2224.81 | 335.6164 | 335.5011 | -335.6164 | -333.7215 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.2 | 2276.3337 | 2275.4764 | 2276.3337 | 2255.7407 | 455.2667 | 455.0953 | -455.2667 | -451.1481 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.25 | 2338.3372 | 2337.9086 | 2338.3372 | 2304.2891 | 584.5843 | 584.4771 | -584.5843 | -576.0723 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.3 | 2400.3408 | 2400.3408 | 2400.3408 | 2352.8376 | 720.1022 | 720.1022 | -720.1022 | -705.8513 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.35 | 2482.0918 | 2482.0918 | 2482.0918 | 2416.5938 | 868.7321 | 868.7321 | -868.7321 | -845.8078 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.4 | 2563.8428 | 2563.8428 | 2563.8428 | 2480.3501 | 1025.5371 | 1025.5371 | -1025.5371 | -992.1401 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.45 | 2661.8254 | 2661.8254 | 2661.8254 | 2556.1705 | 1197.8214 | 1197.8214 | -1197.8214 | -1150.2767 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.5 | 2759.8081 | 2759.8081 | 2759.8081 | 2631.9909 | 1379.9041 | 1379.9041 | -1379.9041 | -1315.9954 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.51 | 2782.0106 | 2782.0106 | 2781.1394 | 2650.3222 | 1418.8254 | 1418.8254 | -1418.3811 | -1351.6643 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.52 | 2804.2131 | 2804.2131 | 2802.4708 | 2668.6535 | 1458.1908 | 1458.1908 | -1457.2848 | -1387.6998 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.53 | 2826.4155 | 2826.4155 | 2823.8021 | 2686.9848 | 1498.0002 | 1498.0002 | -1496.6151 | -1424.1019 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.54 | 2848.618 | 2848.618 | 2845.1334 | 2705.3161 | 1538.2537 | 1538.2537 | -1536.372 | -1460.8707 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.55 | 2870.8205 | 2870.8205 | 2866.4647 | 2723.6473 | 1578.9513 | 1578.9513 | -1576.5556 | -1498.006 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.56 | 2893.0229 | 2893.0229 | 2887.796 | 2741.9786 | 1620.0928 | 1620.0928 | -1617.1658 | -1535.508 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.57 | 2915.2254 | 2915.2254 | 2909.1274 | 2760.3099 | 1661.6785 | 1661.6785 | -1658.2026 | -1573.3767 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.58 | 2937.4279 | 2937.4279 | 2930.4587 | 2778.6412 | 1703.7082 | 1703.7082 | -1699.666 | -1611.6119 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.59 | 2959.6304 | 2959.6304 | 2951.79 | 2796.9725 | 1746.1819 | 1746.1819 | -1741.5561 | -1650.2138 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.6 | 2981.8328 | 2981.8328 | 2973.1213 | 2815.3038 | 1789.0997 | 1789.0997 | -1783.8728 | -1689.1823 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.61 | 3006.1031 | 3006.1031 | 2995.8424 | 2831.1219 | 1833.7229 | 1833.7229 | -1827.4639 | -1726.9843 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.62 | 3030.3733 | 3030.3733 | 3018.5635 | 2846.94 | 1878.8314 | 1878.8314 | -1871.5094 | -1765.1028 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.63 | 3054.6435 | 3054.6435 | 3041.2846 | 2862.758 | 1924.4254 | 1924.4254 | -1916.0093 | -1803.5376 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.64 | 3078.9138 | 3078.9138 | 3064.0057 | 2878.5761 | 1970.5048 | 1970.5048 | -1960.9637 | -1842.2887 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.65 | 3103.184 | 3103.184 | 3086.7268 | 2894.3942 | 2017.0696 | 2017.0696 | -2006.3724 | -1881.3562 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.66 | 3127.4542 | 3127.4542 | 3109.4479 | 2910.2123 | 2064.1198 | 2064.1198 | -2052.2356 | -1920.7401 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.67 | 3151.7245 | 3151.7245 | 3132.169 | 2926.0303 | 2111.6554 | 2111.6554 | -2098.5533 | -1960.4403 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.68 | 3175.9947 | 3175.9947 | 3154.8901 | 2941.8484 | 2159.6764 | 2159.6764 | -2145.3253 | -2000.4569 | 2172.0027 | -2172.0026 | 2172.0027 | -2156.9989
0.69 | 3200.2649 | 3200.2649 | 3177.6112 | 2957.6665 | 2208.1828 | 2208.1828 | -2192.5518 | -2040.7899 | 2172.0027 | -2172.0026 | 2172.0027 | -2140.7867
0.7 | 3224.5352 | 3224.5352 | 3200.3323 | 2973.4846 | 2257.1746 | 2257.1746 | -2240.2326 | -2081.4392 | 2172.0027 | -2172.0026 | 2172.0027 | -2123.4927
0.71 | 3242.3966 | 3242.3966 | 3212.2196 | 2979.9142 | 2302.1016 | 2302.1016 | -2280.6759 | -2115.7391 | 2172.0027 | -2172.0026 | 2172.0027 | -2098.4606
0.72 | 3260.2581 | 3260.2581 | 3224.1069 | 2986.3439 | 2347.3858 | 2347.3858 | -2321.357 | -2150.1676 | 2172.0027 | -2172.0026 | 2172.0027 | -2072.4452
0.73 | 3278.1195 | 3278.1195 | 3235.9942 | 2992.7736 | 2393.0273 | 2393.0273 | -2362.2758 | -2184.7248 | 2172.0027 | -2172.0026 | 2172.0027 | -2045.4026
0.74 | 3295.981 | 3295.981 | 3247.8815 | 2999.2033 | 2439.0259 | 2439.0259 | -2403.4323 | -2219.4105 | 2172.0027 | -2172.0026 | 2172.0027 | -2017.2848
0.75 | 3313.8425 | 3313.8425 | 3259.7688 | 3005.633 | 2485.3818 | 2485.3818 | -2444.8266 | -2254.2248 | 2172.0027 | -2172.0026 | 2156.1344 | -1988.0394
0.76 | 3331.7039 | 3331.7039 | 3271.6561 | 3012.0627 | 2532.095 | 2532.095 | -2486.4586 | -2289.1677 | 2165.3512 | -2165.3512 | 2126.3248 | -1957.6091
0.77 | 3349.5654 | 3349.5654 | 3283.5434 | 3018.4924 | 2579.1653 | 2579.1653 | -2528.3284 | -2324.2392 | 2137.1697 | -2137.1697 | 2095.0448 | -1925.9306
0.78 | 3367.4268 | 3367.4268 | 3295.4307 | 3024.9221 | 2626.5929 | 2626.5929 | -2570.4359 | -2359.4393 | 2107.2667 | -2107.2667 | 2062.213 | -1892.9343
0.79 | 3385.2883 | 3385.2883 | 3307.3179 | 3031.3518 | 2674.3778 | 2674.3778 | -2612.7812 | -2394.7679 | 2075.5434 | -2075.5434 | 2027.7393 | -1858.5425
0.8 | 3403.1498 | 3403.1498 | 3319.2052 | 3037.7815 | 2722.5198 | 2722.5198 | -2655.3642 | -2430.2252 | 2041.8899 | -2041.8899 | 1991.5231 | -1822.6689
0.81 | 3403.1498 | 3403.1498 | 3314.657 | 3042.9876 | 2756.5513 | 2756.5513 | -2684.8722 | -2464.82 | 1995.7087 | -1995.7087 | 1943.8139 | -1784.4988
0.82 | 3403.1498 | 3403.1498 | 3310.1088 | 3048.1937 | 2790.5828 | 2790.5828 | -2714.2892 | -2499.5188 | 1947.8388 | -1947.8388 | 1894.5855 | -1744.6749
0.83 | 3403.1498 | 3403.1498 | 3305.5606 | 3053.3998 | 2824.6143 | 2824.6143 | -2743.6153 | -2534.3218 | 1898.1523 | -1898.1523 | 1843.7207 | -1703.0746
0.84 | 3403.1498 | 3403.1498 | 3301.0123 | 3058.6058 | 2858.6458 | 2858.6458 | -2772.8504 | -2569.2289 | 1846.5028 | -1846.5028 | 1791.0844 | -1659.5579
0.85 | 3403.1498 | 3403.1498 | 3296.4641 | 3063.8119 | 2892.6773 | 2892.6773 | -2801.9945 | -2604.2401 | 1792.7204 | -1792.7204 | 1736.5202 | -1613.9631
0.86 | 3403.1498 | 3403.1498 | 3291.9159 | 3069.018 | 2926.7088 | 2926.7088 | -2831.0477 | -2639.3555 | 1736.607 | -1736.607 | 1679.845 | -1566.1016
0.87 | 3403.1498 | 3403.1498 | 3287.3677 | 3074.2241 | 2960.7403 | 2960.7403 | -2860.0099 | -2674.5749 | 1677.9288 | -1677.9288 | 1620.8423 | -1515.7515
0.88 | 3403.1498 | 3403.1498 | 3282.8194 | 3079.4302 | 2994.7718 | 2994.7718 | -2888.8811 | -2709.8985 | 1616.4066 | -1616.4066 | 1559.2528 | -1462.6483
0.89 | 3403.1498 | 3403.1498 | 3278.2712 | 3084.6362 | 3028.8033 | 3028.8033 | -2917.6614 | -2745.3262 | 1551.7019 | -1551.7019 | 1494.7623 | -1406.4724
0.9 | 3403.1498 | 3403.1498 | 3273.723 | 3089.8423 | 3062.8348 | 3062.8348 | -2946.3507 | -2780.8581 | 1483.3986 | -1483.3986 | 1426.9828 | -1346.831
0.91 | 3403.1498 | 3403.1498 | 3266.9164 | 3096.9003 | 3096.8663 | 3096.8663 | -2972.8939 | -2818.1793 | 1410.974 | -1410.974 | 1354.4905 | -1284.0004
0.92 | 3403.1498 | 3403.1498 | 3260.1098 | 3103.9583 | 3130.8978 | 3130.8978 | -2999.3011 | -2855.6416 | 1333.7569 | -1333.7569 | 1277.6969 | -1216.4982
0.93 | 3403.1498 | 3403.1498 | 3253.3033 | 3111.0163 | 3164.9293 | 3164.9293 | -3025.572 | -2893.2452 | 1250.8601 | -1250.8601 | 1195.7826 | -1143.4837
0.94 | 3403.1498 | 3403.1498 | 3246.4967 | 3118.0743 | 3198.9608 | 3198.9608 | -3051.7069 | -2930.9898 | 1161.0677 | -1161.0677 | 1107.6217 | -1063.8073
0.95 | 3403.1498 | 3403.1498 | 3239.6901 | 3125.1323 | 3232.9923 | 3232.9923 | -3077.7056 | -2968.8757 | 1062.6332 | -1062.6332 | 1011.5929 | -975.8222
0.96 | 3402.5198 | 3402.5198 | 3229.4796 | 3137.8334 | 3266.419 | 3266.419 | -3100.3005 | -3012.32 | 952.7055 | -952.7055 | 904.2543 | -878.5933
0.97 | 3401.8899 | 3401.8899 | 3219.2691 | 3150.5344 | 3299.8332 | 3299.8332 | -3122.6911 | -3056.0184 | 827.0161 | -827.0161 | 782.6202 | -765.9104
0.98 | 3401.2599 | 3401.2599 | 3209.0587 | 3163.2355 | 3333.2347 | 3333.2347 | -3144.8775 | -3099.9708 | 676.8422 | -676.8422 | 638.5946 | -629.4759
0.99 | 3400.63 | 3400.63 | 3198.8482 | 3175.9366 | 3366.6237 | 3366.6237 | -3166.8597 | -3144.1772 | 479.7179 | -479.7179 | 451.2531 | -448.021
1 | 3400 | 3400 | 3188.6377 | 3188.6377 | 3400 | 3400 | -3188.6377 | -3188.6377 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_35C_1.1pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 35 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1490 |  | VDC
Nom. Battery Voltage** |  |  |  | 1291.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1159 |  | VDC |  | Please select:
AC Voltage |  |  |  | 1.1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2172 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP @35°C, 1159Vdc min. battery voltage and 1.1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2172.0027 | 2172.0027 | 2172.0027 | 2172.0027 | 0 | 0 | 0 | 0 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.01 | 2172.0027 | 2172.0027 | 2172.0027 | 2172.0027 | 0.02172 | 0.02172 | -0.02172 | -0.02172 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.05 | 2185.2756 | 2185.2756 | 2185.2756 | 2185.2756 | 109.2638 | 109.2638 | -109.2638 | -109.2638 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.1 | 2198.5512 | 2198.5512 | 2198.5512 | 2198.5512 | 219.8551 | 219.8551 | -219.8551 | -219.8551 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.15 | 2237.4425 | 2237.4425 | 2237.4425 | 2235.6652 | 335.6164 | 335.6164 | -335.6164 | -335.3498 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.2 | 2276.3337 | 2276.3337 | 2276.3337 | 2272.7791 | 455.2667 | 455.2667 | -455.2667 | -454.5558 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.25 | 2338.3372 | 2338.3372 | 2338.3372 | 2330.9694 | 584.5843 | 584.5843 | -584.5843 | -582.7423 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.3 | 2400.3408 | 2400.3408 | 2400.3408 | 2389.1596 | 720.1022 | 720.1022 | -720.1022 | -716.7479 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.35 | 2482.0918 | 2482.0918 | 2482.0918 | 2464.2796 | 868.7321 | 868.7321 | -868.7321 | -862.4979 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.4 | 2563.8428 | 2563.8428 | 2563.8428 | 2539.3996 | 1025.5371 | 1025.5371 | -1025.5371 | -1015.7598 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.45 | 2661.8254 | 2661.8254 | 2661.8254 | 2627.3835 | 1197.8214 | 1197.8214 | -1197.8214 | -1182.3226 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.5 | 2759.8081 | 2759.8081 | 2759.8081 | 2715.3674 | 1379.9041 | 1379.9041 | -1379.9041 | -1357.6837 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.51 | 2782.0106 | 2782.0106 | 2782.0106 | 2737.2597 | 1418.8254 | 1418.8254 | -1418.8254 | -1396.0025 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.52 | 2804.2131 | 2804.2131 | 2804.2131 | 2759.152 | 1458.1908 | 1458.1908 | -1458.1908 | -1434.7591 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.53 | 2826.4155 | 2826.4155 | 2826.4155 | 2781.0444 | 1498.0002 | 1498.0002 | -1498.0002 | -1473.9535 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.54 | 2848.618 | 2848.618 | 2848.618 | 2802.9367 | 1538.2537 | 1538.2537 | -1538.2537 | -1513.5858 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.55 | 2870.8205 | 2870.8205 | 2870.8205 | 2824.829 | 1578.9513 | 1578.9513 | -1578.9513 | -1553.656 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.56 | 2893.0229 | 2893.0229 | 2893.0229 | 2846.7214 | 1620.0928 | 1620.0928 | -1620.0928 | -1594.164 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.57 | 2915.2254 | 2915.2254 | 2915.2254 | 2868.6137 | 1661.6785 | 1661.6785 | -1661.6785 | -1635.1098 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.58 | 2937.4279 | 2937.4279 | 2937.4279 | 2890.506 | 1703.7082 | 1703.7082 | -1703.7082 | -1676.4935 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.59 | 2959.6304 | 2959.6304 | 2959.6304 | 2912.3984 | 1746.1819 | 1746.1819 | -1746.1819 | -1718.315 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.6 | 2981.8328 | 2981.8328 | 2981.8328 | 2934.2907 | 1789.0997 | 1789.0997 | -1789.0997 | -1760.5744 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.61 | 3006.1031 | 3006.1031 | 3006.1031 | 2958.6028 | 1833.7229 | 1833.7229 | -1833.7229 | -1804.7477 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.62 | 3030.3733 | 3030.3733 | 3030.3733 | 2982.9148 | 1878.8314 | 1878.8314 | -1878.8314 | -1849.4072 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.63 | 3054.6435 | 3054.6435 | 3054.6435 | 3007.2269 | 1924.4254 | 1924.4254 | -1924.4254 | -1894.5529 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.64 | 3078.9138 | 3078.9138 | 3078.9138 | 3031.539 | 1970.5048 | 1970.5048 | -1970.5048 | -1940.1849 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.65 | 3103.184 | 3103.184 | 3103.184 | 3055.851 | 2017.0696 | 2017.0696 | -2017.0696 | -1986.3032 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.66 | 3127.4542 | 3127.4542 | 3127.4542 | 3080.1631 | 2064.1198 | 2064.1198 | -2064.1198 | -2032.9077 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.67 | 3151.7245 | 3151.7245 | 3151.7245 | 3104.4752 | 2111.6554 | 2111.6554 | -2111.6554 | -2079.9984 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.68 | 3175.9947 | 3175.9947 | 3175.9947 | 3128.7872 | 2159.6764 | 2159.6764 | -2159.6764 | -2127.5753 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.69 | 3200.2649 | 3200.2649 | 3200.2649 | 3153.0993 | 2208.1828 | 2208.1828 | -2208.1828 | -2175.6385 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.7 | 3224.5352 | 3224.5352 | 3224.5352 | 3177.4114 | 2257.1746 | 2257.1746 | -2257.1746 | -2224.188 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.71 | 3242.3966 | 3242.3966 | 3242.3966 | 3196.7434 | 2302.1016 | 2302.1016 | -2302.1016 | -2269.6878 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.72 | 3260.2581 | 3260.2581 | 3260.2581 | 3216.0755 | 2347.3858 | 2347.3858 | -2347.3858 | -2315.5743 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.73 | 3278.1195 | 3278.1195 | 3278.1195 | 3235.4075 | 2393.0273 | 2393.0273 | -2393.0273 | -2361.8475 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.74 | 3295.981 | 3295.981 | 3295.981 | 3254.7396 | 2439.0259 | 2439.0259 | -2439.0259 | -2408.5073 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.75 | 3313.8425 | 3313.8425 | 3313.8425 | 3274.0716 | 2485.3818 | 2485.3818 | -2485.3818 | -2455.5537 | 2172.0027 | -2172.0027 | 2172.0027 | -2165.5948
0.76 | 3331.7039 | 3331.7039 | 3331.7039 | 3293.4037 | 2532.095 | 2532.095 | -2532.095 | -2502.9868 | 2165.3512 | -2165.3512 | 2165.3512 | -2140.459
0.77 | 3349.5654 | 3349.5654 | 3349.5654 | 3312.7357 | 2579.1653 | 2579.1653 | -2579.1653 | -2550.8065 | 2137.1697 | -2137.1697 | 2137.1697 | -2113.6708
0.78 | 3367.4268 | 3367.4268 | 3367.4268 | 3327.4143 | 2626.5929 | 2626.5929 | -2626.5929 | -2595.3832 | 2107.2667 | -2107.2667 | 2107.2667 | -2082.2277
0.79 | 3385.2883 | 3385.2883 | 3385.2883 | 3334.487 | 2674.3778 | 2674.3778 | -2674.3778 | -2634.2447 | 2075.5434 | -2075.5434 | 2075.5434 | -2044.3968
0.8 | 3403.1498 | 3403.1498 | 3403.1498 | 3341.5597 | 2722.5198 | 2722.5198 | -2722.5198 | -2673.2477 | 2041.8899 | -2041.8899 | 2041.8899 | -2004.9358
0.81 | 3403.1498 | 3403.1498 | 3403.1498 | 3347.2864 | 2756.5513 | 2756.5513 | -2756.5513 | -2711.302 | 1995.7087 | -1995.7087 | 1995.7087 | -1962.9487
0.82 | 3403.1498 | 3403.1498 | 3403.1498 | 3353.0131 | 2790.5828 | 2790.5828 | -2790.5828 | -2749.4707 | 1947.8388 | -1947.8388 | 1947.8388 | -1919.1424
0.83 | 3403.1498 | 3403.1498 | 3403.1498 | 3358.7397 | 2824.6143 | 2824.6143 | -2824.6143 | -2787.754 | 1898.1523 | -1898.1523 | 1898.1523 | -1873.3821
0.84 | 3403.1498 | 3403.1498 | 3403.1498 | 3364.4664 | 2858.6458 | 2858.6458 | -2858.6458 | -2826.1518 | 1846.5028 | -1846.5028 | 1846.5028 | -1825.5137
0.85 | 3403.1498 | 3403.1498 | 3403.1498 | 3370.1931 | 2892.6773 | 2892.6773 | -2892.6773 | -2864.6641 | 1792.7204 | -1792.7204 | 1792.7204 | -1775.3594
0.86 | 3403.1498 | 3403.1498 | 3403.1498 | 3375.9198 | 2926.7088 | 2926.7088 | -2926.7088 | -2903.291 | 1736.607 | -1736.607 | 1736.607 | -1722.7117
0.87 | 3403.1498 | 3403.1498 | 3403.1498 | 3381.6465 | 2960.7403 | 2960.7403 | -2960.7403 | -2942.0324 | 1677.9288 | -1677.9288 | 1677.9288 | -1667.3266
0.88 | 3403.1498 | 3403.1498 | 3403.1498 | 3387.3732 | 2994.7718 | 2994.7718 | -2994.7718 | -2980.8884 | 1616.4066 | -1616.4066 | 1616.4066 | -1608.9131
0.89 | 3403.1498 | 3403.1498 | 3403.1498 | 3393.0999 | 3028.8033 | 3028.8033 | -3028.8033 | -3019.8589 | 1551.7019 | -1551.7019 | 1551.7019 | -1547.1196
0.9 | 3403.1498 | 3403.1498 | 3403.1498 | 3398.8265 | 3062.8348 | 3062.8348 | -3062.8348 | -3058.9439 | 1483.3986 | -1483.3986 | 1483.3986 | -1481.5141
0.91 | 3403.1498 | 3403.1498 | 3403.1498 | 3403.1498 | 3096.8663 | 3096.8663 | -3096.8663 | -3096.8663 | 1410.974 | -1410.974 | 1410.974 | -1410.974
0.92 | 3403.1498 | 3403.1498 | 3403.1498 | 3403.1498 | 3130.8978 | 3130.8978 | -3130.8978 | -3130.8978 | 1333.7569 | -1333.7569 | 1333.7569 | -1333.7569
0.93 | 3403.1498 | 3403.1498 | 3403.1498 | 3403.1498 | 3164.9293 | 3164.9293 | -3164.9293 | -3164.9293 | 1250.8601 | -1250.8601 | 1250.8601 | -1250.8601
0.94 | 3403.1498 | 3403.1498 | 3403.1498 | 3403.1498 | 3198.9608 | 3198.9608 | -3198.9608 | -3198.9608 | 1161.0677 | -1161.0677 | 1161.0677 | -1161.0677
0.95 | 3403.1498 | 3403.1498 | 3403.1498 | 3403.1498 | 3232.9923 | 3232.9923 | -3232.9923 | -3232.9923 | 1062.6332 | -1062.6332 | 1062.6332 | -1062.6332
0.96 | 3402.5198 | 3402.5198 | 3402.5198 | 3402.5198 | 3266.419 | 3266.419 | -3266.419 | -3266.419 | 952.7055 | -952.7055 | 952.7055 | -952.7055
0.97 | 3401.8899 | 3401.8899 | 3401.8899 | 3401.8899 | 3299.8332 | 3299.8332 | -3299.8332 | -3299.8332 | 827.0161 | -827.0161 | 827.0161 | -827.0161
0.98 | 3401.2599 | 3401.2599 | 3401.2599 | 3401.2599 | 3333.2347 | 3333.2347 | -3333.2347 | -3333.2347 | 676.8422 | -676.8422 | 676.8422 | -676.8422
0.99 | 3400.63 | 3400.63 | 3400.63 | 3400.63 | 3366.6237 | 3366.6237 | -3366.6237 | -3366.6237 | 479.7179 | -479.7179 | 479.7179 | -479.7179
1 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | -3400 | -3400 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_50C_0.9pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 50 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1490 |  | VDC
Nom. Battery Voltage** |  |  |  | 1291.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1159 |  | VDC |  | Please select:
AC Voltage |  |  |  | 0.9 |  | pu |  | Project plant specific |  |  | VArRtg: | 2172 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP @50°C, 1159Vdc min. battery voltage and 0.9pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 1954.8019 | 1954.8019 | 1954.8019 | 1954.8016 | 0 | 0 | 0 | 0 | 1954.8019 | -1954.8019 | 1954.8019 | -1954.8016
0.01 | 1954.8019 | 1954.8019 | 1954.8019 | 1954.8016 | 0.019548 | 0.019548 | -0.019548 | -0.019548 | 1954.8019 | -1954.8019 | 1954.8019 | -1954.8016
0.05 | 1964.5427 | 1964.1001 | 1964.5427 | 1962.6657 | 98.2271 | 98.205 | -98.2271 | -98.1333 | 1954.8019 | -1954.8019 | 1954.8019 | -1954.8019
0.1 | 1974.2853 | 1973.4003 | 1974.2853 | 1970.5313 | 197.4285 | 197.34 | -197.4285 | -197.0531 | 1954.8019 | -1954.8019 | 1954.8019 | -1954.8019
0.15 | 2002.9528 | 2002.045 | 2002.9528 | 1992.8506 | 300.4429 | 300.3068 | -300.4429 | -298.9276 | 1954.8019 | -1954.8019 | 1954.8019 | -1954.8019
0.2 | 2031.6203 | 2030.6897 | 2031.6203 | 2015.17 | 406.3241 | 406.1379 | -406.3241 | -403.034 | 1954.8019 | -1954.8019 | 1954.8019 | -1954.8019
0.25 | 2077.681 | 2077.2157 | 2077.681 | 2050.3187 | 519.4203 | 519.3039 | -519.4203 | -512.5797 | 1954.8019 | -1954.8019 | 1954.8019 | -1954.8019
0.3 | 2123.7417 | 2123.7417 | 2123.7417 | 2085.4674 | 637.1225 | 637.1225 | -637.1225 | -625.6402 | 1954.8019 | -1954.8019 | 1954.8019 | -1954.8019
0.35 | 2185.0578 | 2185.0578 | 2185.0578 | 2131.784 | 764.7702 | 764.7702 | -764.7702 | -746.1244 | 1954.8019 | -1954.8019 | 1954.8019 | -1954.8019
0.4 | 2246.3738 | 2246.3738 | 2246.3738 | 2178.1006 | 898.5495 | 898.5495 | -898.5495 | -871.2403 | 1954.8019 | -1954.8019 | 1954.8019 | -1954.8019
0.45 | 2320.604 | 2320.604 | 2318.255 | 2233.6276 | 1044.2718 | 1044.2718 | -1043.2147 | -1005.1324 | 1954.8019 | -1954.8019 | 1954.8019 | -1954.8019
0.5 | 2394.8342 | 2394.8342 | 2390.1361 | 2289.1545 | 1197.4171 | 1197.4171 | -1195.0681 | -1144.5773 | 1954.8019 | -1954.8019 | 1954.8019 | -1954.8019
0.51 | 2411.815 | 2411.815 | 2406.1565 | 2299.3486 | 1230.0256 | 1230.0256 | -1227.1398 | -1172.6678 | 1954.8019 | -1954.8019 | 1954.8019 | -1954.8019
0.52 | 2428.7957 | 2428.7957 | 2422.1769 | 2309.5426 | 1262.9738 | 1262.9738 | -1259.532 | -1200.9622 | 1954.8019 | -1954.8019 | 1954.8019 | -1954.8019
0.53 | 2445.7764 | 2445.7764 | 2438.1973 | 2319.7367 | 1296.2615 | 1296.2615 | -1292.2446 | -1229.4604 | 1954.8019 | -1954.8019 | 1954.8019 | -1954.8019
0.54 | 2462.7571 | 2462.7571 | 2454.2176 | 2329.9307 | 1329.8889 | 1329.8889 | -1325.2775 | -1258.1626 | 1954.8019 | -1954.8019 | 1954.8019 | -1954.8019
0.55 | 2479.7379 | 2479.7379 | 2470.238 | 2340.1248 | 1363.8558 | 1363.8558 | -1358.6309 | -1287.0686 | 1954.8019 | -1954.8019 | 1954.8019 | -1954.3895
0.56 | 2496.7186 | 2496.7186 | 2486.2584 | 2350.3188 | 1398.1624 | 1398.1624 | -1392.3047 | -1316.1785 | 1954.8019 | -1954.8019 | 1954.8019 | -1947.2217
0.57 | 2513.6993 | 2513.6993 | 2502.2788 | 2360.5128 | 1432.8086 | 1432.8086 | -1426.2989 | -1345.4923 | 1954.8019 | -1954.8019 | 1954.8019 | -1939.5028
0.58 | 2530.68 | 2530.68 | 2518.2992 | 2370.7069 | 1467.7944 | 1467.7944 | -1460.6135 | -1375.01 | 1954.8019 | -1954.8019 | 1954.8019 | -1931.2169
0.59 | 2547.6607 | 2547.6607 | 2534.3195 | 2380.9009 | 1503.1198 | 1503.1198 | -1495.2485 | -1404.7315 | 1954.8019 | -1954.8019 | 1954.8019 | -1922.3471
0.6 | 2564.6415 | 2564.6415 | 2550.3399 | 2391.095 | 1538.7849 | 1538.7849 | -1530.204 | -1434.657 | 1954.8019 | -1954.8019 | 1954.8019 | -1912.876
0.61 | 2583.362 | 2583.362 | 2564.7441 | 2393.1574 | 1575.8508 | 1575.8508 | -1564.4939 | -1459.826 | 1954.8019 | -1954.8019 | 1954.8019 | -1896.3413
0.62 | 2602.0825 | 2602.0825 | 2579.1484 | 2395.2198 | 1613.2911 | 1613.2911 | -1599.072 | -1485.0363 | 1954.8019 | -1954.8019 | 1954.8019 | -1879.2938
0.63 | 2620.803 | 2620.803 | 2593.5526 | 2397.2822 | 1651.1059 | 1651.1059 | -1633.9381 | -1510.2878 | 1954.8019 | -1954.8019 | 1954.8019 | -1861.7177
0.64 | 2639.5235 | 2639.5235 | 2607.9568 | 2399.3446 | 1689.295 | 1689.295 | -1669.0924 | -1535.5805 | 1954.8019 | -1954.8019 | 1954.8019 | -1843.5962
0.65 | 2658.244 | 2658.244 | 2622.361 | 2401.407 | 1727.8586 | 1727.8586 | -1704.5347 | -1560.9146 | 1954.8019 | -1954.8019 | 1954.8019 | -1824.9113
0.66 | 2676.9645 | 2676.9645 | 2636.7653 | 2403.4694 | 1766.7966 | 1766.7966 | -1740.2651 | -1586.2898 | 1954.8019 | -1954.8019 | 1954.8019 | -1805.6439
0.67 | 2695.685 | 2695.685 | 2651.1695 | 2405.5318 | 1806.109 | 1806.109 | -1776.2836 | -1611.7063 | 1954.8019 | -1954.8019 | 1954.8019 | -1785.7733
0.68 | 2714.4056 | 2714.4056 | 2665.5737 | 2407.5942 | 1845.7958 | 1845.7958 | -1812.5901 | -1637.1641 | 1954.8019 | -1954.8019 | 1954.4309 | -1765.2773
0.69 | 2733.1261 | 2733.1261 | 2679.9779 | 2409.6566 | 1885.857 | 1885.857 | -1849.1848 | -1662.6631 | 1954.8019 | -1954.8019 | 1939.7931 | -1744.1321
0.7 | 2751.8466 | 2751.8466 | 2694.3822 | 2411.7191 | 1926.2926 | 1926.2926 | -1886.0675 | -1688.2033 | 1954.8019 | -1954.8019 | 1924.1737 | -1722.3119
0.71 | 2753.3558 | 2753.3558 | 2692.1813 | 2414.6313 | 1954.8826 | 1954.8826 | -1911.4487 | -1714.3882 | 1938.9178 | -1938.9178 | 1895.8386 | -1700.3874
0.72 | 2754.8651 | 2754.8651 | 2689.9805 | 2417.5435 | 1983.5029 | 1983.5029 | -1936.7859 | -1740.6314 | 1911.8049 | -1911.8049 | 1866.7767 | -1677.7125
0.73 | 2756.3743 | 2756.3743 | 2687.7796 | 2420.4558 | 2012.1533 | 2012.1533 | -1962.0791 | -1766.9327 | 1883.8362 | -1883.8362 | 1836.9553 | -1654.2536
0.74 | 2757.8836 | 2757.8836 | 2685.5788 | 2423.368 | 2040.8339 | 2040.8339 | -1987.3283 | -1793.2923 | 1854.9715 | -1854.9715 | 1806.3387 | -1629.974
0.75 | 2759.3929 | 2759.3929 | 2683.3779 | 2426.2803 | 2069.5446 | 2069.5446 | -2012.5334 | -1819.7102 | 1825.1668 | -1825.1668 | 1774.8877 | -1604.8336
0.76 | 2760.9021 | 2760.9021 | 2681.1771 | 2429.1925 | 2098.2856 | 2098.2856 | -2037.6946 | -1846.1863 | 1794.374 | -1794.374 | 1742.5588 | -1578.7883
0.77 | 2762.4114 | 2762.4114 | 2678.9762 | 2432.1048 | 2127.0568 | 2127.0568 | -2062.8117 | -1872.7207 | 1762.5397 | -1762.5397 | 1709.3044 | -1551.7896
0.78 | 2763.9206 | 2763.9206 | 2676.7754 | 2435.017 | 2155.8581 | 2155.8581 | -2087.8848 | -1899.3133 | 1729.6049 | -1729.6049 | 1675.0712 | -1523.7838
0.79 | 2765.4299 | 2765.4299 | 2674.5745 | 2437.9293 | 2184.6896 | 2184.6896 | -2112.9139 | -1925.9641 | 1695.504 | -1695.504 | 1639.7999 | -1494.7111
0.8 | 2766.9391 | 2766.9391 | 2672.3737 | 2440.8415 | 2213.5513 | 2213.5513 | -2137.8989 | -1952.6732 | 1660.1635 | -1660.1635 | 1603.4242 | -1464.5049
0.81 | 2766.9391 | 2766.9391 | 2668.7308 | 2445.3612 | 2241.2207 | 2241.2207 | -2161.672 | -1980.7426 | 1622.6158 | -1622.6158 | 1565.0235 | -1434.0329
0.82 | 2766.9391 | 2766.9391 | 2665.088 | 2449.881 | 2268.8901 | 2268.8901 | -2185.3722 | -2008.9024 | 1583.695 | -1583.695 | 1525.3992 | -1402.2225
0.83 | 2766.9391 | 2766.9391 | 2661.4452 | 2454.4007 | 2296.5595 | 2296.5595 | -2208.9995 | -2037.1526 | 1543.2974 | -1543.2974 | 1484.4567 | -1368.9749
0.84 | 2766.9391 | 2766.9391 | 2657.8024 | 2458.9204 | 2324.2289 | 2324.2289 | -2232.554 | -2065.4932 | 1501.3035 | -1501.3035 | 1442.0874 | -1334.1768
0.85 | 2766.9391 | 2766.9391 | 2654.1596 | 2463.4402 | 2351.8983 | 2351.8983 | -2256.0356 | -2093.9241 | 1457.5756 | -1457.5756 | 1398.1653 | -1297.6976
0.86 | 2766.9391 | 2766.9391 | 2650.5167 | 2467.9599 | 2379.5677 | 2379.5677 | -2279.4444 | -2122.4455 | 1411.9525 | -1411.9525 | 1352.5429 | -1259.3852
0.87 | 2766.9391 | 2766.9391 | 2646.8739 | 2472.4796 | 2407.237 | 2407.237 | -2302.7803 | -2151.0573 | 1364.2441 | -1364.2441 | 1305.0457 | -1219.0603
0.88 | 2766.9391 | 2766.9391 | 2643.2311 | 2476.9993 | 2434.9064 | 2434.9064 | -2326.0434 | -2179.7594 | 1314.2233 | -1314.2233 | 1255.4652 | -1176.5095
0.89 | 2766.9391 | 2766.9391 | 2639.5883 | 2481.5191 | 2462.5758 | 2462.5758 | -2349.2336 | -2208.552 | 1261.615 | -1261.615 | 1203.5481 | -1131.4747
0.9 | 2766.9391 | 2766.9391 | 2635.9455 | 2486.0388 | 2490.2452 | 2490.2452 | -2372.3509 | -2237.4349 | 1206.0808 | -1206.0808 | 1148.982 | -1083.6392
0.91 | 2766.9391 | 2766.9391 | 2629.7446 | 2492.048 | 2517.9146 | 2517.9146 | -2393.0676 | -2267.7637 | 1147.1958 | -1147.1958 | 1090.3138 | -1033.2237
0.92 | 2766.9391 | 2766.9391 | 2623.5437 | 2498.0572 | 2545.584 | 2545.584 | -2413.6602 | -2298.2126 | 1084.4142 | -1084.4142 | 1028.2149 | -979.0345
0.93 | 2766.9391 | 2766.9391 | 2617.3428 | 2504.0664 | 2573.2534 | 2573.2534 | -2434.1288 | -2328.7817 | 1017.0148 | -1017.0148 | 962.0293 | -920.3934
0.94 | 2766.9391 | 2766.9391 | 2611.1419 | 2510.0756 | 2600.9228 | 2600.9228 | -2454.4734 | -2359.4711 | 944.0089 | -944.0089 | 890.8549 | -856.3736
0.95 | 2766.9391 | 2766.9391 | 2604.941 | 2516.0848 | 2628.5922 | 2628.5922 | -2474.6939 | -2390.2806 | 863.9765 | -863.9765 | 813.3926 | -785.6472
0.96 | 2766.9488 | 2766.9488 | 2597.9281 | 2526.8431 | 2656.2708 | 2656.2708 | -2494.0109 | -2425.7694 | 774.7457 | -774.7457 | 727.4199 | -707.5161
0.97 | 2766.9584 | 2766.9584 | 2590.9151 | 2537.6014 | 2683.9497 | 2683.9497 | -2513.1877 | -2461.4734 | 672.6612 | -672.6612 | 629.8642 | -616.9034
0.98 | 2766.9681 | 2766.9681 | 2583.9022 | 2548.3597 | 2711.6287 | 2711.6287 | -2532.2241 | -2497.3925 | 550.6197 | -550.6197 | 514.19 | -507.1172
0.99 | 2766.9777 | 2766.9777 | 2576.8893 | 2559.118 | 2739.3079 | 2739.3079 | -2551.1204 | -2533.5268 | 390.3302 | -390.3302 | 363.515 | -361.008
1 | 2766.9874 | 2766.9874 | 2569.8763 | 2569.8763 | 2766.9874 | 2766.9874 | -2569.8763 | -2569.8763 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_50C_1.0pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 50 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1490 |  | VDC
Nom. Battery Voltage** |  |  |  | 1291.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1159 |  | VDC |  | Please select:
AC Voltage |  |  |  | 1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2172 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP @50°C, 1159Vdc min. battery voltage and 1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2172.0022 | 2172.0021 | 2172.0022 | 2172.0017 | 0 | 0 | 0 | 0 | 2172.0022 | -2172.0021 | 2172.0022 | -2172.0017
0.01 | 2172.0022 | 2172.0021 | 2172.0022 | 2172.0017 | 0.02172 | 0.02172 | -0.02172 | -0.02172 | 2172.0022 | -2172.0021 | 2172.0022 | -2172.0017
0.05 | 2182.8252 | 2182.3335 | 2182.8252 | 2180.7396 | 109.1413 | 109.1167 | -109.1413 | -109.037 | 2172.0022 | -2172.0021 | 2172.0022 | -2172.0021
0.1 | 2193.6504 | 2192.667 | 2193.6504 | 2189.4792 | 219.365 | 219.2667 | -219.365 | -218.9479 | 2172.0022 | -2172.0021 | 2172.0022 | -2172.0021
0.15 | 2225.5031 | 2224.4945 | 2225.5031 | 2214.2785 | 333.8255 | 333.6742 | -333.8255 | -332.1418 | 2172.0022 | -2172.0021 | 2172.0022 | -2172.0021
0.2 | 2257.3559 | 2256.3219 | 2257.3559 | 2239.0777 | 451.4712 | 451.2644 | -451.4712 | -447.8155 | 2172.0022 | -2172.0021 | 2172.0022 | -2172.0021
0.25 | 2308.5344 | 2308.0175 | 2308.5344 | 2278.1319 | 577.1336 | 577.0044 | -577.1336 | -569.533 | 2172.0022 | -2172.0021 | 2172.0022 | -2172.0021
0.3 | 2359.713 | 2359.713 | 2359.713 | 2317.186 | 707.9139 | 707.9139 | -707.9139 | -695.1558 | 2172.0022 | -2172.0021 | 2172.0022 | -2172.0021
0.35 | 2427.842 | 2427.842 | 2427.842 | 2368.6489 | 849.7447 | 849.7447 | -849.7447 | -829.0271 | 2172.0022 | -2172.0021 | 2172.0022 | -2172.0021
0.4 | 2495.9709 | 2495.9709 | 2495.9709 | 2420.1118 | 998.3884 | 998.3884 | -998.3884 | -968.0447 | 2172.0022 | -2172.0021 | 2172.0022 | -2172.0021
0.45 | 2578.4489 | 2578.4489 | 2575.8389 | 2481.8084 | 1160.302 | 1160.302 | -1159.1275 | -1116.8138 | 2172.0022 | -2172.0021 | 2172.0022 | -2172.0021
0.5 | 2660.9269 | 2660.9269 | 2655.7068 | 2543.505 | 1330.4635 | 1330.4635 | -1327.8534 | -1271.7525 | 2172.0022 | -2172.0021 | 2172.0022 | -2172.0021
0.51 | 2679.7944 | 2679.7944 | 2673.5072 | 2554.8318 | 1366.6951 | 1366.6951 | -1363.4887 | -1302.9642 | 2172.0022 | -2172.0021 | 2172.0022 | -2172.0021
0.52 | 2698.6619 | 2698.6619 | 2691.3077 | 2566.1585 | 1403.3042 | 1403.3042 | -1399.48 | -1334.4024 | 2172.0022 | -2172.0021 | 2172.0022 | -2172.0021
0.53 | 2717.5293 | 2717.5293 | 2709.1081 | 2577.4852 | 1440.2906 | 1440.2906 | -1435.8273 | -1366.0671 | 2172.0022 | -2172.0021 | 2172.0022 | -2172.0021
0.54 | 2736.3968 | 2736.3968 | 2726.9085 | 2588.8119 | 1477.6543 | 1477.6543 | -1472.5306 | -1397.9584 | 2172.0022 | -2172.0021 | 2172.0022 | -2172.0021
0.55 | 2755.2643 | 2755.2643 | 2744.7089 | 2600.1386 | 1515.3954 | 1515.3954 | -1509.5899 | -1430.0762 | 2172.0022 | -2172.0021 | 2172.0022 | -2171.5439
0.56 | 2774.1317 | 2774.1317 | 2762.5093 | 2611.4653 | 1553.5138 | 1553.5138 | -1547.0052 | -1462.4206 | 2172.0022 | -2172.0021 | 2172.0022 | -2163.5797
0.57 | 2792.9992 | 2792.9992 | 2780.3098 | 2622.792 | 1592.0096 | 1592.0096 | -1584.7766 | -1494.9915 | 2172.0022 | -2172.0021 | 2172.0022 | -2155.0032
0.58 | 2811.8667 | 2811.8667 | 2798.1102 | 2634.1188 | 1630.8827 | 1630.8827 | -1622.9039 | -1527.7889 | 2172.0022 | -2172.0021 | 2172.0022 | -2145.7965
0.59 | 2830.7342 | 2830.7342 | 2815.9106 | 2645.4455 | 1670.1332 | 1670.1332 | -1661.3873 | -1560.8128 | 2172.0022 | -2172.0021 | 2172.0022 | -2135.9413
0.6 | 2849.6016 | 2849.6016 | 2833.711 | 2656.7722 | 1709.761 | 1709.761 | -1700.2266 | -1594.0633 | 2172.0022 | -2172.0021 | 2172.0022 | -2125.4177
0.61 | 2870.4022 | 2870.4022 | 2849.7157 | 2659.0637 | 1750.9453 | 1750.9453 | -1738.3266 | -1622.0289 | 2172.0022 | -2172.0021 | 2172.0022 | -2107.0459
0.62 | 2891.2028 | 2891.2028 | 2865.7204 | 2661.3553 | 1792.5457 | 1792.5457 | -1776.7467 | -1650.0403 | 2172.0022 | -2172.0021 | 2172.0022 | -2088.1042
0.63 | 2912.0033 | 2912.0033 | 2881.7251 | 2663.6469 | 1834.5621 | 1834.5621 | -1815.4868 | -1678.0975 | 2172.0022 | -2172.0021 | 2172.0022 | -2068.5752
0.64 | 2932.8039 | 2932.8039 | 2897.7298 | 2665.9384 | 1876.9945 | 1876.9945 | -1854.5471 | -1706.2006 | 2172.0022 | -2172.0021 | 2172.0022 | -2048.4402
0.65 | 2953.6045 | 2953.6045 | 2913.7345 | 2668.23 | 1919.8429 | 1919.8429 | -1893.9274 | -1734.3495 | 2172.0022 | -2172.0021 | 2172.0022 | -2027.6793
0.66 | 2974.405 | 2974.405 | 2929.7392 | 2670.5216 | 1963.1073 | 1963.1073 | -1933.6279 | -1762.5442 | 2172.0022 | -2172.0021 | 2172.0022 | -2006.271
0.67 | 2995.2056 | 2995.2056 | 2945.7439 | 2672.8131 | 2006.7878 | 2006.7878 | -1973.6484 | -1790.7848 | 2172.0022 | -2172.0021 | 2172.0022 | -1984.1925
0.68 | 3016.0062 | 3016.0062 | 2961.7486 | 2675.1047 | 2050.8842 | 2050.8842 | -2013.989 | -1819.0712 | 2172.0022 | -2172.0021 | 2171.5899 | -1961.4192
0.69 | 3036.8067 | 3036.8067 | 2977.7533 | 2677.3963 | 2095.3967 | 2095.3967 | -2054.6498 | -1847.4034 | 2172.0022 | -2172.0021 | 2155.3257 | -1937.9245
0.7 | 3057.6073 | 3057.6073 | 2993.758 | 2679.6878 | 2140.3251 | 2140.3251 | -2095.6306 | -1875.7815 | 2172.0022 | -2172.0021 | 2137.9708 | -1913.6799
0.71 | 3059.2843 | 3059.2843 | 2991.3126 | 2682.9237 | 2172.0918 | 2172.0918 | -2123.8319 | -1904.8758 | 2154.3531 | -2154.3531 | 2106.4873 | -1889.3193
0.72 | 3060.9612 | 3060.9612 | 2988.8672 | 2686.1595 | 2203.8921 | 2203.8921 | -2151.9844 | -1934.0348 | 2124.2277 | -2124.2277 | 2074.1963 | -1864.125
0.73 | 3062.6382 | 3062.6382 | 2986.4218 | 2689.3953 | 2235.7259 | 2235.7259 | -2180.0879 | -1963.2586 | 2093.1513 | -2093.1513 | 2041.0614 | -1838.0596
0.74 | 3064.3151 | 3064.3151 | 2983.9764 | 2692.6312 | 2267.5932 | 2267.5932 | -2208.1425 | -1992.5471 | 2061.0794 | -2061.0794 | 2007.043 | -1811.0822
0.75 | 3065.9921 | 3065.9921 | 2981.531 | 2695.867 | 2299.494 | 2299.494 | -2236.1483 | -2021.9002 | 2027.9631 | -2027.9631 | 1972.0974 | -1783.1484
0.76 | 3067.669 | 3067.669 | 2979.0856 | 2699.1028 | 2331.4284 | 2331.4284 | -2264.1051 | -2051.3181 | 1993.7489 | -1993.7489 | 1936.1765 | -1754.2092
0.77 | 3069.346 | 3069.346 | 2976.6402 | 2702.3386 | 2363.3964 | 2363.3964 | -2292.013 | -2080.8008 | 1958.3774 | -1958.3774 | 1899.2271 | -1724.2106
0.78 | 3071.0229 | 3071.0229 | 2974.1948 | 2705.5745 | 2395.3979 | 2395.3979 | -2319.872 | -2110.3481 | 1921.7832 | -1921.7832 | 1861.1902 | -1693.0931
0.79 | 3072.6999 | 3072.6999 | 2971.7494 | 2708.8103 | 2427.4329 | 2427.4329 | -2347.6821 | -2139.9601 | 1883.8933 | -1883.8933 | 1821.9999 | -1660.7901
0.8 | 3074.3768 | 3074.3768 | 2969.3041 | 2712.0461 | 2459.5014 | 2459.5014 | -2375.4432 | -2169.6369 | 1844.6261 | -1844.6261 | 1781.5824 | -1627.2277
0.81 | 3074.3768 | 3074.3768 | 2965.2565 | 2717.068 | 2490.2452 | 2490.2452 | -2401.8578 | -2200.8251 | 1802.9064 | -1802.9064 | 1738.915 | -1593.3699
0.82 | 3074.3768 | 3074.3768 | 2961.2089 | 2722.09 | 2520.989 | 2520.989 | -2428.1913 | -2232.1138 | 1759.6611 | -1759.6611 | 1694.888 | -1558.025
0.83 | 3074.3768 | 3074.3768 | 2957.1613 | 2727.1119 | 2551.7328 | 2551.7328 | -2454.4439 | -2263.5029 | 1714.7748 | -1714.7748 | 1649.3963 | -1521.0832
0.84 | 3074.3768 | 3074.3768 | 2953.1138 | 2732.1338 | 2582.4765 | 2582.4765 | -2480.6156 | -2294.9924 | 1668.115 | -1668.115 | 1602.3194 | -1482.4186
0.85 | 3074.3768 | 3074.3768 | 2949.0662 | 2737.1557 | 2613.2203 | 2613.2203 | -2506.7063 | -2326.5824 | 1619.5285 | -1619.5285 | 1553.517 | -1441.8862
0.86 | 3074.3768 | 3074.3768 | 2945.0186 | 2742.1776 | 2643.9641 | 2643.9641 | -2532.716 | -2358.2728 | 1568.8361 | -1568.8361 | 1502.8254 | -1399.3169
0.87 | 3074.3768 | 3074.3768 | 2940.971 | 2747.1996 | 2674.7078 | 2674.7078 | -2558.6448 | -2390.0636 | 1515.8268 | -1515.8268 | 1450.0508 | -1354.5115
0.88 | 3074.3768 | 3074.3768 | 2936.9235 | 2752.2215 | 2705.4516 | 2705.4516 | -2584.4926 | -2421.9549 | 1460.2481 | -1460.2481 | 1394.9614 | -1307.2328
0.89 | 3074.3768 | 3074.3768 | 2932.8759 | 2757.2434 | 2736.1954 | 2736.1954 | -2610.2595 | -2453.9466 | 1401.7945 | -1401.7945 | 1337.2756 | -1257.1941
0.9 | 3074.3768 | 3074.3768 | 2928.8283 | 2762.2653 | 2766.9391 | 2766.9391 | -2635.9455 | -2486.0388 | 1340.0898 | -1340.0898 | 1276.6467 | -1204.0435
0.91 | 3074.3768 | 3074.3768 | 2921.9384 | 2768.9422 | 2797.6829 | 2797.6829 | -2658.964 | -2519.7374 | 1274.662 | -1274.662 | 1211.4598 | -1148.0263
0.92 | 3074.3768 | 3074.3768 | 2915.0485 | 2775.6191 | 2828.4267 | 2828.4267 | -2681.8447 | -2553.5696 | 1204.9047 | -1204.9047 | 1142.461 | -1087.8161
0.93 | 3074.3768 | 3074.3768 | 2908.1586 | 2782.296 | 2859.1704 | 2859.1704 | -2704.5875 | -2587.5353 | 1130.0165 | -1130.0165 | 1068.9214 | -1022.6594
0.94 | 3074.3768 | 3074.3768 | 2901.2688 | 2788.9729 | 2889.9142 | 2889.9142 | -2727.1926 | -2621.6345 | 1048.8988 | -1048.8988 | 989.8388 | -951.5263
0.95 | 3074.3768 | 3074.3768 | 2894.3789 | 2795.6498 | 2920.658 | 2920.658 | -2749.6599 | -2655.8673 | 959.9739 | -959.9739 | 903.7695 | -872.9414
0.96 | 3074.3875 | 3074.3875 | 2886.5867 | 2807.6034 | 2951.412 | 2951.412 | -2771.1233 | -2695.2993 | 860.8285 | -860.8285 | 808.2443 | -786.129
0.97 | 3074.3982 | 3074.3982 | 2878.7946 | 2819.5571 | 2982.1663 | 2982.1663 | -2792.4307 | -2734.9704 | 747.4013 | -747.4013 | 699.8491 | -685.4482
0.98 | 3074.409 | 3074.409 | 2871.0024 | 2831.5108 | 3012.9208 | 3012.9208 | -2813.5824 | -2774.8806 | 611.7997 | -611.7997 | 571.3223 | -563.4635
0.99 | 3074.4197 | 3074.4197 | 2863.2103 | 2843.4645 | 3043.6755 | 3043.6755 | -2834.5782 | -2815.0298 | 433.7003 | -433.7003 | 403.9055 | -401.12
1 | 3074.4304 | 3074.4304 | 2855.4181 | 2855.4181 | 3074.4304 | 3074.4304 | -2855.4181 | -2855.4181 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_50C_1.1pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 50 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1490 |  | VDC
Nom. Battery Voltage** |  |  |  | 1291.4 |  | VDC
Min. Battery Voltage*** |  |  |  | 1159 |  | VDC |  | Please select:
AC Voltage |  |  |  | 1.1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2172 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP @50°C, 1159Vdc min. battery voltage and 1.1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2172.0022 | 2172.0022 | 2172.0022 | 2172.0021 | 0 | 0 | 0 | 0 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0021
0.01 | 2172.0022 | 2172.0022 | 2172.0022 | 2172.0021 | 0.02172 | 0.02172 | -0.02172 | -0.02172 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0021
0.05 | 2182.8252 | 2182.8252 | 2182.8252 | 2182.706 | 109.1413 | 109.1413 | -109.1413 | -109.1353 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.1 | 2193.6504 | 2193.6504 | 2193.6504 | 2193.412 | 219.365 | 219.365 | -219.365 | -219.3412 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.15 | 2225.5031 | 2225.5031 | 2225.5031 | 2223.479 | 333.8255 | 333.8255 | -333.8255 | -333.5218 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.2 | 2257.3559 | 2257.3559 | 2257.3559 | 2253.546 | 451.4712 | 451.4712 | -451.4712 | -450.7092 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.25 | 2308.5344 | 2308.5344 | 2308.5344 | 2301.1058 | 577.1336 | 577.1336 | -577.1336 | -575.2764 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.3 | 2359.713 | 2359.713 | 2359.713 | 2348.6655 | 707.9139 | 707.9139 | -707.9139 | -704.5997 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.35 | 2427.842 | 2427.842 | 2427.842 | 2411.0079 | 849.7447 | 849.7447 | -849.7447 | -843.8528 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.4 | 2495.9709 | 2495.9709 | 2495.9709 | 2473.3503 | 998.3884 | 998.3884 | -998.3884 | -989.3401 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.45 | 2578.4489 | 2578.4489 | 2578.4489 | 2545.1097 | 1160.302 | 1160.302 | -1160.302 | -1145.2994 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.5 | 2660.9269 | 2660.9269 | 2660.9269 | 2616.8692 | 1330.4635 | 1330.4635 | -1330.4635 | -1308.4346 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.51 | 2679.7944 | 2679.7944 | 2679.7944 | 2635.4512 | 1366.6951 | 1366.6951 | -1366.6951 | -1344.0801 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.52 | 2698.6619 | 2698.6619 | 2698.6619 | 2654.0332 | 1403.3042 | 1403.3042 | -1403.3042 | -1380.0972 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.53 | 2717.5293 | 2717.5293 | 2717.5293 | 2672.6152 | 1440.2906 | 1440.2906 | -1440.2906 | -1416.486 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.54 | 2736.3968 | 2736.3968 | 2736.3968 | 2691.1972 | 1477.6543 | 1477.6543 | -1477.6543 | -1453.2465 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.55 | 2755.2643 | 2755.2643 | 2755.2643 | 2709.7792 | 1515.3954 | 1515.3954 | -1515.3954 | -1490.3785 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.56 | 2774.1317 | 2774.1317 | 2774.1317 | 2728.3612 | 1553.5138 | 1553.5138 | -1553.5138 | -1527.8823 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.57 | 2792.9992 | 2792.9992 | 2792.9992 | 2746.9432 | 1592.0096 | 1592.0096 | -1592.0096 | -1565.7576 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.58 | 2811.8667 | 2811.8667 | 2811.8667 | 2765.5252 | 1630.8827 | 1630.8827 | -1630.8827 | -1604.0046 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.59 | 2830.7342 | 2830.7342 | 2830.7342 | 2784.1072 | 1670.1332 | 1670.1332 | -1670.1332 | -1642.6232 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.6 | 2849.6016 | 2849.6016 | 2849.6016 | 2802.6892 | 1709.761 | 1709.761 | -1709.761 | -1681.6135 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.61 | 2870.4022 | 2870.4022 | 2870.4022 | 2820.085 | 1750.9453 | 1750.9453 | -1750.9453 | -1720.2519 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.62 | 2891.2028 | 2891.2028 | 2891.2028 | 2837.4809 | 1792.5457 | 1792.5457 | -1792.5457 | -1759.2381 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.63 | 2912.0033 | 2912.0033 | 2912.0033 | 2854.8767 | 1834.5621 | 1834.5621 | -1834.5621 | -1798.5723 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.64 | 2932.8039 | 2932.8039 | 2932.8039 | 2872.2726 | 1876.9945 | 1876.9945 | -1876.9945 | -1838.2545 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.65 | 2953.6045 | 2953.6045 | 2953.6045 | 2889.6684 | 1919.8429 | 1919.8429 | -1919.8429 | -1878.2845 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.66 | 2974.405 | 2974.405 | 2974.405 | 2907.0643 | 1963.1073 | 1963.1073 | -1963.1073 | -1918.6624 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.67 | 2995.2056 | 2995.2056 | 2995.2056 | 2924.4601 | 2006.7878 | 2006.7878 | -2006.7878 | -1959.3883 | 2172.0022 | -2172.0022 | 2172.0022 | -2171.0054
0.68 | 3016.0062 | 3016.0062 | 3016.0062 | 2941.856 | 2050.8842 | 2050.8842 | -2050.8842 | -2000.4621 | 2172.0022 | -2172.0022 | 2172.0022 | -2157.0044
0.69 | 3036.8067 | 3036.8067 | 3036.8067 | 2945.1359 | 2095.3967 | 2095.3967 | -2095.3967 | -2032.1438 | 2172.0022 | -2172.0022 | 2172.0022 | -2131.717
0.7 | 3057.6073 | 3057.6073 | 3057.6073 | 2947.6566 | 2140.3251 | 2140.3251 | -2140.3251 | -2063.3596 | 2172.0022 | -2172.0022 | 2172.0022 | -2105.0479
0.71 | 3059.2843 | 3059.2843 | 3059.2843 | 2951.216 | 2172.0918 | 2172.0918 | -2172.0918 | -2095.3634 | 2154.3531 | -2154.3531 | 2154.3531 | -2078.2513
0.72 | 3060.9612 | 3060.9612 | 3060.9612 | 2954.7754 | 2203.8921 | 2203.8921 | -2203.8921 | -2127.4383 | 2124.2277 | -2124.2277 | 2124.2277 | -2050.5375
0.73 | 3062.6382 | 3062.6382 | 3062.6382 | 2958.3349 | 2235.7259 | 2235.7259 | -2235.7259 | -2159.5844 | 2093.1513 | -2093.1513 | 2093.1513 | -2021.8655
0.74 | 3064.3151 | 3064.3151 | 3064.3151 | 2961.8943 | 2267.5932 | 2267.5932 | -2267.5932 | -2191.8018 | 2061.0794 | -2061.0794 | 2061.0794 | -1992.1904
0.75 | 3065.9921 | 3065.9921 | 3065.9921 | 2965.4537 | 2299.494 | 2299.494 | -2299.494 | -2224.0903 | 2027.9631 | -2027.9631 | 2027.9631 | -1961.4632
0.76 | 3067.669 | 3067.669 | 3067.669 | 2969.0131 | 2331.4284 | 2331.4284 | -2331.4284 | -2256.4499 | 1993.7489 | -1993.7489 | 1993.7489 | -1929.6301
0.77 | 3069.346 | 3069.346 | 3069.346 | 2972.5725 | 2363.3964 | 2363.3964 | -2363.3964 | -2288.8808 | 1958.3774 | -1958.3774 | 1958.3774 | -1896.6317
0.78 | 3071.0229 | 3071.0229 | 3071.0229 | 2976.1319 | 2395.3979 | 2395.3979 | -2395.3979 | -2321.3829 | 1921.7832 | -1921.7832 | 1921.7832 | -1862.4024
0.79 | 3072.6999 | 3072.6999 | 3072.6999 | 2979.6913 | 2427.4329 | 2427.4329 | -2427.4329 | -2353.9561 | 1883.8933 | -1883.8933 | 1883.8933 | -1826.8691
0.8 | 3074.3768 | 3074.3768 | 3074.3768 | 2983.2507 | 2459.5014 | 2459.5014 | -2459.5014 | -2386.6006 | 1844.6261 | -1844.6261 | 1844.6261 | -1789.9504
0.81 | 3074.3768 | 3074.3768 | 3074.3768 | 2988.7748 | 2490.2452 | 2490.2452 | -2490.2452 | -2420.9076 | 1802.9064 | -1802.9064 | 1802.9064 | -1752.7069
0.82 | 3074.3768 | 3074.3768 | 3074.3768 | 2994.299 | 2520.989 | 2520.989 | -2520.989 | -2455.3251 | 1759.6611 | -1759.6611 | 1759.6611 | -1713.8275
0.83 | 3074.3768 | 3074.3768 | 3074.3768 | 2999.8231 | 2551.7328 | 2551.7328 | -2551.7328 | -2489.8531 | 1714.7748 | -1714.7748 | 1714.7748 | -1673.1915
0.84 | 3074.3768 | 3074.3768 | 3074.3768 | 3005.3472 | 2582.4765 | 2582.4765 | -2582.4765 | -2524.4916 | 1668.115 | -1668.115 | 1668.115 | -1630.6605
0.85 | 3074.3768 | 3074.3768 | 3074.3768 | 3010.8713 | 2613.2203 | 2613.2203 | -2613.2203 | -2559.2406 | 1619.5285 | -1619.5285 | 1619.5285 | -1586.0749
0.86 | 3074.3768 | 3074.3768 | 3074.3768 | 3016.3954 | 2643.9641 | 2643.9641 | -2643.9641 | -2594.1001 | 1568.8361 | -1568.8361 | 1568.8361 | -1539.2486
0.87 | 3074.3768 | 3074.3768 | 3074.3768 | 3021.9195 | 2674.7078 | 2674.7078 | -2674.7078 | -2629.07 | 1515.8268 | -1515.8268 | 1515.8268 | -1489.9626
0.88 | 3074.3768 | 3074.3768 | 3074.3768 | 3027.4436 | 2705.4516 | 2705.4516 | -2705.4516 | -2664.1504 | 1460.2481 | -1460.2481 | 1460.2481 | -1437.9561
0.89 | 3074.3768 | 3074.3768 | 3074.3768 | 3032.9677 | 2736.1954 | 2736.1954 | -2736.1954 | -2699.3413 | 1401.7945 | -1401.7945 | 1401.7945 | -1382.9136
0.9 | 3074.3768 | 3074.3768 | 3074.3768 | 3038.4919 | 2766.9391 | 2766.9391 | -2766.9391 | -2734.6427 | 1340.0898 | -1340.0898 | 1340.0898 | -1324.4479
0.91 | 3074.3768 | 3074.3768 | 3074.3768 | 3045.8364 | 2797.6829 | 2797.6829 | -2797.6829 | -2771.7112 | 1274.662 | -1274.662 | 1274.662 | -1262.8289
0.92 | 3074.3768 | 3074.3768 | 3074.3768 | 3053.181 | 2828.4267 | 2828.4267 | -2828.4267 | -2808.9265 | 1204.9047 | -1204.9047 | 1204.9047 | -1196.5977
0.93 | 3074.3768 | 3074.3768 | 3074.3768 | 3060.5256 | 2859.1704 | 2859.1704 | -2859.1704 | -2846.2888 | 1130.0165 | -1130.0165 | 1130.0165 | -1124.9253
0.94 | 3074.3768 | 3074.3768 | 3074.3768 | 3067.8702 | 2889.9142 | 2889.9142 | -2889.9142 | -2883.798 | 1048.8988 | -1048.8988 | 1048.8988 | -1046.6789
0.95 | 3074.3768 | 3074.3768 | 3074.3768 | 3074.3768 | 2920.658 | 2920.658 | -2920.658 | -2920.658 | 959.9739 | -959.9739 | 959.9739 | -959.9739
0.96 | 3074.5014 | 3074.5014 | 3074.5014 | 3074.5014 | 2951.5214 | 2951.5214 | -2951.5214 | -2951.5214 | 860.8604 | -860.8604 | 860.8604 | -860.8604
0.97 | 3074.6261 | 3074.6261 | 3074.6261 | 3074.6261 | 2982.3873 | 2982.3873 | -2982.3873 | -2982.3873 | 747.4567 | -747.4567 | 747.4567 | -747.4567
0.98 | 3074.7507 | 3074.7507 | 3074.7507 | 3074.7507 | 3013.2557 | 3013.2557 | -3013.2557 | -3013.2557 | 611.8677 | -611.8677 | 611.8677 | -611.8677
0.99 | 3074.8754 | 3074.8754 | 3074.8754 | 3074.8754 | 3044.1266 | 3044.1266 | -3044.1266 | -3044.1266 | 433.7645 | -433.7645 | 433.7645 | -433.7645
1 | 3075 | 3075 | 3075 | 3075 | 3075 | 3075 | -3075 | -3075 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE