## CATL_25C_0.9pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 25 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V) |  |  |  | 1496 |  | VDC
Min. battery voltage |  |  |  | 1164 |  | VDC |  | Please select:
AC voltage |  |  |  | 0.9 |  | pu |  | Project plant specific |  |  | VArRtg: | 2172 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@min battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP @25°C, 1164Vdc min. battery voltage and 0.9pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 1954.8027 | 1954.8024 | 1954.8027 | 1954.8023 | 0 | 0 | 0 | 0 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8023
0.01 | 1954.8027 | 1954.8024 | 1954.8027 | 1954.8023 | 0.019548 | 0.019548 | -0.019548 | -0.019548 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8023
0.05 | 1968.282 | 1966.6535 | 1968.282 | 1966.1358 | 98.4141 | 98.3327 | -98.4141 | -98.3068 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.1 | 1981.764 | 1978.5069 | 1981.764 | 1977.4716 | 198.1764 | 197.8507 | -198.1764 | -197.7472 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.15 | 2021.1521 | 2014.1898 | 2021.1521 | 2009.2744 | 303.1728 | 302.1285 | -303.1728 | -301.3912 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.2 | 2060.5401 | 2049.8727 | 2060.5401 | 2041.0771 | 412.108 | 409.9745 | -412.108 | -408.2154 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.25 | 2123.0365 | 2109.934 | 2123.0365 | 2090.9983 | 530.7591 | 527.4835 | -530.7591 | -522.7496 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.3 | 2185.5328 | 2169.9953 | 2185.5328 | 2140.9195 | 655.6599 | 650.9986 | -655.6599 | -642.2759 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.35 | 2267.455 | 2251.6732 | 2267.455 | 2206.092 | 793.6093 | 788.0856 | -793.6093 | -772.1322 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.4 | 2349.3772 | 2333.3511 | 2349.3772 | 2271.2644 | 939.7509 | 933.3405 | -939.7509 | -908.5058 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.45 | 2446.9783 | 2438.9652 | 2446.9783 | 2348.5837 | 1101.1402 | 1097.5344 | -1101.1402 | -1056.8627 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.5 | 2544.5793 | 2544.5793 | 2544.5793 | 2425.9031 | 1272.2897 | 1272.2897 | -1272.2897 | -1212.9515 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.51 | 2566.5719 | 2566.5719 | 2566.5719 | 2444.4016 | 1308.9517 | 1308.9517 | -1308.9517 | -1246.6448 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.52 | 2588.5644 | 2588.5644 | 2588.5644 | 2462.9002 | 1346.0535 | 1346.0535 | -1346.0535 | -1280.7081 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.53 | 2610.5569 | 2610.5569 | 2610.5569 | 2481.3988 | 1383.5952 | 1383.5952 | -1383.5952 | -1315.1414 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.54 | 2632.5495 | 2632.5495 | 2632.5495 | 2499.8974 | 1421.5767 | 1421.5767 | -1421.5767 | -1349.9446 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.55 | 2654.542 | 2654.542 | 2654.542 | 2518.3959 | 1459.9981 | 1459.9981 | -1459.9981 | -1385.1178 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.56 | 2676.5345 | 2676.5345 | 2676.5345 | 2536.8945 | 1498.8593 | 1498.8593 | -1498.8593 | -1420.6609 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.57 | 2698.5271 | 2698.5271 | 2698.5271 | 2555.3931 | 1538.1604 | 1538.1604 | -1538.1604 | -1456.5741 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.58 | 2720.5196 | 2720.5196 | 2720.5196 | 2573.8917 | 1577.9014 | 1577.9014 | -1577.9014 | -1492.8572 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.59 | 2742.5121 | 2742.5121 | 2742.5121 | 2592.3903 | 1618.0822 | 1618.0822 | -1618.0822 | -1529.5103 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.6 | 2764.5047 | 2764.5047 | 2764.5047 | 2610.8888 | 1658.7028 | 1658.7028 | -1658.7028 | -1566.5333 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.61 | 2788.427 | 2788.427 | 2788.427 | 2631.7315 | 1700.9404 | 1700.9404 | -1700.9404 | -1605.3562 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.62 | 2812.3493 | 2812.3493 | 2812.3493 | 2652.5742 | 1743.6565 | 1743.6565 | -1743.6565 | -1644.596 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.63 | 2836.2715 | 2836.2715 | 2836.2715 | 2673.4169 | 1786.8511 | 1786.8511 | -1786.8511 | -1684.2526 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.64 | 2860.1938 | 2860.1938 | 2860.1938 | 2694.2596 | 1830.5241 | 1830.5241 | -1830.5241 | -1724.3261 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.65 | 2884.1161 | 2884.1161 | 2884.1161 | 2715.1023 | 1874.6755 | 1874.6755 | -1874.6755 | -1764.8165 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.66 | 2908.0384 | 2908.0384 | 2908.0384 | 2735.9449 | 1919.3054 | 1919.3054 | -1919.3054 | -1805.7237 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.67 | 2931.9607 | 2931.9607 | 2931.9607 | 2756.7876 | 1964.4137 | 1964.4137 | -1964.4137 | -1847.0477 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.68 | 2955.883 | 2955.883 | 2955.883 | 2777.6303 | 2010.0004 | 2010.0004 | -2010.0004 | -1888.7886 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.69 | 2979.8053 | 2979.8053 | 2979.8053 | 2798.473 | 2056.0657 | 2056.0657 | -2056.0657 | -1930.9464 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.7 | 3003.7276 | 3003.7276 | 3003.7276 | 2819.3157 | 2102.6093 | 2102.6093 | -2102.6093 | -1973.521 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.71 | 3029.1548 | 3029.1548 | 3024.9395 | 2830.6917 | 2150.6999 | 2150.6999 | -2147.707 | -2009.7911 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.72 | 3054.5821 | 3054.5821 | 3046.1513 | 2842.0678 | 2199.2991 | 2199.2991 | -2193.229 | -2046.2888 | 1954.8027 | -1954.8024 | 1954.8027 | -1954.8024
0.73 | 3080.0093 | 3080.0093 | 3067.3632 | 2853.4439 | 2248.4068 | 2248.4068 | -2239.1752 | -2083.014 | 1954.8027 | -1954.8024 | 1954.8027 | -1950.1781
0.74 | 3105.4366 | 3105.4366 | 3088.5751 | 2864.8199 | 2298.023 | 2298.023 | -2285.5456 | -2119.9668 | 1954.8027 | -1954.8024 | 1954.8027 | -1926.8976
0.75 | 3130.8638 | 3130.8638 | 3109.787 | 2876.196 | 2348.1478 | 2348.1478 | -2332.3402 | -2157.147 | 1954.8027 | -1954.8024 | 1954.8027 | -1902.4248
0.76 | 3156.291 | 3156.291 | 3130.9989 | 2887.5721 | 2398.7812 | 2398.7812 | -2379.5591 | -2194.5548 | 1954.8027 | -1954.8024 | 1954.8027 | -1876.6997
0.77 | 3181.7183 | 3181.7183 | 3152.2107 | 2898.9481 | 2449.9231 | 2449.9231 | -2427.2023 | -2232.1901 | 1954.8027 | -1954.8024 | 1954.8027 | -1849.6561
0.78 | 3207.1455 | 3207.1455 | 3173.4226 | 2910.3242 | 2501.5735 | 2501.5735 | -2475.2696 | -2270.0529 | 1954.8027 | -1954.8024 | 1954.8027 | -1821.2213
0.79 | 3232.5728 | 3232.5728 | 3194.6345 | 2921.7003 | 2553.7325 | 2553.7325 | -2523.7613 | -2308.1432 | 1954.8027 | -1954.8024 | 1954.8027 | -1791.3144
0.8 | 3258 | 3258 | 3215.8464 | 2933.0763 | 2606.4 | 2606.4 | -2572.6771 | -2346.4611 | 1954.8 | -1954.8 | 1929.5078 | -1759.8458
0.81 | 3258 | 3258 | 3211.2034 | 2938.2362 | 2638.98 | 2638.98 | -2601.0748 | -2379.9713 | 1910.5885 | -1910.5885 | 1883.1456 | -1723.0695
0.82 | 3258 | 3258 | 3206.5604 | 2943.3961 | 2671.56 | 2671.56 | -2629.3795 | -2413.5848 | 1864.7604 | -1864.7604 | 1835.3182 | -1684.6925
0.83 | 3258 | 3258 | 3201.9174 | 2948.5559 | 2704.14 | 2704.14 | -2657.5915 | -2447.3014 | 1817.1931 | -1817.1931 | 1785.9123 | -1644.5966
0.84 | 3258 | 3258 | 3197.2744 | 2953.7158 | 2736.72 | 2736.72 | -2685.7105 | -2481.1213 | 1767.7465 | -1767.7465 | 1734.7976 | -1602.646
0.85 | 3258 | 3258 | 3192.6314 | 2958.8757 | 2769.3 | 2769.3 | -2713.7367 | -2515.0443 | 1716.258 | -1716.258 | 1681.823 | -1558.6845
0.86 | 3258 | 3258 | 3187.9885 | 2964.0355 | 2801.88 | 2801.88 | -2741.6701 | -2549.0705 | 1662.538 | -1662.538 | 1626.8115 | -1512.5296
0.87 | 3258 | 3258 | 3183.3455 | 2969.1954 | 2834.46 | 2834.46 | -2769.5106 | -2583.2 | 1606.3625 | -1606.3625 | 1569.554 | -1463.9669
0.88 | 3258 | 3258 | 3178.7025 | 2974.3552 | 2867.04 | 2867.04 | -2797.2582 | -2617.4326 | 1547.4643 | -1547.4643 | 1509.8 | -1412.7405
0.89 | 3258 | 3258 | 3174.0595 | 2979.5151 | 2899.62 | 2899.62 | -2824.913 | -2651.7684 | 1485.5194 | -1485.5194 | 1447.2458 | -1358.5413
0.9 | 3258 | 3258 | 3169.4165 | 2984.675 | 2932.2 | 2932.2 | -2852.4749 | -2686.2075 | 1420.1293 | -1420.1293 | 1381.5166 | -1300.9897
0.91 | 3258 | 3258 | 3162.9277 | 2990.9726 | 2964.78 | 2964.78 | -2878.2642 | -2721.7851 | 1350.7937 | -1350.7937 | 1311.3759 | -1240.0819
0.92 | 3258 | 3258 | 3156.4389 | 2997.2703 | 2997.36 | 2997.36 | -2903.9237 | -2757.4887 | 1276.87 | -1276.87 | 1237.0663 | -1174.6852
0.93 | 3258 | 3258 | 3149.95 | 3003.5679 | 3029.94 | 3029.94 | -2929.4535 | -2793.3182 | 1197.5089 | -1197.5089 | 1157.7941 | -1103.99
0.94 | 3258 | 3258 | 3143.4612 | 3009.8656 | 3062.52 | 3062.52 | -2954.8535 | -2829.2737 | 1111.5463 | -1111.5463 | 1072.4686 | -1026.8892
0.95 | 3258 | 3258 | 3136.9724 | 3016.1633 | 3095.1 | 3095.1 | -2980.1238 | -2865.3551 | 1017.3102 | -1017.3102 | 979.5193 | -941.7967
0.96 | 3258 | 3258 | 3125.0436 | 3028.3963 | 3127.68 | 3127.68 | -3000.0419 | -2907.2605 | 912.24 | -912.24 | 875.0122 | -847.951
0.97 | 3258 | 3258 | 3113.1149 | 3040.6294 | 3160.26 | 3160.26 | -3019.7214 | -2949.4105 | 792.0358 | -792.0358 | 756.8135 | -739.192
0.98 | 3258 | 3258 | 3101.1861 | 3052.8625 | 3192.84 | 3192.84 | -3039.1624 | -2991.8052 | 648.3338 | -648.3338 | 617.1282 | -607.512
0.99 | 3258 | 3258 | 3089.2574 | 3065.0955 | 3225.42 | 3225.42 | -3058.3648 | -3034.4446 | 459.5975 | -459.5975 | 435.7934 | -432.3849
1 | 3258 | 3258 | 3077.3286 | 3077.3286 | 3258 | 3258 | -3077.3286 | -3077.3286 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited

## CATL_25C_1.0pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 25 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V) |  |  |  | 1496 |  | VDC
Min. battery voltage |  |  |  | 1164 |  | VDC |  | Please select:
AC voltage |  |  |  | 1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2172 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@min battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP @25°C, 1164Vdc min. battery voltage and 1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2172.003 | 2172.0026 | 2172.003 | 2172.0025 | 0 | 0 | 0 | 0 | 2172.003 | -2172.0026 | 2172.003 | -2172.0025
0.01 | 2172.003 | 2172.0026 | 2172.003 | 2172.0025 | 0.02172 | 0.02172 | -0.02172 | -0.02172 | 2172.003 | -2172.0026 | 2172.003 | -2172.0025
0.05 | 2186.98 | 2185.1705 | 2186.98 | 2184.5954 | 109.349 | 109.2585 | -109.349 | -109.2298 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.1 | 2201.96 | 2198.341 | 2201.96 | 2197.1907 | 220.196 | 219.8341 | -220.196 | -219.7191 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.15 | 2245.7245 | 2237.9887 | 2245.7245 | 2232.5271 | 336.8587 | 335.6983 | -336.8587 | -334.8791 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.2 | 2289.489 | 2277.6363 | 2289.489 | 2267.8635 | 457.8978 | 455.5273 | -457.8978 | -453.5727 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.25 | 2358.9294 | 2344.3711 | 2358.9294 | 2323.3315 | 589.7324 | 586.0928 | -589.7324 | -580.8329 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.3 | 2428.3698 | 2411.1059 | 2428.3698 | 2378.7995 | 728.5109 | 723.3318 | -728.5109 | -713.6398 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.35 | 2519.3945 | 2501.8591 | 2519.3945 | 2451.2133 | 881.7881 | 875.6507 | -881.7881 | -857.9247 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.4 | 2610.4191 | 2592.6124 | 2610.4191 | 2523.6271 | 1044.1676 | 1037.0449 | -1044.1676 | -1009.4509 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.45 | 2718.8648 | 2709.9614 | 2718.8648 | 2609.5375 | 1223.4891 | 1219.4826 | -1223.4891 | -1174.2919 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.5 | 2827.3104 | 2827.3104 | 2827.3104 | 2695.4478 | 1413.6552 | 1413.6552 | -1413.6552 | -1347.7239 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.51 | 2851.7465 | 2851.7465 | 2851.7465 | 2716.0018 | 1454.3907 | 1454.3907 | -1454.3907 | -1385.1609 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.52 | 2876.1827 | 2876.1827 | 2876.1827 | 2736.5558 | 1495.615 | 1495.615 | -1495.615 | -1423.009 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.53 | 2900.6188 | 2900.6188 | 2900.6188 | 2757.1098 | 1537.328 | 1537.328 | -1537.328 | -1461.2682 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.54 | 2925.055 | 2925.055 | 2925.055 | 2777.6637 | 1579.5297 | 1579.5297 | -1579.5297 | -1499.9384 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.55 | 2949.4911 | 2949.4911 | 2949.4911 | 2798.2177 | 1622.2201 | 1622.2201 | -1622.2201 | -1539.0197 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.56 | 2973.9273 | 2973.9273 | 2973.9273 | 2818.7717 | 1665.3993 | 1665.3993 | -1665.3993 | -1578.5121 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.57 | 2998.3634 | 2998.3634 | 2998.3634 | 2839.3257 | 1709.0671 | 1709.0671 | -1709.0671 | -1618.4156 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.58 | 3022.7996 | 3022.7996 | 3022.7996 | 2859.8796 | 1753.2237 | 1753.2237 | -1753.2237 | -1658.7302 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.59 | 3047.2357 | 3047.2357 | 3047.2357 | 2880.4336 | 1797.8691 | 1797.8691 | -1797.8691 | -1699.4558 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.6 | 3071.6719 | 3071.6719 | 3071.6719 | 2900.9876 | 1843.0031 | 1843.0031 | -1843.0031 | -1740.5926 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.61 | 3098.2522 | 3098.2522 | 3098.2522 | 2924.1461 | 1889.9338 | 1889.9338 | -1889.9338 | -1783.7291 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.62 | 3124.8325 | 3124.8325 | 3124.8325 | 2947.3047 | 1937.3962 | 1937.3962 | -1937.3962 | -1827.3289 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.63 | 3151.4128 | 3151.4128 | 3151.4128 | 2970.4632 | 1985.3901 | 1985.3901 | -1985.3901 | -1871.3918 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.64 | 3177.9932 | 3177.9932 | 3177.9932 | 2993.6217 | 2033.9156 | 2033.9156 | -2033.9156 | -1915.9179 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.65 | 3204.5735 | 3204.5735 | 3204.5735 | 3016.7803 | 2082.9728 | 2082.9728 | -2082.9728 | -1960.9072 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.66 | 3231.1538 | 3231.1538 | 3231.1538 | 3039.9388 | 2132.5615 | 2132.5615 | -2132.5615 | -2006.3596 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.67 | 3257.7341 | 3257.7341 | 3257.7341 | 3063.0974 | 2182.6819 | 2182.6819 | -2182.6819 | -2052.2752 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.68 | 3284.3144 | 3284.3144 | 3284.3144 | 3086.2559 | 2233.3338 | 2233.3338 | -2233.3338 | -2098.654 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.69 | 3310.8948 | 3310.8948 | 3310.8948 | 3109.4144 | 2284.5174 | 2284.5174 | -2284.5174 | -2145.496 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.7 | 3337.4751 | 3337.4751 | 3337.4751 | 3132.573 | 2336.2326 | 2336.2326 | -2336.2326 | -2192.8011 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.71 | 3365.7276 | 3365.7276 | 3361.0438 | 3145.213 | 2389.6666 | 2389.6666 | -2386.3411 | -2233.1013 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.72 | 3393.9801 | 3393.9801 | 3384.6126 | 3157.8531 | 2443.6657 | 2443.6657 | -2436.9211 | -2273.6542 | 2172.003 | -2172.0026 | 2172.003 | -2172.0026
0.73 | 3422.2326 | 3422.2326 | 3408.1814 | 3170.4932 | 2498.2298 | 2498.2298 | -2487.9724 | -2314.46 | 2172.003 | -2172.0026 | 2172.003 | -2166.8645
0.74 | 3450.4851 | 3450.4851 | 3431.7501 | 3183.1333 | 2553.3589 | 2553.3589 | -2539.4951 | -2355.5186 | 2172.003 | -2172.0026 | 2172.003 | -2140.9973
0.75 | 3478.7375 | 3478.7375 | 3455.3189 | 3195.7733 | 2609.0532 | 2609.0532 | -2591.4892 | -2396.83 | 2172.003 | -2172.0026 | 2172.003 | -2113.8054
0.76 | 3506.99 | 3506.99 | 3478.8876 | 3208.4134 | 2665.3124 | 2665.3124 | -2643.9546 | -2438.3942 | 2172.003 | -2172.0026 | 2172.003 | -2085.2219
0.77 | 3535.2425 | 3535.2425 | 3502.4564 | 3221.0535 | 2722.1367 | 2722.1367 | -2696.8914 | -2480.2112 | 2172.003 | -2172.0026 | 2172.003 | -2055.1735
0.78 | 3563.495 | 3563.495 | 3526.0251 | 3233.6936 | 2779.5261 | 2779.5261 | -2750.2996 | -2522.281 | 2172.003 | -2172.0026 | 2172.003 | -2023.5792
0.79 | 3591.7475 | 3591.7475 | 3549.5939 | 3246.3336 | 2837.4805 | 2837.4805 | -2804.1792 | -2564.6036 | 2172.003 | -2172.0026 | 2172.003 | -1990.3494
0.8 | 3620 | 3620 | 3573.1627 | 3258.9737 | 2896 | 2896 | -2858.5301 | -2607.179 | 2172 | -2172 | 2143.8976 | -1955.3842
0.81 | 3620 | 3620 | 3568.0038 | 3264.7069 | 2932.2 | 2932.2 | -2890.0831 | -2644.4126 | 2122.8762 | -2122.8762 | 2092.384 | -1914.5217
0.82 | 3620 | 3620 | 3562.8449 | 3270.4401 | 2968.4 | 2968.4 | -2921.5328 | -2681.7609 | 2071.9559 | -2071.9559 | 2039.2425 | -1871.8806
0.83 | 3620 | 3620 | 3557.686 | 3276.1733 | 3004.6 | 3004.6 | -2952.8794 | -2719.2238 | 2019.1035 | -2019.1035 | 1984.347 | -1827.3295
0.84 | 3620 | 3620 | 3552.5272 | 3281.9064 | 3040.8 | 3040.8 | -2984.1228 | -2756.8014 | 1964.1628 | -1964.1628 | 1927.5529 | -1780.7178
0.85 | 3620 | 3620 | 3547.3683 | 3287.6396 | 3077 | 3077 | -3015.263 | -2794.4937 | 1906.9533 | -1906.9533 | 1868.6922 | -1731.8716
0.86 | 3620 | 3620 | 3542.2094 | 3293.3728 | 3113.2 | 3113.2 | -3046.3001 | -2832.3006 | 1847.2644 | -1847.2644 | 1807.5683 | -1680.5885
0.87 | 3620 | 3620 | 3537.0505 | 3299.106 | 3149.4 | 3149.4 | -3077.234 | -2870.2222 | 1784.8472 | -1784.8472 | 1743.9488 | -1626.6299
0.88 | 3620 | 3620 | 3531.8916 | 3304.8392 | 3185.6 | 3185.6 | -3108.0647 | -2908.2585 | 1719.4047 | -1719.4047 | 1677.5556 | -1569.7116
0.89 | 3620 | 3620 | 3526.7328 | 3310.5723 | 3221.8 | 3221.8 | -3138.7922 | -2946.4094 | 1650.5771 | -1650.5771 | 1608.0509 | -1509.4903
0.9 | 3620 | 3620 | 3521.5739 | 3316.3055 | 3258 | 3258 | -3169.4165 | -2984.675 | 1577.9214 | -1577.9214 | 1535.0185 | -1445.5441
0.91 | 3620 | 3620 | 3514.3641 | 3323.3029 | 3294.2 | 3294.2 | -3198.0713 | -3024.2057 | 1500.8819 | -1500.8819 | 1457.0843 | -1377.8688
0.92 | 3620 | 3620 | 3507.1543 | 3330.3003 | 3330.4 | 3330.4 | -3226.5819 | -3063.8763 | 1418.7445 | -1418.7445 | 1374.5182 | -1305.2058
0.93 | 3620 | 3620 | 3499.9445 | 3337.2977 | 3366.6 | 3366.6 | -3254.9484 | -3103.6869 | 1330.5655 | -1330.5655 | 1286.4379 | -1226.6555
0.94 | 3620 | 3620 | 3492.7347 | 3344.2951 | 3402.8 | 3402.8 | -3283.1706 | -3143.6374 | 1235.0515 | -1235.0515 | 1191.6318 | -1140.988
0.95 | 3620 | 3620 | 3485.5249 | 3351.2925 | 3439 | 3439 | -3311.2486 | -3183.7279 | 1130.3446 | -1130.3446 | 1088.3548 | -1046.4407
0.96 | 3620 | 3620 | 3472.2707 | 3364.8848 | 3475.2 | 3475.2 | -3333.3799 | -3230.2894 | 1013.6 | -1013.6 | 972.2358 | -942.1677
0.97 | 3620 | 3620 | 3459.0165 | 3378.4771 | 3511.4 | 3511.4 | -3355.246 | -3277.1228 | 880.0398 | -880.0398 | 840.9039 | -821.3244
0.98 | 3620 | 3620 | 3445.7623 | 3392.0694 | 3547.6 | 3547.6 | -3376.8471 | -3324.228 | 720.3709 | -720.3709 | 685.698 | -675.0133
0.99 | 3620 | 3620 | 3432.5082 | 3405.6617 | 3583.8 | 3583.8 | -3398.1831 | -3371.6051 | 510.6638 | -510.6638 | 484.2149 | -480.4277
1 | 3620 | 3620 | 3419.254 | 3419.254 | 3620 | 3620 | -3419.254 | -3419.254 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited

## CATL_25C_1.1pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 25 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V) |  |  |  | 1496 |  | VDC
Min. battery voltage |  |  |  | 1164 |  | VDC |  | Please select:
AC voltage |  |  |  | 1.1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2172 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@min battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP @25°C, 1164Vdc min. battery voltage and 1.1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2172.003 | 2172.003 | 2172.003 | 2172.003 | 0 | 0 | 0 | 0 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.01 | 2172.003 | 2172.003 | 2172.003 | 2172.003 | 0.02172 | 0.02172 | -0.02172 | -0.02172 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.05 | 2186.98 | 2186.98 | 2186.98 | 2186.98 | 109.349 | 109.349 | -109.349 | -109.349 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.1 | 2201.96 | 2201.96 | 2201.96 | 2201.96 | 220.196 | 220.196 | -220.196 | -220.196 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.15 | 2245.7245 | 2245.7245 | 2245.7245 | 2244.6232 | 336.8587 | 336.8587 | -336.8587 | -336.6935 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.2 | 2289.489 | 2289.489 | 2289.489 | 2287.2863 | 457.8978 | 457.8978 | -457.8978 | -457.4573 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.25 | 2358.9294 | 2358.9294 | 2358.9294 | 2352.8682 | 589.7324 | 589.7324 | -589.7324 | -588.2171 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.3 | 2428.3698 | 2428.3698 | 2428.3698 | 2418.4501 | 728.5109 | 728.5109 | -728.5109 | -725.535 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.35 | 2519.3945 | 2519.3945 | 2519.3945 | 2502.9902 | 881.7881 | 881.7881 | -881.7881 | -876.0466 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.4 | 2610.4191 | 2610.4191 | 2610.4191 | 2587.5302 | 1044.1676 | 1044.1676 | -1044.1676 | -1035.0121 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.45 | 2718.8648 | 2718.8648 | 2718.8648 | 2688.5166 | 1223.4891 | 1223.4891 | -1223.4891 | -1209.8325 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.5 | 2827.3104 | 2827.3104 | 2827.3104 | 2789.503 | 1413.6552 | 1413.6552 | -1413.6552 | -1394.7515 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.51 | 2851.7465 | 2851.7465 | 2851.7465 | 2813.3979 | 1454.3907 | 1454.3907 | -1454.3907 | -1434.833 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.52 | 2876.1827 | 2876.1827 | 2876.1827 | 2837.2929 | 1495.615 | 1495.615 | -1495.615 | -1475.3923 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.53 | 2900.6188 | 2900.6188 | 2900.6188 | 2861.1879 | 1537.328 | 1537.328 | -1537.328 | -1516.4296 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.54 | 2925.055 | 2925.055 | 2925.055 | 2885.0828 | 1579.5297 | 1579.5297 | -1579.5297 | -1557.9447 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.55 | 2949.4911 | 2949.4911 | 2949.4911 | 2908.9778 | 1622.2201 | 1622.2201 | -1622.2201 | -1599.9378 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.56 | 2973.9273 | 2973.9273 | 2973.9273 | 2932.8727 | 1665.3993 | 1665.3993 | -1665.3993 | -1642.4087 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.57 | 2998.3634 | 2998.3634 | 2998.3634 | 2956.7677 | 1709.0671 | 1709.0671 | -1709.0671 | -1685.3576 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.58 | 3022.7996 | 3022.7996 | 3022.7996 | 2980.6626 | 1753.2237 | 1753.2237 | -1753.2237 | -1728.7843 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.59 | 3047.2357 | 3047.2357 | 3047.2357 | 3004.5576 | 1797.8691 | 1797.8691 | -1797.8691 | -1772.689 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.6 | 3071.6719 | 3071.6719 | 3071.6719 | 3028.4525 | 1843.0031 | 1843.0031 | -1843.0031 | -1817.0715 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.61 | 3098.2522 | 3098.2522 | 3098.2522 | 3055.192 | 1889.9338 | 1889.9338 | -1889.9338 | -1863.6671 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.62 | 3124.8325 | 3124.8325 | 3124.8325 | 3081.9314 | 1937.3962 | 1937.3962 | -1937.3962 | -1910.7975 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.63 | 3151.4128 | 3151.4128 | 3151.4128 | 3108.6708 | 1985.3901 | 1985.3901 | -1985.3901 | -1958.4626 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.64 | 3177.9932 | 3177.9932 | 3177.9932 | 3135.4103 | 2033.9156 | 2033.9156 | -2033.9156 | -2006.6626 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.65 | 3204.5735 | 3204.5735 | 3204.5735 | 3162.1497 | 2082.9728 | 2082.9728 | -2082.9728 | -2055.3973 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.66 | 3231.1538 | 3231.1538 | 3231.1538 | 3188.8892 | 2132.5615 | 2132.5615 | -2132.5615 | -2104.6668 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.67 | 3257.7341 | 3257.7341 | 3257.7341 | 3215.6286 | 2182.6819 | 2182.6819 | -2182.6819 | -2154.4712 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.68 | 3284.3144 | 3284.3144 | 3284.3144 | 3242.368 | 2233.3338 | 2233.3338 | -2233.3338 | -2204.8103 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.69 | 3310.8948 | 3310.8948 | 3310.8948 | 3269.1075 | 2284.5174 | 2284.5174 | -2284.5174 | -2255.6841 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.7 | 3337.4751 | 3337.4751 | 3337.4751 | 3295.8469 | 2336.2326 | 2336.2326 | -2336.2326 | -2307.0928 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.71 | 3365.7276 | 3365.7276 | 3365.7276 | 3328.2622 | 2389.6666 | 2389.6666 | -2389.6666 | -2363.0662 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.72 | 3393.9801 | 3393.9801 | 3393.9801 | 3360.6775 | 2443.6657 | 2443.6657 | -2443.6657 | -2419.6878 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.73 | 3422.2326 | 3422.2326 | 3422.2326 | 3393.0928 | 2498.2298 | 2498.2298 | -2498.2298 | -2476.9578 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.74 | 3450.4851 | 3450.4851 | 3450.4851 | 3425.5081 | 2553.3589 | 2553.3589 | -2553.3589 | -2534.876 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.75 | 3478.7375 | 3478.7375 | 3478.7375 | 3457.9234 | 2609.0532 | 2609.0532 | -2609.0532 | -2593.4426 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.76 | 3506.99 | 3506.99 | 3506.99 | 3490.3388 | 2665.3124 | 2665.3124 | -2665.3124 | -2652.6575 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.77 | 3535.2425 | 3535.2425 | 3535.2425 | 3522.7541 | 2722.1367 | 2722.1367 | -2722.1367 | -2712.5206 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.78 | 3563.495 | 3563.495 | 3563.495 | 3555.1694 | 2779.5261 | 2779.5261 | -2779.5261 | -2773.0321 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.79 | 3591.7475 | 3591.7475 | 3591.7475 | 3570.967 | 2837.4805 | 2837.4805 | -2837.4805 | -2821.0639 | 2172.003 | -2172.003 | 2172.003 | -2172.003
0.8 | 3620 | 3620 | 3620 | 3584.8711 | 2896 | 2896 | -2896 | -2867.8969 | 2172 | -2172 | 2172 | -2150.9226
0.81 | 3620 | 3620 | 3620 | 3591.1776 | 2932.2 | 2932.2 | -2932.2 | -2908.8538 | 2122.8762 | -2122.8762 | 2122.8762 | -2105.9738
0.82 | 3620 | 3620 | 3620 | 3597.4841 | 2968.4 | 2968.4 | -2968.4 | -2949.9369 | 2071.9559 | -2071.9559 | 2071.9559 | -2059.0687
0.83 | 3620 | 3620 | 3620 | 3603.7906 | 3004.6 | 3004.6 | -3004.6 | -2991.1462 | 2019.1035 | -2019.1035 | 2019.1035 | -2010.0625
0.84 | 3620 | 3620 | 3620 | 3610.0971 | 3040.8 | 3040.8 | -3040.8 | -3032.4815 | 1964.1628 | -1964.1628 | 1964.1628 | -1958.7896
0.85 | 3620 | 3620 | 3620 | 3616.4036 | 3077 | 3077 | -3077 | -3073.943 | 1906.9533 | -1906.9533 | 1906.9533 | -1905.0588
0.86 | 3620 | 3620 | 3620 | 3620 | 3113.2 | 3113.2 | -3113.2 | -3113.2 | 1847.2644 | -1847.2644 | 1847.2644 | -1847.2644
0.87 | 3620 | 3620 | 3620 | 3620 | 3149.4 | 3149.4 | -3149.4 | -3149.4 | 1784.8472 | -1784.8472 | 1784.8472 | -1784.8472
0.88 | 3620 | 3620 | 3620 | 3620 | 3185.6 | 3185.6 | -3185.6 | -3185.6 | 1719.4047 | -1719.4047 | 1719.4047 | -1719.4047
0.89 | 3620 | 3620 | 3620 | 3620 | 3221.8 | 3221.8 | -3221.8 | -3221.8 | 1650.5771 | -1650.5771 | 1650.5771 | -1650.5771
0.9 | 3620 | 3620 | 3620 | 3620 | 3258 | 3258 | -3258 | -3258 | 1577.9214 | -1577.9214 | 1577.9214 | -1577.9214
0.91 | 3620 | 3620 | 3620 | 3620 | 3294.2 | 3294.2 | -3294.2 | -3294.2 | 1500.8819 | -1500.8819 | 1500.8819 | -1500.8819
0.92 | 3620 | 3620 | 3620 | 3620 | 3330.4 | 3330.4 | -3330.4 | -3330.4 | 1418.7445 | -1418.7445 | 1418.7445 | -1418.7445
0.93 | 3620 | 3620 | 3620 | 3620 | 3366.6 | 3366.6 | -3366.6 | -3366.6 | 1330.5655 | -1330.5655 | 1330.5655 | -1330.5655
0.94 | 3620 | 3620 | 3620 | 3620 | 3402.8 | 3402.8 | -3402.8 | -3402.8 | 1235.0515 | -1235.0515 | 1235.0515 | -1235.0515
0.95 | 3620 | 3620 | 3620 | 3620 | 3439 | 3439 | -3439 | -3439 | 1130.3446 | -1130.3446 | 1130.3446 | -1130.3446
0.96 | 3620 | 3620 | 3620 | 3620 | 3475.2 | 3475.2 | -3475.2 | -3475.2 | 1013.6 | -1013.6 | 1013.6 | -1013.6
0.97 | 3620 | 3620 | 3620 | 3620 | 3511.4 | 3511.4 | -3511.4 | -3511.4 | 880.0398 | -880.0398 | 880.0398 | -880.0398
0.98 | 3620 | 3620 | 3620 | 3620 | 3547.6 | 3547.6 | -3547.6 | -3547.6 | 720.3709 | -720.3709 | 720.3709 | -720.3709
0.99 | 3620 | 3620 | 3620 | 3620 | 3583.8 | 3583.8 | -3583.8 | -3583.8 | 510.6638 | -510.6638 | 510.6638 | -510.6638
1 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | -3620 | -3620 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited

## CATL_35C_0.9pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 35 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1496 |  | VDC
Nom. Battery Voltage** |  |  |  | 1296.8 |  | VDC
Min. Battery Voltage*** |  |  |  | 1164 |  | VDC |  | Please select:
AC Voltage |  |  |  | 0.9 |  | pu |  | Project plant specific |  |  | VArRtg: | 2172 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP @35°C, 1164Vdc min. battery voltage and 0.9pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 1954.8024 | 1954.8023 | 1954.8024 | 1954.802 | 0 | 0 | 0 | 0 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.802
0.01 | 1954.8024 | 1954.8023 | 1954.8024 | 1954.802 | 0.019548 | 0.019548 | -0.019548 | -0.019548 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.802
0.05 | 1966.7481 | 1966.4244 | 1966.7481 | 1964.6121 | 98.3374 | 98.3212 | -98.3374 | -98.2306 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.1 | 1978.6961 | 1978.0488 | 1978.6961 | 1974.4241 | 197.8696 | 197.8049 | -197.8696 | -197.4424 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.15 | 2013.6982 | 2012.966 | 2013.6982 | 2002.1679 | 302.0547 | 301.9449 | -302.0547 | -300.3252 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.2 | 2048.7003 | 2047.8831 | 2048.7003 | 2029.9117 | 409.7401 | 409.5766 | -409.7401 | -405.9823 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.25 | 2104.5035 | 2104.0949 | 2104.5035 | 2073.4511 | 526.1259 | 526.0237 | -526.1259 | -518.3628 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.3 | 2160.3067 | 2160.3067 | 2160.3067 | 2116.9904 | 648.092 | 648.092 | -648.092 | -635.0971 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.35 | 2233.8826 | 2233.8826 | 2233.8826 | 2174.1962 | 781.8589 | 781.8589 | -781.8589 | -760.9687 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.4 | 2307.4585 | 2307.4585 | 2307.4585 | 2231.402 | 922.9834 | 922.9834 | -922.9834 | -892.5608 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.45 | 2395.6429 | 2395.6429 | 2395.6429 | 2299.4346 | 1078.0393 | 1078.0393 | -1078.0393 | -1034.7456 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.5 | 2483.8273 | 2483.8273 | 2483.8273 | 2367.4673 | 1241.9136 | 1241.9136 | -1241.9136 | -1183.7337 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.51 | 2503.8095 | 2503.8095 | 2502.9732 | 2383.911 | 1276.9429 | 1276.9429 | -1276.5163 | -1215.7946 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.52 | 2523.7917 | 2523.7917 | 2522.1191 | 2400.3546 | 1312.3717 | 1312.3717 | -1311.502 | -1248.1844 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.53 | 2543.774 | 2543.774 | 2541.2651 | 2416.7982 | 1348.2002 | 1348.2002 | -1346.8705 | -1280.9031 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.54 | 2563.7562 | 2563.7562 | 2560.411 | 2433.2419 | 1384.4283 | 1384.4283 | -1382.6219 | -1313.9506 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.55 | 2583.7384 | 2583.7384 | 2579.5569 | 2449.6855 | 1421.0561 | 1421.0561 | -1418.7563 | -1347.3271 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.56 | 2603.7206 | 2603.7206 | 2598.7028 | 2466.1292 | 1458.0836 | 1458.0836 | -1455.2736 | -1381.0324 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.57 | 2623.7029 | 2623.7029 | 2617.8487 | 2482.5728 | 1495.5106 | 1495.5106 | -1492.1738 | -1415.0665 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.58 | 2643.6851 | 2643.6851 | 2636.9947 | 2499.0165 | 1533.3374 | 1533.3374 | -1529.4569 | -1449.4296 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.59 | 2663.6673 | 2663.6673 | 2656.1406 | 2515.4601 | 1571.5637 | 1571.5637 | -1567.1229 | -1484.1215 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.6 | 2683.6495 | 2683.6495 | 2675.2865 | 2531.9038 | 1610.1897 | 1610.1897 | -1605.1719 | -1519.1423 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.61 | 2705.4928 | 2705.4928 | 2695.6426 | 2545.9245 | 1650.3506 | 1650.3506 | -1644.342 | -1553.0139 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.62 | 2727.336 | 2727.336 | 2715.9986 | 2559.9452 | 1690.9483 | 1690.9483 | -1683.9191 | -1587.166 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.63 | 2749.1792 | 2749.1792 | 2736.3546 | 2573.9659 | 1731.9829 | 1731.9829 | -1723.9034 | -1621.5985 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.64 | 2771.0224 | 2771.0224 | 2756.7107 | 2587.9866 | 1773.4543 | 1773.4543 | -1764.2948 | -1656.3114 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.65 | 2792.8656 | 2792.8656 | 2777.0667 | 2602.0073 | 1815.3626 | 1815.3626 | -1805.0934 | -1691.3048 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.66 | 2814.7088 | 2814.7088 | 2797.4228 | 2616.028 | 1857.7078 | 1857.7078 | -1846.299 | -1726.5785 | 1954.8024 | -1954.8023 | 1954.8024 | -1954.8023
0.67 | 2836.552 | 2836.552 | 2817.7788 | 2630.0487 | 1900.4899 | 1900.4899 | -1887.9118 | -1762.1326 | 1954.8024 | -1954.8023 | 1954.8024 | -1952.4459
0.68 | 2858.3952 | 2858.3952 | 2838.1349 | 2644.0694 | 1943.7088 | 1943.7088 | -1929.9317 | -1797.9672 | 1954.8024 | -1954.8023 | 1954.8024 | -1938.6637
0.69 | 2880.2384 | 2880.2384 | 2858.4909 | 2658.0901 | 1987.3645 | 1987.3645 | -1972.3587 | -1834.0822 | 1954.8024 | -1954.8023 | 1954.8024 | -1923.9505
0.7 | 2902.0816 | 2902.0816 | 2878.8469 | 2672.1108 | 2031.4572 | 2031.4572 | -2015.1929 | -1870.4776 | 1954.8024 | -1954.8023 | 1954.8024 | -1908.2688
0.71 | 2918.157 | 2918.157 | 2889.1871 | 2677.8099 | 2071.8914 | 2071.8914 | -2051.3228 | -1901.245 | 1954.8024 | -1954.8023 | 1954.8024 | -1885.7182
0.72 | 2934.2323 | 2934.2323 | 2899.5272 | 2683.5089 | 2112.6472 | 2112.6472 | -2087.6596 | -1932.1264 | 1954.8024 | -1954.8023 | 1954.8024 | -1862.2856
0.73 | 2950.3076 | 2950.3076 | 2909.8673 | 2689.208 | 2153.7245 | 2153.7245 | -2124.2031 | -1963.1218 | 1954.8024 | -1954.8023 | 1954.8024 | -1837.9315
0.74 | 2966.3829 | 2966.3829 | 2920.2074 | 2694.907 | 2195.1233 | 2195.1233 | -2160.9535 | -1994.2312 | 1954.8024 | -1954.8023 | 1954.8024 | -1812.613
0.75 | 2982.4582 | 2982.4582 | 2930.5475 | 2700.6061 | 2236.8437 | 2236.8437 | -2197.9106 | -2025.4546 | 1954.8024 | -1954.8023 | 1938.375 | -1786.283
0.76 | 2998.5335 | 2998.5335 | 2940.8876 | 2706.3051 | 2278.8855 | 2278.8855 | -2235.0746 | -2056.7919 | 1948.8161 | -1948.8161 | 1911.3507 | -1758.8901
0.77 | 3014.6088 | 3014.6088 | 2951.2277 | 2712.0042 | 2321.2488 | 2321.2488 | -2272.4453 | -2088.2432 | 1923.4527 | -1923.4527 | 1883.0128 | -1730.3777
0.78 | 3030.6842 | 3030.6842 | 2961.5678 | 2717.7032 | 2363.9336 | 2363.9336 | -2310.0229 | -2119.8085 | 1896.5401 | -1896.5401 | 1853.2885 | -1700.683
0.79 | 3046.7595 | 3046.7595 | 2971.9079 | 2723.4023 | 2406.94 | 2406.94 | -2347.8073 | -2151.4878 | 1867.9891 | -1867.9891 | 1822.0971 | -1669.7366
0.8 | 3062.8348 | 3062.8348 | 2982.248 | 2729.1013 | 2450.2678 | 2450.2678 | -2385.7984 | -2183.2811 | 1837.7009 | -1837.7009 | 1789.3488 | -1637.4608
0.81 | 3062.8348 | 3062.8348 | 2977.9845 | 2733.7771 | 2480.8962 | 2480.8962 | -2412.1674 | -2214.3595 | 1796.1378 | -1796.1378 | 1746.3791 | -1603.1686
0.82 | 3062.8348 | 3062.8348 | 2973.7209 | 2738.453 | 2511.5245 | 2511.5245 | -2438.4511 | -2245.5314 | 1753.0549 | -1753.0549 | 1702.0494 | -1567.3906
0.83 | 3062.8348 | 3062.8348 | 2969.4573 | 2743.1288 | 2542.1529 | 2542.1529 | -2464.6496 | -2276.7969 | 1708.3371 | -1708.3371 | 1656.2546 | -1530.0168
0.84 | 3062.8348 | 3062.8348 | 2965.1938 | 2747.8046 | 2572.7812 | 2572.7812 | -2490.7628 | -2308.1559 | 1661.8525 | -1661.8525 | 1608.8738 | -1490.9214
0.85 | 3062.8348 | 3062.8348 | 2960.9302 | 2752.4804 | 2603.4096 | 2603.4096 | -2516.7907 | -2339.6083 | 1613.4483 | -1613.4483 | 1559.7668 | -1449.959
0.86 | 3062.8348 | 3062.8348 | 2956.6666 | 2757.1562 | 2634.0379 | 2634.0379 | -2542.7333 | -2371.1543 | 1562.9463 | -1562.9463 | 1508.7693 | -1406.9604
0.87 | 3062.8348 | 3062.8348 | 2952.4031 | 2761.832 | 2664.6663 | 2664.6663 | -2568.5907 | -2402.7939 | 1510.136 | -1510.136 | 1455.6874 | -1361.726
0.88 | 3062.8348 | 3062.8348 | 2948.1395 | 2766.5078 | 2695.2946 | 2695.2946 | -2594.3628 | -2434.5269 | 1454.7659 | -1454.7659 | 1400.2887 | -1314.0184
0.89 | 3062.8348 | 3062.8348 | 2943.8759 | 2771.1837 | 2725.923 | 2725.923 | -2620.0496 | -2466.3535 | 1396.5318 | -1396.5318 | 1342.2912 | -1263.5504
0.9 | 3062.8348 | 3062.8348 | 2939.6124 | 2775.8595 | 2756.5513 | 2756.5513 | -2645.6511 | -2498.2735 | 1335.0587 | -1335.0587 | 1281.3473 | -1209.9691
0.91 | 3062.8348 | 3062.8348 | 2933.4686 | 2782.1414 | 2787.1797 | 2787.1797 | -2669.4564 | -2531.7487 | 1269.8766 | -1269.8766 | 1216.2403 | -1153.4988
0.92 | 3062.8348 | 3062.8348 | 2927.3248 | 2788.4233 | 2817.808 | 2817.808 | -2693.1388 | -2565.3495 | 1200.3812 | -1200.3812 | 1147.2723 | -1092.8343
0.93 | 3062.8348 | 3062.8348 | 2921.181 | 2794.7053 | 2848.4363 | 2848.4363 | -2716.6984 | -2599.0759 | 1125.7741 | -1125.7741 | 1073.7079 | -1027.2205
0.94 | 3062.8348 | 3062.8348 | 2915.0373 | 2800.9872 | 2879.0647 | 2879.0647 | -2740.135 | -2632.928 | 1044.9609 | -1044.9609 | 994.5362 | -955.6252
0.95 | 3062.8348 | 3062.8348 | 2908.8935 | 2807.2691 | 2909.693 | 2909.693 | -2763.4488 | -2666.9057 | 956.3699 | -956.3699 | 908.3017 | -876.5695
0.96 | 3062.8166 | 3062.8166 | 2899.8237 | 2818.5242 | 2940.304 | 2940.304 | -2783.8307 | -2705.7832 | 857.5887 | -857.5887 | 811.9506 | -789.1868
0.97 | 3062.7985 | 3062.7985 | 2890.7539 | 2829.7792 | 2970.9145 | 2970.9145 | -2804.0312 | -2744.8859 | 744.5814 | -744.5814 | 702.7565 | -687.9332
0.98 | 3062.7804 | 3062.7804 | 2881.684 | 2841.0343 | 3001.5247 | 3001.5247 | -2824.0504 | -2784.2136 | 609.4856 | -609.4856 | 573.4479 | -565.3587
0.99 | 3062.7622 | 3062.7622 | 2872.6142 | 2852.2893 | 3032.1346 | 3032.1346 | -2843.8881 | -2823.7665 | 432.0558 | -432.0558 | 405.2321 | -402.3649
1 | 3062.7441 | 3062.7441 | 2863.5444 | 2863.5444 | 3062.7441 | 3062.7441 | -2863.5444 | -2863.5444 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_35C_1.0pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 35 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1496 |  | VDC
Nom. Battery Voltage** |  |  |  | 1296.8 |  | VDC
Min. Battery Voltage*** |  |  |  | 1164 |  | VDC |  | Please select:
AC Voltage |  |  |  | 1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2172 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP @35°C, 1164Vdc min. battery voltage and 1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2172.0027 | 2172.0026 | 2172.0027 | 2172.0022 | 0 | 0 | 0 | 0 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0022
0.01 | 2172.0027 | 2172.0026 | 2172.0027 | 2172.0022 | 0.02172 | 0.02172 | -0.02172 | -0.02172 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0022
0.05 | 2185.2756 | 2184.916 | 2185.2756 | 2182.9023 | 109.2638 | 109.2458 | -109.2638 | -109.1451 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.1 | 2198.5512 | 2197.832 | 2198.5512 | 2193.8046 | 219.8551 | 219.7832 | -219.8551 | -219.3805 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.15 | 2237.4425 | 2236.6289 | 2237.4425 | 2224.631 | 335.6164 | 335.4943 | -335.6164 | -333.6947 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.2 | 2276.3337 | 2275.4257 | 2276.3337 | 2255.4575 | 455.2667 | 455.0851 | -455.2667 | -451.0915 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.25 | 2338.3372 | 2337.8832 | 2338.3372 | 2303.8345 | 584.5843 | 584.4708 | -584.5843 | -575.9586 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.3 | 2400.3408 | 2400.3408 | 2400.3408 | 2352.2115 | 720.1022 | 720.1022 | -720.1022 | -705.6635 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.35 | 2482.0918 | 2482.0918 | 2482.0918 | 2415.7735 | 868.7321 | 868.7321 | -868.7321 | -845.5207 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.4 | 2563.8428 | 2563.8428 | 2563.8428 | 2479.3355 | 1025.5371 | 1025.5371 | -1025.5371 | -991.7342 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.45 | 2661.8254 | 2661.8254 | 2661.8254 | 2554.9274 | 1197.8214 | 1197.8214 | -1197.8214 | -1149.7173 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.5 | 2759.8081 | 2759.8081 | 2759.8081 | 2630.5192 | 1379.9041 | 1379.9041 | -1379.9041 | -1315.2596 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.51 | 2782.0106 | 2782.0106 | 2781.0814 | 2648.7899 | 1418.8254 | 1418.8254 | -1418.3515 | -1350.8829 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.52 | 2804.2131 | 2804.2131 | 2802.3546 | 2667.0607 | 1458.1908 | 1458.1908 | -1457.2244 | -1386.8715 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.53 | 2826.4155 | 2826.4155 | 2823.6278 | 2685.3314 | 1498.0002 | 1498.0002 | -1496.5228 | -1423.2256 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.54 | 2848.618 | 2848.618 | 2844.9011 | 2703.6021 | 1538.2537 | 1538.2537 | -1536.2466 | -1459.9451 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.55 | 2870.8205 | 2870.8205 | 2866.1743 | 2721.8728 | 1578.9513 | 1578.9513 | -1576.3959 | -1497.0301 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.56 | 2893.0229 | 2893.0229 | 2887.4476 | 2740.1436 | 1620.0928 | 1620.0928 | -1616.9706 | -1534.4804 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.57 | 2915.2254 | 2915.2254 | 2908.7208 | 2758.4143 | 1661.6785 | 1661.6785 | -1657.9709 | -1572.2961 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.58 | 2937.4279 | 2937.4279 | 2929.9941 | 2776.685 | 1703.7082 | 1703.7082 | -1699.3966 | -1610.4773 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.59 | 2959.6304 | 2959.6304 | 2951.2673 | 2794.9557 | 1746.1819 | 1746.1819 | -1741.2477 | -1649.0239 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.6 | 2981.8328 | 2981.8328 | 2972.5406 | 2813.2264 | 1789.0997 | 1789.0997 | -1783.5243 | -1687.9359 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.61 | 3006.1031 | 3006.1031 | 2995.1584 | 2828.805 | 1833.7229 | 1833.7229 | -1827.0466 | -1725.571 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.62 | 3030.3733 | 3030.3733 | 3017.7762 | 2844.3836 | 1878.8314 | 1878.8314 | -1871.0213 | -1763.5178 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.63 | 3054.6435 | 3054.6435 | 3040.394 | 2859.9621 | 1924.4254 | 1924.4254 | -1915.4482 | -1801.7761 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.64 | 3078.9138 | 3078.9138 | 3063.0119 | 2875.5407 | 1970.5048 | 1970.5048 | -1960.3276 | -1840.346 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.65 | 3103.184 | 3103.184 | 3085.6297 | 2891.1192 | 2017.0696 | 2017.0696 | -2005.6593 | -1879.2275 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.66 | 3127.4542 | 3127.4542 | 3108.2475 | 2906.6978 | 2064.1198 | 2064.1198 | -2051.4434 | -1918.4205 | 2172.0027 | -2172.0026 | 2172.0027 | -2172.0026
0.67 | 3151.7245 | 3151.7245 | 3130.8653 | 2922.2764 | 2111.6554 | 2111.6554 | -2097.6798 | -1957.9252 | 2172.0027 | -2172.0026 | 2172.0027 | -2169.3843
0.68 | 3175.9947 | 3175.9947 | 3153.4832 | 2937.8549 | 2159.6764 | 2159.6764 | -2144.3686 | -1997.7413 | 2172.0027 | -2172.0026 | 2172.0027 | -2154.0708
0.69 | 3200.2649 | 3200.2649 | 3176.101 | 2953.4335 | 2208.1828 | 2208.1828 | -2191.5097 | -2037.8691 | 2172.0027 | -2172.0026 | 2172.0027 | -2137.7228
0.7 | 3224.5352 | 3224.5352 | 3198.7188 | 2969.012 | 2257.1746 | 2257.1746 | -2239.1032 | -2078.3084 | 2172.0027 | -2172.0026 | 2172.0027 | -2120.2987
0.71 | 3242.3966 | 3242.3966 | 3210.2078 | 2975.3443 | 2302.1016 | 2302.1016 | -2279.2476 | -2112.4945 | 2172.0027 | -2172.0026 | 2172.0027 | -2095.2425
0.72 | 3260.2581 | 3260.2581 | 3221.6968 | 2981.6766 | 2347.3858 | 2347.3858 | -2319.6217 | -2146.8072 | 2172.0027 | -2172.0026 | 2172.0027 | -2069.2062
0.73 | 3278.1195 | 3278.1195 | 3233.1859 | 2988.0089 | 2393.0273 | 2393.0273 | -2360.2257 | -2181.2465 | 2172.0027 | -2172.0026 | 2172.0027 | -2042.1461
0.74 | 3295.981 | 3295.981 | 3244.6749 | 2994.3412 | 2439.0259 | 2439.0259 | -2401.0594 | -2215.8125 | 2172.0027 | -2172.0026 | 2172.0027 | -2014.0144
0.75 | 3313.8425 | 3313.8425 | 3256.1639 | 3000.6734 | 2485.3818 | 2485.3818 | -2442.1229 | -2250.5051 | 2172.0027 | -2172.0026 | 2153.75 | -1984.7589
0.76 | 3331.7039 | 3331.7039 | 3267.6529 | 3007.0057 | 2532.095 | 2532.095 | -2483.4162 | -2285.3243 | 2165.3512 | -2165.3512 | 2123.723 | -1954.3224
0.77 | 3349.5654 | 3349.5654 | 3279.1419 | 3013.338 | 2579.1653 | 2579.1653 | -2524.9393 | -2320.2702 | 2137.1697 | -2137.1697 | 2092.2364 | -1922.6419
0.78 | 3367.4268 | 3367.4268 | 3290.6309 | 3019.6703 | 2626.5929 | 2626.5929 | -2566.6921 | -2355.3428 | 2107.2667 | -2107.2667 | 2059.2094 | -1889.6478
0.79 | 3385.2883 | 3385.2883 | 3302.1199 | 3026.0025 | 2674.3778 | 2674.3778 | -2608.6747 | -2390.542 | 2075.5434 | -2075.5434 | 2024.5523 | -1855.2629
0.8 | 3403.1498 | 3403.1498 | 3313.6089 | 3032.3348 | 2722.5198 | 2722.5198 | -2650.8871 | -2425.8678 | 2041.8899 | -2041.8899 | 1988.1654 | -1819.4009
0.81 | 3403.1498 | 3403.1498 | 3308.8716 | 3037.5302 | 2756.5513 | 2756.5513 | -2680.186 | -2460.3994 | 1995.7087 | -1995.7087 | 1940.4212 | -1781.2984
0.82 | 3403.1498 | 3403.1498 | 3304.1343 | 3042.7255 | 2790.5828 | 2790.5828 | -2709.3902 | -2495.0349 | 1947.8388 | -1947.8388 | 1891.166 | -1741.5451
0.83 | 3403.1498 | 3403.1498 | 3299.397 | 3047.9209 | 2824.6143 | 2824.6143 | -2738.4995 | -2529.7743 | 1898.1523 | -1898.1523 | 1840.2829 | -1700.0187
0.84 | 3403.1498 | 3403.1498 | 3294.6597 | 3053.1162 | 2858.6458 | 2858.6458 | -2767.5142 | -2564.6176 | 1846.5028 | -1846.5028 | 1787.6376 | -1656.5793
0.85 | 3403.1498 | 3403.1498 | 3289.9224 | 3058.3116 | 2892.6773 | 2892.6773 | -2796.4341 | -2599.5648 | 1792.7204 | -1792.7204 | 1733.0742 | -1611.0656
0.86 | 3403.1498 | 3403.1498 | 3285.1851 | 3063.5069 | 2926.7088 | 2926.7088 | -2825.2592 | -2634.6159 | 1736.607 | -1736.607 | 1676.4104 | -1563.2893
0.87 | 3403.1498 | 3403.1498 | 3280.4478 | 3068.7023 | 2960.7403 | 2960.7403 | -2853.9896 | -2669.771 | 1677.9288 | -1677.9288 | 1617.4305 | -1513.0289
0.88 | 3403.1498 | 3403.1498 | 3275.7106 | 3073.8976 | 2994.7718 | 2994.7718 | -2882.6253 | -2705.0299 | 1616.4066 | -1616.4066 | 1555.8763 | -1460.0205
0.89 | 3403.1498 | 3403.1498 | 3270.9733 | 3079.093 | 3028.8033 | 3028.8033 | -2911.1662 | -2740.3927 | 1551.7019 | -1551.7019 | 1491.4347 | -1403.9448
0.9 | 3403.1498 | 3403.1498 | 3266.236 | 3084.2883 | 3062.8348 | 3062.8348 | -2939.6124 | -2775.8595 | 1483.3986 | -1483.3986 | 1423.7192 | -1344.4101
0.91 | 3403.1498 | 3403.1498 | 3259.4095 | 3091.2682 | 3096.8663 | 3096.8663 | -2966.0627 | -2813.0541 | 1410.974 | -1410.974 | 1351.3781 | -1281.6653
0.92 | 3403.1498 | 3403.1498 | 3252.5831 | 3098.2482 | 3130.8978 | 3130.8978 | -2992.3765 | -2850.3883 | 1333.7569 | -1333.7569 | 1274.747 | -1214.2603
0.93 | 3403.1498 | 3403.1498 | 3245.7567 | 3105.2281 | 3164.9293 | 3164.9293 | -3018.5537 | -2887.8621 | 1250.8601 | -1250.8601 | 1193.0088 | -1141.3561
0.94 | 3403.1498 | 3403.1498 | 3238.9303 | 3112.208 | 3198.9608 | 3198.9608 | -3044.5945 | -2925.4755 | 1161.0677 | -1161.0677 | 1105.0402 | -1061.8058
0.95 | 3403.1498 | 3403.1498 | 3232.1039 | 3119.1879 | 3232.9923 | 3232.9923 | -3070.4987 | -2963.2285 | 1062.6332 | -1062.6332 | 1009.2241 | -973.9661
0.96 | 3402.5198 | 3402.5198 | 3222.0263 | 3131.6935 | 3266.419 | 3266.419 | -3093.1453 | -3006.4258 | 952.7055 | -952.7055 | 902.1674 | -876.8742
0.97 | 3401.8899 | 3401.8899 | 3211.9487 | 3144.1992 | 3299.8332 | 3299.8332 | -3115.5903 | -3049.8732 | 827.0161 | -827.0161 | 780.8405 | -764.3703
0.98 | 3401.2599 | 3401.2599 | 3201.8712 | 3156.7048 | 3333.2347 | 3333.2347 | -3137.8337 | -3093.5707 | 676.8422 | -676.8422 | 637.1643 | -628.1763
0.99 | 3400.63 | 3400.63 | 3191.7936 | 3169.2104 | 3366.6237 | 3366.6237 | -3159.8756 | -3137.5183 | 479.7179 | -479.7179 | 450.2579 | -447.0721
1 | 3400 | 3400 | 3181.716 | 3181.716 | 3400 | 3400 | -3181.716 | -3181.716 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_35C_1.1pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 35 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V)* |  |  |  | 1496 |  | VDC
Nom. Battery Voltage** |  |  |  | 1296.8 |  | VDC
Min. Battery Voltage*** |  |  |  | 1164 |  | VDC |  | Please select:
AC Voltage |  |  |  | 1.1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2172 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@nom battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP @35°C, 1164Vdc min. battery voltage and 1.1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2172.0027 | 2172.0027 | 2172.0027 | 2172.0027 | 0 | 0 | 0 | 0 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.01 | 2172.0027 | 2172.0027 | 2172.0027 | 2172.0027 | 0.02172 | 0.02172 | -0.02172 | -0.02172 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.05 | 2185.2756 | 2185.2756 | 2185.2756 | 2185.2756 | 109.2638 | 109.2638 | -109.2638 | -109.2638 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.1 | 2198.5512 | 2198.5512 | 2198.5512 | 2198.5512 | 219.8551 | 219.8551 | -219.8551 | -219.8551 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.15 | 2237.4425 | 2237.4425 | 2237.4425 | 2235.6652 | 335.6164 | 335.6164 | -335.6164 | -335.3498 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.2 | 2276.3337 | 2276.3337 | 2276.3337 | 2272.7791 | 455.2667 | 455.2667 | -455.2667 | -454.5558 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.25 | 2338.3372 | 2338.3372 | 2338.3372 | 2330.9694 | 584.5843 | 584.5843 | -584.5843 | -582.7423 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.3 | 2400.3408 | 2400.3408 | 2400.3408 | 2389.1596 | 720.1022 | 720.1022 | -720.1022 | -716.7479 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.35 | 2482.0918 | 2482.0918 | 2482.0918 | 2464.2796 | 868.7321 | 868.7321 | -868.7321 | -862.4979 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.4 | 2563.8428 | 2563.8428 | 2563.8428 | 2539.3996 | 1025.5371 | 1025.5371 | -1025.5371 | -1015.7598 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.45 | 2661.8254 | 2661.8254 | 2661.8254 | 2627.3835 | 1197.8214 | 1197.8214 | -1197.8214 | -1182.3226 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.5 | 2759.8081 | 2759.8081 | 2759.8081 | 2715.3674 | 1379.9041 | 1379.9041 | -1379.9041 | -1357.6837 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.51 | 2782.0106 | 2782.0106 | 2782.0106 | 2737.2597 | 1418.8254 | 1418.8254 | -1418.8254 | -1396.0025 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.52 | 2804.2131 | 2804.2131 | 2804.2131 | 2759.152 | 1458.1908 | 1458.1908 | -1458.1908 | -1434.7591 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.53 | 2826.4155 | 2826.4155 | 2826.4155 | 2781.0444 | 1498.0002 | 1498.0002 | -1498.0002 | -1473.9535 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.54 | 2848.618 | 2848.618 | 2848.618 | 2802.9367 | 1538.2537 | 1538.2537 | -1538.2537 | -1513.5858 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.55 | 2870.8205 | 2870.8205 | 2870.8205 | 2824.829 | 1578.9513 | 1578.9513 | -1578.9513 | -1553.656 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.56 | 2893.0229 | 2893.0229 | 2893.0229 | 2846.7214 | 1620.0928 | 1620.0928 | -1620.0928 | -1594.164 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.57 | 2915.2254 | 2915.2254 | 2915.2254 | 2868.6137 | 1661.6785 | 1661.6785 | -1661.6785 | -1635.1098 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.58 | 2937.4279 | 2937.4279 | 2937.4279 | 2890.506 | 1703.7082 | 1703.7082 | -1703.7082 | -1676.4935 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.59 | 2959.6304 | 2959.6304 | 2959.6304 | 2912.3984 | 1746.1819 | 1746.1819 | -1746.1819 | -1718.315 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.6 | 2981.8328 | 2981.8328 | 2981.8328 | 2934.2907 | 1789.0997 | 1789.0997 | -1789.0997 | -1760.5744 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.61 | 3006.1031 | 3006.1031 | 3006.1031 | 2958.6028 | 1833.7229 | 1833.7229 | -1833.7229 | -1804.7477 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.62 | 3030.3733 | 3030.3733 | 3030.3733 | 2982.9148 | 1878.8314 | 1878.8314 | -1878.8314 | -1849.4072 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.63 | 3054.6435 | 3054.6435 | 3054.6435 | 3007.2269 | 1924.4254 | 1924.4254 | -1924.4254 | -1894.5529 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.64 | 3078.9138 | 3078.9138 | 3078.9138 | 3031.539 | 1970.5048 | 1970.5048 | -1970.5048 | -1940.1849 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.65 | 3103.184 | 3103.184 | 3103.184 | 3055.851 | 2017.0696 | 2017.0696 | -2017.0696 | -1986.3032 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.66 | 3127.4542 | 3127.4542 | 3127.4542 | 3080.1631 | 2064.1198 | 2064.1198 | -2064.1198 | -2032.9077 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.67 | 3151.7245 | 3151.7245 | 3151.7245 | 3104.4752 | 2111.6554 | 2111.6554 | -2111.6554 | -2079.9984 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.68 | 3175.9947 | 3175.9947 | 3175.9947 | 3128.7872 | 2159.6764 | 2159.6764 | -2159.6764 | -2127.5753 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.69 | 3200.2649 | 3200.2649 | 3200.2649 | 3153.0993 | 2208.1828 | 2208.1828 | -2208.1828 | -2175.6385 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.7 | 3224.5352 | 3224.5352 | 3224.5352 | 3177.4114 | 2257.1746 | 2257.1746 | -2257.1746 | -2224.188 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.71 | 3242.3966 | 3242.3966 | 3242.3966 | 3196.7434 | 2302.1016 | 2302.1016 | -2302.1016 | -2269.6878 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.72 | 3260.2581 | 3260.2581 | 3260.2581 | 3216.0755 | 2347.3858 | 2347.3858 | -2347.3858 | -2315.5743 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.73 | 3278.1195 | 3278.1195 | 3278.1195 | 3235.4075 | 2393.0273 | 2393.0273 | -2393.0273 | -2361.8475 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.74 | 3295.981 | 3295.981 | 3295.981 | 3254.7396 | 2439.0259 | 2439.0259 | -2439.0259 | -2408.5073 | 2172.0027 | -2172.0027 | 2172.0027 | -2172.0027
0.75 | 3313.8425 | 3313.8425 | 3313.8425 | 3274.0716 | 2485.3818 | 2485.3818 | -2485.3818 | -2455.5537 | 2172.0027 | -2172.0027 | 2172.0027 | -2165.5948
0.76 | 3331.7039 | 3331.7039 | 3331.7039 | 3293.4037 | 2532.095 | 2532.095 | -2532.095 | -2502.9868 | 2165.3512 | -2165.3512 | 2165.3512 | -2140.459
0.77 | 3349.5654 | 3349.5654 | 3349.5654 | 3312.7357 | 2579.1653 | 2579.1653 | -2579.1653 | -2550.8065 | 2137.1697 | -2137.1697 | 2137.1697 | -2113.6708
0.78 | 3367.4268 | 3367.4268 | 3367.4268 | 3321.6373 | 2626.5929 | 2626.5929 | -2626.5929 | -2590.8771 | 2107.2667 | -2107.2667 | 2107.2667 | -2078.6126
0.79 | 3385.2883 | 3385.2883 | 3385.2883 | 3328.6028 | 2674.3778 | 2674.3778 | -2674.3778 | -2629.5962 | 2075.5434 | -2075.5434 | 2075.5434 | -2040.7891
0.8 | 3403.1498 | 3403.1498 | 3403.1498 | 3335.5683 | 2722.5198 | 2722.5198 | -2722.5198 | -2668.4546 | 2041.8899 | -2041.8899 | 2041.8899 | -2001.341
0.81 | 3403.1498 | 3403.1498 | 3403.1498 | 3341.2832 | 2756.5513 | 2756.5513 | -2756.5513 | -2706.4394 | 1995.7087 | -1995.7087 | 1995.7087 | -1959.4283
0.82 | 3403.1498 | 3403.1498 | 3403.1498 | 3346.9981 | 2790.5828 | 2790.5828 | -2790.5828 | -2744.5384 | 1947.8388 | -1947.8388 | 1947.8388 | -1915.6996
0.83 | 3403.1498 | 3403.1498 | 3403.1498 | 3352.7129 | 2824.6143 | 2824.6143 | -2824.6143 | -2782.7517 | 1898.1523 | -1898.1523 | 1898.1523 | -1870.0205
0.84 | 3403.1498 | 3403.1498 | 3403.1498 | 3358.4278 | 2858.6458 | 2858.6458 | -2858.6458 | -2821.0794 | 1846.5028 | -1846.5028 | 1846.5028 | -1822.2373
0.85 | 3403.1498 | 3403.1498 | 3403.1498 | 3364.1427 | 2892.6773 | 2892.6773 | -2892.6773 | -2859.5213 | 1792.7204 | -1792.7204 | 1792.7204 | -1772.1721
0.86 | 3403.1498 | 3403.1498 | 3403.1498 | 3369.8576 | 2926.7088 | 2926.7088 | -2926.7088 | -2898.0775 | 1736.607 | -1736.607 | 1736.607 | -1719.6182
0.87 | 3403.1498 | 3403.1498 | 3403.1498 | 3375.5725 | 2960.7403 | 2960.7403 | -2960.7403 | -2936.7481 | 1677.9288 | -1677.9288 | 1677.9288 | -1664.3318
0.88 | 3403.1498 | 3403.1498 | 3403.1498 | 3381.2874 | 2994.7718 | 2994.7718 | -2994.7718 | -2975.5329 | 1616.4066 | -1616.4066 | 1616.4066 | -1606.0225
0.89 | 3403.1498 | 3403.1498 | 3403.1498 | 3387.0022 | 3028.8033 | 3028.8033 | -3028.8033 | -3014.432 | 1551.7019 | -1551.7019 | 1551.7019 | -1544.3393
0.9 | 3403.1498 | 3403.1498 | 3403.1498 | 3392.7171 | 3062.8348 | 3062.8348 | -3062.8348 | -3053.4454 | 1483.3986 | -1483.3986 | 1483.3986 | -1478.8511
0.91 | 3403.1498 | 3403.1498 | 3403.1498 | 3400.395 | 3096.8663 | 3096.8663 | -3096.8663 | -3094.3595 | 1410.974 | -1410.974 | 1410.974 | -1409.8318
0.92 | 3403.1498 | 3403.1498 | 3403.1498 | 3403.1498 | 3130.8978 | 3130.8978 | -3130.8978 | -3130.8978 | 1333.7569 | -1333.7569 | 1333.7569 | -1333.7569
0.93 | 3403.1498 | 3403.1498 | 3403.1498 | 3403.1498 | 3164.9293 | 3164.9293 | -3164.9293 | -3164.9293 | 1250.8601 | -1250.8601 | 1250.8601 | -1250.8601
0.94 | 3403.1498 | 3403.1498 | 3403.1498 | 3403.1498 | 3198.9608 | 3198.9608 | -3198.9608 | -3198.9608 | 1161.0677 | -1161.0677 | 1161.0677 | -1161.0677
0.95 | 3403.1498 | 3403.1498 | 3403.1498 | 3403.1498 | 3232.9923 | 3232.9923 | -3232.9923 | -3232.9923 | 1062.6332 | -1062.6332 | 1062.6332 | -1062.6332
0.96 | 3402.5198 | 3402.5198 | 3402.5198 | 3402.5198 | 3266.419 | 3266.419 | -3266.419 | -3266.419 | 952.7055 | -952.7055 | 952.7055 | -952.7055
0.97 | 3401.8899 | 3401.8899 | 3401.8899 | 3401.8899 | 3299.8332 | 3299.8332 | -3299.8332 | -3299.8332 | 827.0161 | -827.0161 | 827.0161 | -827.0161
0.98 | 3401.2599 | 3401.2599 | 3401.2599 | 3401.2599 | 3333.2347 | 3333.2347 | -3333.2347 | -3333.2347 | 676.8422 | -676.8422 | 676.8422 | -676.8422
0.99 | 3400.63 | 3400.63 | 3400.63 | 3400.63 | 3366.6237 | 3366.6237 | -3366.6237 | -3366.6237 | 479.7179 | -479.7179 | 479.7179 | -479.7179
1 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | -3400 | -3400 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited
* Max. battery voltage is used to determine the charging power (UE and OE)
** Nominal battery voltage is used to determine the discharging power (UE and OE) and the max. power factor for charging OE
*** Min. battery voltage is used to determine the max. power factor for discharging OE

## CATL_50C_0.9pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 50 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V) |  |  |  | 1496 |  | VDC
Min. battery voltage |  |  |  | 1164 |  | VDC |  | Please select:
AC voltage |  |  |  | 0.9 |  | pu |  | Project plant specific |  |  | VArRtg: | 2172 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@min battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP @50°C, 1164Vdc min. battery voltage and 0.9pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 1954.8019 | 1954.8016 | 1954.8019 | 1954.8016 | 0 | 0 | 0 | 0 | 1954.8019 | -1954.8016 | 1954.8019 | -1954.8016
0.01 | 1954.8019 | 1954.8016 | 1954.8019 | 1954.8016 | 0.019548 | 0.019548 | -0.019548 | -0.019548 | 1954.8019 | -1954.8016 | 1954.8019 | -1954.8016
0.05 | 1964.5427 | 1963.0034 | 1964.5427 | 1962.6374 | 98.2271 | 98.1502 | -98.2271 | -98.1319 | 1954.8019 | -1954.8016 | 1954.8019 | -1954.8016
0.1 | 1974.2853 | 1971.2068 | 1974.2853 | 1970.4748 | 197.4285 | 197.1207 | -197.4285 | -197.0475 | 1954.8019 | -1954.8016 | 1954.8019 | -1954.8016
0.15 | 2002.9528 | 1996.1217 | 2002.9528 | 1992.7141 | 300.4429 | 299.4183 | -300.4429 | -298.9071 | 1954.8019 | -1954.8016 | 1954.8019 | -1954.8016
0.2 | 2031.6203 | 2021.0366 | 2031.6203 | 2014.9535 | 406.3241 | 404.2073 | -406.3241 | -402.9907 | 1954.8019 | -1954.8016 | 1954.8019 | -1954.8016
0.25 | 2077.681 | 2063.1376 | 2077.681 | 2049.9714 | 519.4203 | 515.7844 | -519.4203 | -512.4928 | 1954.8019 | -1954.8016 | 1954.8019 | -1954.8016
0.3 | 2123.7417 | 2105.2385 | 2123.7417 | 2084.9893 | 637.1225 | 631.5715 | -637.1225 | -625.4968 | 1954.8019 | -1954.8016 | 1954.8019 | -1954.8016
0.35 | 2185.0578 | 2164.8921 | 2185.0578 | 2131.1409 | 764.7702 | 757.7122 | -764.7702 | -745.8993 | 1954.8019 | -1954.8016 | 1954.8019 | -1954.8016
0.4 | 2246.3738 | 2224.5457 | 2246.3738 | 2177.2925 | 898.5495 | 889.8183 | -898.5495 | -870.917 | 1954.8019 | -1954.8016 | 1954.8019 | -1954.8016
0.45 | 2320.604 | 2299.4049 | 2318.0984 | 2232.6371 | 1044.2718 | 1034.7322 | -1043.1443 | -1004.6867 | 1954.8019 | -1954.8016 | 1954.8019 | -1954.8016
0.5 | 2394.8342 | 2374.2642 | 2389.8229 | 2287.9817 | 1197.4171 | 1187.1321 | -1194.9115 | -1143.9909 | 1954.8019 | -1954.8016 | 1954.8019 | -1954.8016
0.51 | 2411.815 | 2393.3019 | 2405.7793 | 2297.8988 | 1230.0256 | 1220.584 | -1226.9474 | -1171.9284 | 1954.8019 | -1954.8016 | 1954.8019 | -1954.8016
0.52 | 2428.7957 | 2412.3396 | 2421.7356 | 2307.8159 | 1262.9738 | 1254.4166 | -1259.3025 | -1200.0643 | 1954.8019 | -1954.8016 | 1954.8019 | -1954.8016
0.53 | 2445.7764 | 2431.3774 | 2437.692 | 2317.733 | 1296.2615 | 1288.63 | -1291.9768 | -1228.3985 | 1954.8019 | -1954.8016 | 1954.8019 | -1954.8016
0.54 | 2462.7571 | 2450.4151 | 2453.6483 | 2327.6501 | 1329.8889 | 1323.2242 | -1324.9701 | -1256.9311 | 1954.8019 | -1954.8016 | 1954.8019 | -1954.8016
0.55 | 2479.7379 | 2469.4528 | 2469.6047 | 2337.5672 | 1363.8558 | 1358.1991 | -1358.2826 | -1285.662 | 1954.8019 | -1954.8016 | 1954.8019 | -1952.2535
0.56 | 2496.7186 | 2488.4905 | 2485.5611 | 2347.4843 | 1398.1624 | 1393.5547 | -1391.9142 | -1314.5912 | 1954.8019 | -1954.8016 | 1954.8019 | -1944.8734
0.57 | 2513.6993 | 2507.5283 | 2501.5174 | 2357.4014 | 1432.8086 | 1429.2911 | -1425.8649 | -1343.7188 | 1954.8019 | -1954.8016 | 1954.8019 | -1936.9463
0.58 | 2530.68 | 2526.566 | 2517.4738 | 2367.3185 | 1467.7944 | 1465.4083 | -1460.1348 | -1373.0447 | 1954.8019 | -1954.8016 | 1954.8019 | -1928.4566
0.59 | 2547.6607 | 2545.6037 | 2533.4301 | 2377.2356 | 1503.1198 | 1501.9062 | -1494.7238 | -1402.569 | 1954.8019 | -1954.8016 | 1954.8019 | -1919.3877
0.6 | 2564.6415 | 2564.6415 | 2549.3865 | 2387.1527 | 1538.7849 | 1538.7849 | -1529.6319 | -1432.2916 | 1954.8019 | -1954.8016 | 1954.8019 | -1909.7221
0.61 | 2583.362 | 2583.362 | 2563.503 | 2389.1429 | 1575.8508 | 1575.8508 | -1563.7368 | -1457.3772 | 1954.8019 | -1954.8016 | 1954.8019 | -1893.1602
0.62 | 2602.0825 | 2602.0825 | 2577.6194 | 2391.1331 | 1613.2911 | 1613.2911 | -1598.124 | -1482.5025 | 1954.8019 | -1954.8016 | 1954.8019 | -1876.0874
0.63 | 2620.803 | 2620.803 | 2591.7359 | 2393.1233 | 1651.1059 | 1651.1059 | -1632.7936 | -1507.6677 | 1954.8019 | -1954.8016 | 1954.8019 | -1858.4879
0.64 | 2639.5235 | 2639.5235 | 2605.8524 | 2395.1135 | 1689.295 | 1689.295 | -1667.7455 | -1532.8727 | 1954.8019 | -1954.8016 | 1954.8019 | -1840.3451
0.65 | 2658.244 | 2658.244 | 2619.9688 | 2397.1037 | 1727.8586 | 1727.8586 | -1702.9797 | -1558.1174 | 1954.8019 | -1954.8016 | 1954.8019 | -1821.6411
0.66 | 2676.9645 | 2676.9645 | 2634.0853 | 2399.0939 | 1766.7966 | 1766.7966 | -1738.4963 | -1583.402 | 1954.8019 | -1954.8016 | 1954.8019 | -1802.3567
0.67 | 2695.685 | 2695.685 | 2648.2018 | 2401.0841 | 1806.109 | 1806.109 | -1774.2952 | -1608.7264 | 1954.8019 | -1954.8016 | 1954.8019 | -1782.4715
0.68 | 2714.4056 | 2714.4056 | 2662.3183 | 2403.0744 | 1845.7958 | 1845.7958 | -1810.3764 | -1634.0906 | 1954.8019 | -1954.8016 | 1952.044 | -1761.9632
0.69 | 2733.1261 | 2733.1261 | 2676.4347 | 2405.0646 | 1885.857 | 1885.857 | -1846.74 | -1659.4946 | 1954.8019 | -1954.8016 | 1937.2285 | -1740.8083
0.7 | 2751.8466 | 2751.8466 | 2690.5512 | 2407.0548 | 1926.2926 | 1926.2926 | -1883.3858 | -1684.9383 | 1954.8019 | -1954.8016 | 1921.4379 | -1718.9809
0.71 | 2753.3558 | 2753.3558 | 2688.103 | 2409.9639 | 1954.8826 | 1954.8826 | -1908.5531 | -1711.0744 | 1938.9178 | -1938.9178 | 1892.9666 | -1697.1006
0.72 | 2754.8651 | 2754.8651 | 2685.6548 | 2412.873 | 1983.5029 | 1983.5029 | -1933.6715 | -1737.2686 | 1911.8049 | -1911.8049 | 1863.7748 | -1674.4713
0.73 | 2756.3743 | 2756.3743 | 2683.2066 | 2415.7822 | 2012.1533 | 2012.1533 | -1958.7408 | -1763.521 | 1883.8362 | -1883.8362 | 1833.8299 | -1651.0594
0.74 | 2757.8836 | 2757.8836 | 2680.7584 | 2418.6913 | 2040.8339 | 2040.8339 | -1983.7612 | -1789.8316 | 1854.9715 | -1854.9715 | 1803.0965 | -1626.8284
0.75 | 2759.3929 | 2759.3929 | 2678.3102 | 2421.6004 | 2069.5446 | 2069.5446 | -2008.7327 | -1816.2003 | 1825.1668 | -1825.1668 | 1771.5357 | -1601.7381
0.76 | 2760.9021 | 2760.9021 | 2675.8621 | 2424.5095 | 2098.2856 | 2098.2856 | -2033.6552 | -1842.6273 | 1794.374 | -1794.374 | 1739.1045 | -1575.7447
0.77 | 2762.4114 | 2762.4114 | 2673.4139 | 2427.4187 | 2127.0568 | 2127.0568 | -2058.5287 | -1869.1124 | 1762.5397 | -1762.5397 | 1705.7554 | -1548.7996
0.78 | 2763.9206 | 2763.9206 | 2670.9657 | 2430.3278 | 2155.8581 | 2155.8581 | -2083.3532 | -1895.6557 | 1729.6049 | -1729.6049 | 1671.4356 | -1520.8493
0.79 | 2765.4299 | 2765.4299 | 2668.5175 | 2433.2369 | 2184.6896 | 2184.6896 | -2108.1288 | -1922.2572 | 1695.504 | -1695.504 | 1636.0863 | -1491.8342
0.8 | 2766.9391 | 2766.9391 | 2666.0693 | 2436.1461 | 2213.5513 | 2213.5513 | -2132.8554 | -1948.9168 | 1660.1635 | -1660.1635 | 1599.6416 | -1461.6876
0.81 | 2766.9391 | 2766.9391 | 2662.3553 | 2440.672 | 2241.2207 | 2241.2207 | -2156.5078 | -1976.9443 | 1622.6158 | -1622.6158 | 1561.2847 | -1431.283
0.82 | 2766.9391 | 2766.9391 | 2658.6414 | 2445.1979 | 2268.8901 | 2268.8901 | -2180.0859 | -2005.0623 | 1583.695 | -1583.695 | 1521.7093 | -1399.5421
0.83 | 2766.9391 | 2766.9391 | 2654.9274 | 2449.7238 | 2296.5595 | 2296.5595 | -2203.5898 | -2033.2708 | 1543.2974 | -1543.2974 | 1480.8213 | -1366.3663
0.84 | 2766.9391 | 2766.9391 | 2651.2135 | 2454.2498 | 2324.2289 | 2324.2289 | -2227.0193 | -2061.5698 | 1501.3035 | -1501.3035 | 1438.5124 | -1331.6425
0.85 | 2766.9391 | 2766.9391 | 2647.4995 | 2458.7757 | 2351.8983 | 2351.8983 | -2250.3746 | -2089.9593 | 1457.5756 | -1457.5756 | 1394.6569 | -1295.2405
0.86 | 2766.9391 | 2766.9391 | 2643.7855 | 2463.3016 | 2379.5677 | 2379.5677 | -2273.6556 | -2118.4394 | 1411.9525 | -1411.9525 | 1349.108 | -1257.0081
0.87 | 2766.9391 | 2766.9391 | 2640.0716 | 2467.8276 | 2407.237 | 2407.237 | -2296.8623 | -2147.01 | 1364.2441 | -1364.2441 | 1301.6918 | -1216.7666
0.88 | 2766.9391 | 2766.9391 | 2636.3576 | 2472.3535 | 2434.9064 | 2434.9064 | -2319.9947 | -2175.6711 | 1314.2233 | -1314.2233 | 1252.2005 | -1174.3028
0.89 | 2766.9391 | 2766.9391 | 2632.6437 | 2476.8794 | 2462.5758 | 2462.5758 | -2343.0529 | -2204.4227 | 1261.615 | -1261.615 | 1200.3816 | -1129.3592
0.9 | 2766.9391 | 2766.9391 | 2628.9297 | 2481.4053 | 2490.2452 | 2490.2452 | -2366.0367 | -2233.2648 | 1206.0808 | -1206.0808 | 1145.9239 | -1081.6195
0.91 | 2766.9391 | 2766.9391 | 2622.9642 | 2487.4079 | 2517.9146 | 2517.9146 | -2386.8974 | -2263.5412 | 1147.1958 | -1147.1958 | 1087.5026 | -1031.2998
0.92 | 2766.9391 | 2766.9391 | 2616.9987 | 2493.4104 | 2545.584 | 2545.584 | -2407.6388 | -2293.9376 | 1084.4142 | -1084.4142 | 1025.6498 | -977.2133
0.93 | 2766.9391 | 2766.9391 | 2611.0331 | 2499.413 | 2573.2534 | 2573.2534 | -2428.2608 | -2324.4541 | 1017.0148 | -1017.0148 | 959.7101 | -918.683
0.94 | 2766.9391 | 2766.9391 | 2605.0676 | 2505.4156 | 2600.9228 | 2600.9228 | -2448.7635 | -2355.0906 | 944.0089 | -944.0089 | 888.7825 | -854.7838
0.95 | 2766.9391 | 2766.9391 | 2599.1021 | 2511.4181 | 2628.5922 | 2628.5922 | -2469.147 | -2385.8472 | 863.9765 | -863.9765 | 811.5694 | -784.1901
0.96 | 2766.9391 | 2766.9391 | 2592.1122 | 2521.965 | 2656.2616 | 2656.2616 | -2488.4277 | -2421.0864 | 774.743 | -774.743 | 725.7914 | -706.1502
0.97 | 2766.9391 | 2766.9391 | 2585.1223 | 2532.5119 | 2683.931 | 2683.931 | -2507.5686 | -2456.5365 | 672.6565 | -672.6565 | 628.4559 | -615.6661
0.98 | 2766.9391 | 2766.9391 | 2578.1324 | 2543.0588 | 2711.6003 | 2711.6003 | -2526.5697 | -2492.1976 | 550.6139 | -550.6139 | 513.0419 | -506.0623
0.99 | 2766.9391 | 2766.9391 | 2571.1425 | 2553.6057 | 2739.2697 | 2739.2697 | -2545.4311 | -2528.0696 | 390.3248 | -390.3248 | 362.7043 | -360.2304
1 | 2766.9391 | 2766.9391 | 2564.1526 | 2564.1526 | 2766.9391 | 2766.9391 | -2564.1526 | -2564.1526 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited

## CATL_50C_1.0pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 50 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V) |  |  |  | 1496 |  | VDC
Min. battery voltage |  |  |  | 1164 |  | VDC |  | Please select:
AC voltage |  |  |  | 1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2172 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@min battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP @50°C, 1164Vdc min. battery voltage and 1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2172.0022 | 2172.0018 | 2172.0022 | 2172.0017 | 0 | 0 | 0 | 0 | 2172.0022 | -2172.0018 | 2172.0022 | -2172.0017
0.01 | 2172.0022 | 2172.0018 | 2172.0022 | 2172.0017 | 0.02172 | 0.02172 | -0.02172 | -0.02172 | 2172.0022 | -2172.0018 | 2172.0022 | -2172.0017
0.05 | 2182.8252 | 2181.1149 | 2182.8252 | 2180.7082 | 109.1413 | 109.0557 | -109.1413 | -109.0354 | 2172.0022 | -2172.0018 | 2172.0022 | -2172.0018
0.1 | 2193.6504 | 2190.2298 | 2193.6504 | 2189.4164 | 219.365 | 219.023 | -219.365 | -218.9416 | 2172.0022 | -2172.0018 | 2172.0022 | -2172.0018
0.15 | 2225.5031 | 2217.913 | 2225.5031 | 2214.1268 | 333.8255 | 332.687 | -333.8255 | -332.119 | 2172.0022 | -2172.0018 | 2172.0022 | -2172.0018
0.2 | 2257.3559 | 2245.5963 | 2257.3559 | 2238.8372 | 451.4712 | 449.1193 | -451.4712 | -447.7674 | 2172.0022 | -2172.0018 | 2172.0022 | -2172.0018
0.25 | 2308.5344 | 2292.3751 | 2308.5344 | 2277.746 | 577.1336 | 573.0938 | -577.1336 | -569.4365 | 2172.0022 | -2172.0018 | 2172.0022 | -2172.0018
0.3 | 2359.713 | 2339.1539 | 2359.713 | 2316.6547 | 707.9139 | 701.7462 | -707.9139 | -694.9964 | 2172.0022 | -2172.0018 | 2172.0022 | -2172.0018
0.35 | 2427.842 | 2405.4356 | 2427.842 | 2367.9343 | 849.7447 | 841.9025 | -849.7447 | -828.777 | 2172.0022 | -2172.0018 | 2172.0022 | -2172.0018
0.4 | 2495.9709 | 2471.7174 | 2495.9709 | 2419.2139 | 998.3884 | 988.687 | -998.3884 | -967.6856 | 2172.0022 | -2172.0018 | 2172.0022 | -2172.0018
0.45 | 2578.4489 | 2554.8944 | 2575.6649 | 2480.7079 | 1160.302 | 1149.7025 | -1159.0492 | -1116.3186 | 2172.0022 | -2172.0018 | 2172.0022 | -2172.0018
0.5 | 2660.9269 | 2638.0713 | 2655.3588 | 2542.2019 | 1330.4635 | 1319.0357 | -1327.6794 | -1271.101 | 2172.0022 | -2172.0018 | 2172.0022 | -2172.0018
0.51 | 2679.7944 | 2659.2243 | 2673.0881 | 2553.2209 | 1366.6951 | 1356.2044 | -1363.2749 | -1302.1427 | 2172.0022 | -2172.0018 | 2172.0022 | -2172.0018
0.52 | 2698.6619 | 2680.3774 | 2690.8174 | 2564.2399 | 1403.3042 | 1393.7962 | -1399.225 | -1333.4048 | 2172.0022 | -2172.0018 | 2172.0022 | -2172.0018
0.53 | 2717.5293 | 2701.5304 | 2708.5467 | 2575.2589 | 1440.2906 | 1431.8111 | -1435.5297 | -1364.8872 | 2172.0022 | -2172.0018 | 2172.0022 | -2172.0018
0.54 | 2736.3968 | 2722.6834 | 2726.2759 | 2586.2779 | 1477.6543 | 1470.2491 | -1472.189 | -1396.5901 | 2172.0022 | -2172.0018 | 2172.0022 | -2172.0018
0.55 | 2755.2643 | 2743.8365 | 2744.0052 | 2597.2969 | 1515.3954 | 1509.1101 | -1509.2029 | -1428.5133 | 2172.0022 | -2172.0018 | 2172.0022 | -2169.1706
0.56 | 2774.1317 | 2764.9895 | 2761.7345 | 2608.3159 | 1553.5138 | 1548.3941 | -1546.5713 | -1460.6569 | 2172.0022 | -2172.0018 | 2172.0022 | -2160.9704
0.57 | 2792.9992 | 2786.1425 | 2779.4638 | 2619.3349 | 1592.0096 | 1588.1012 | -1584.2944 | -1493.0209 | 2172.0022 | -2172.0018 | 2172.0022 | -2152.1626
0.58 | 2811.8667 | 2807.2956 | 2797.1931 | 2630.3539 | 1630.8827 | 1628.2314 | -1622.372 | -1525.6052 | 2172.0022 | -2172.0018 | 2172.0022 | -2142.7296
0.59 | 2830.7342 | 2828.4486 | 2814.9224 | 2641.3729 | 1670.1332 | 1668.7847 | -1660.8042 | -1558.41 | 2172.0022 | -2172.0018 | 2172.0022 | -2132.653
0.6 | 2849.6016 | 2849.6016 | 2832.6516 | 2652.3919 | 1709.761 | 1709.761 | -1699.591 | -1591.4351 | 2172.0022 | -2172.0018 | 2172.0022 | -2121.9135
0.61 | 2870.4022 | 2870.4022 | 2848.3366 | 2654.6032 | 1750.9453 | 1750.9453 | -1737.4853 | -1619.308 | 2172.0022 | -2172.0018 | 2172.0022 | -2103.5113
0.62 | 2891.2028 | 2891.2028 | 2864.0216 | 2656.8146 | 1792.5457 | 1792.5457 | -1775.6934 | -1647.225 | 2172.0022 | -2172.0018 | 2172.0022 | -2084.5415
0.63 | 2912.0033 | 2912.0033 | 2879.7066 | 2659.0259 | 1834.5621 | 1834.5621 | -1814.2151 | -1675.1863 | 2172.0022 | -2172.0018 | 2172.0022 | -2064.9866
0.64 | 2932.8039 | 2932.8039 | 2895.3915 | 2661.2372 | 1876.9945 | 1876.9945 | -1853.0506 | -1703.1918 | 2172.0022 | -2172.0018 | 2172.0022 | -2044.8279
0.65 | 2953.6045 | 2953.6045 | 2911.0765 | 2663.4486 | 1919.8429 | 1919.8429 | -1892.1997 | -1731.2416 | 2172.0022 | -2172.0018 | 2172.0022 | -2024.0457
0.66 | 2974.405 | 2974.405 | 2926.7615 | 2665.6599 | 1963.1073 | 1963.1073 | -1931.6626 | -1759.3356 | 2172.0022 | -2172.0018 | 2172.0022 | -2002.6186
0.67 | 2995.2056 | 2995.2056 | 2942.4464 | 2667.8713 | 2006.7878 | 2006.7878 | -1971.4391 | -1787.4738 | 2172.0022 | -2172.0018 | 2172.0022 | -1980.5238
0.68 | 3016.0062 | 3016.0062 | 2958.1314 | 2670.0826 | 2050.8842 | 2050.8842 | -2011.5294 | -1815.6562 | 2172.0022 | -2172.0018 | 2168.9378 | -1957.7369
0.69 | 3036.8067 | 3036.8067 | 2973.8164 | 2672.294 | 2095.3967 | 2095.3967 | -2051.9333 | -1843.8828 | 2172.0022 | -2172.0018 | 2152.4761 | -1934.2314
0.7 | 3057.6073 | 3057.6073 | 2989.5013 | 2674.5053 | 2140.3251 | 2140.3251 | -2092.6509 | -1872.1537 | 2172.0022 | -2172.0018 | 2134.931 | -1909.9788
0.71 | 3059.2843 | 3059.2843 | 2986.7811 | 2677.7377 | 2172.0918 | 2172.0918 | -2120.6146 | -1901.1937 | 2154.3531 | -2154.3531 | 2103.2963 | -1885.6674
0.72 | 3060.9612 | 3060.9612 | 2984.0609 | 2680.97 | 2203.8921 | 2203.8921 | -2148.5239 | -1930.2984 | 2124.2277 | -2124.2277 | 2070.8609 | -1860.5237
0.73 | 3062.6382 | 3062.6382 | 2981.3407 | 2684.2024 | 2235.7259 | 2235.7259 | -2176.3787 | -1959.4678 | 2093.1513 | -2093.1513 | 2037.5888 | -1834.5105
0.74 | 3064.3151 | 3064.3151 | 2978.6205 | 2687.4348 | 2267.5932 | 2267.5932 | -2204.1792 | -1988.7017 | 2061.0794 | -2061.0794 | 2003.4406 | -1807.5871
0.75 | 3065.9921 | 3065.9921 | 2975.9003 | 2690.6671 | 2299.494 | 2299.494 | -2231.9252 | -2018.0003 | 2027.9631 | -2027.9631 | 1968.373 | -1779.709
0.76 | 3067.669 | 3067.669 | 2973.1801 | 2693.8995 | 2331.4284 | 2331.4284 | -2259.6168 | -2047.3636 | 1993.7489 | -1993.7489 | 1932.3383 | -1750.8274
0.77 | 3069.346 | 3069.346 | 2970.4598 | 2697.1319 | 2363.3964 | 2363.3964 | -2287.2541 | -2076.7915 | 1958.3774 | -1958.3774 | 1895.2837 | -1720.8885
0.78 | 3071.0229 | 3071.0229 | 2967.7396 | 2700.3642 | 2395.3979 | 2395.3979 | -2314.8369 | -2106.2841 | 1921.7832 | -1921.7832 | 1857.1507 | -1689.8326
0.79 | 3072.6999 | 3072.6999 | 2965.0194 | 2703.5966 | 2427.4329 | 2427.4329 | -2342.3653 | -2135.8413 | 1883.8933 | -1883.8933 | 1817.8737 | -1657.5936
0.8 | 3074.3768 | 3074.3768 | 2962.2992 | 2706.8289 | 2459.5014 | 2459.5014 | -2369.8394 | -2165.4632 | 1844.6261 | -1844.6261 | 1777.3795 | -1624.0974
0.81 | 3074.3768 | 3074.3768 | 2958.1726 | 2711.8578 | 2490.2452 | 2490.2452 | -2396.1198 | -2196.6048 | 1802.9064 | -1802.9064 | 1734.7608 | -1590.3144
0.82 | 3074.3768 | 3074.3768 | 2954.046 | 2716.8866 | 2520.989 | 2520.989 | -2422.3177 | -2227.847 | 1759.6611 | -1759.6611 | 1690.7881 | -1555.0468
0.83 | 3074.3768 | 3074.3768 | 2949.9193 | 2721.9154 | 2551.7328 | 2551.7328 | -2448.4331 | -2259.1898 | 1714.7748 | -1714.7748 | 1645.357 | -1518.1848
0.84 | 3074.3768 | 3074.3768 | 2945.7927 | 2726.9442 | 2582.4765 | 2582.4765 | -2474.4659 | -2290.6331 | 1668.115 | -1668.115 | 1598.3471 | -1479.6028
0.85 | 3074.3768 | 3074.3768 | 2941.6661 | 2731.973 | 2613.2203 | 2613.2203 | -2500.4162 | -2322.177 | 1619.5285 | -1619.5285 | 1549.6188 | -1439.1561
0.86 | 3074.3768 | 3074.3768 | 2937.5395 | 2737.0018 | 2643.9641 | 2643.9641 | -2526.284 | -2353.8216 | 1568.8361 | -1568.8361 | 1499.0089 | -1396.6757
0.87 | 3074.3768 | 3074.3768 | 2933.4129 | 2742.0306 | 2674.7078 | 2674.7078 | -2552.0692 | -2385.5666 | 1515.8268 | -1515.8268 | 1446.3243 | -1351.9629
0.88 | 3074.3768 | 3074.3768 | 2929.2862 | 2747.0594 | 2705.4516 | 2705.4516 | -2577.7719 | -2417.4123 | 1460.2481 | -1460.2481 | 1391.3339 | -1304.7809
0.89 | 3074.3768 | 3074.3768 | 2925.1596 | 2752.0882 | 2736.1954 | 2736.1954 | -2603.3921 | -2449.3585 | 1401.7945 | -1401.7945 | 1333.7573 | -1254.8436
0.9 | 3074.3768 | 3074.3768 | 2921.033 | 2757.117 | 2766.9391 | 2766.9391 | -2628.9297 | -2481.4053 | 1340.0898 | -1340.0898 | 1273.2488 | -1201.7995
0.91 | 3074.3768 | 3074.3768 | 2914.4046 | 2763.7866 | 2797.6829 | 2797.6829 | -2652.1082 | -2515.0458 | 1274.662 | -1274.662 | 1208.3362 | -1145.8887
0.92 | 3074.3768 | 3074.3768 | 2907.7763 | 2770.4561 | 2828.4267 | 2828.4267 | -2675.1542 | -2548.8196 | 1204.9047 | -1204.9047 | 1139.6109 | -1085.7926
0.93 | 3074.3768 | 3074.3768 | 2901.1479 | 2777.1256 | 2859.1704 | 2859.1704 | -2698.0676 | -2582.7268 | 1130.0165 | -1130.0165 | 1066.3445 | -1020.7589
0.94 | 3074.3768 | 3074.3768 | 2894.5196 | 2783.7951 | 2889.9142 | 2889.9142 | -2720.8484 | -2616.7674 | 1048.8988 | -1048.8988 | 987.5361 | -949.7597
0.95 | 3074.3768 | 3074.3768 | 2887.8912 | 2790.4646 | 2920.658 | 2920.658 | -2743.4966 | -2650.9413 | 959.9739 | -959.9739 | 901.7437 | -871.3223
0.96 | 3074.3768 | 3074.3768 | 2880.1246 | 2802.1833 | 2951.4017 | 2951.4017 | -2764.9197 | -2690.096 | 860.8255 | -860.8255 | 806.4349 | -784.6113
0.97 | 3074.3768 | 3074.3768 | 2872.3581 | 2813.9021 | 2982.1455 | 2982.1455 | -2786.1874 | -2729.4851 | 747.3961 | -747.3961 | 698.2844 | -684.0734
0.98 | 3074.3768 | 3074.3768 | 2864.5915 | 2825.6209 | 3012.8893 | 3012.8893 | -2807.2997 | -2769.1085 | 611.7933 | -611.7933 | 570.0465 | -562.2915
0.99 | 3074.3768 | 3074.3768 | 2856.825 | 2837.3397 | 3043.633 | 3043.633 | -2828.2567 | -2808.9663 | 433.6942 | -433.6942 | 403.0048 | -400.256
1 | 3074.3768 | 3074.3768 | 2849.0584 | 2849.0584 | 3074.3768 | 3074.3768 | -2849.0584 | -2849.0584 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited

## CATL_50C_1.1pu
Sunny Central Storage UP Inverter PQ Capability
SCS UP (XT) device |  |  |  | 3600 UP |  |  |  | All values on inverter terminal level!
Design temperature |  |  |  | 50 |  | °C |  | Power Factor adjustable: 0.0 UE to 0.0 OE
Installation Altitude |  |  |  | 0 … 1000 |  | m
Max. Battery Voltage (min. 1200V) |  |  |  | 1496 |  | VDC
Min. battery voltage |  |  |  | 1164 |  | VDC |  | Please select:
AC voltage |  |  |  | 1.1 |  | pu |  | Project plant specific |  |  | VArRtg: | 2172 | kVAr
PF Dis-OE (@min battery voltage) |  |  |  | 0
PF Cha-OE (@min battery voltage) |  |  |  | 0
PQ-Diagram - SCS 3600 UP @50°C, 1164Vdc min. battery voltage and 1.1pu AC voltage
| Apparent Power [kVA] |  |  |  | Active Power [kW] |  |  |  | Reactive Power [kVAR]
PF | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE | Dis-OE | Dis-UE | Cha-OE | Cha-UE
0 | 2172.0022 | 2172.0022 | 2172.0022 | 2172.0021 | 0 | 0 | 0 | 0 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0021
0.01 | 2172.0022 | 2172.0022 | 2172.0022 | 2172.0021 | 0.02172 | 0.02172 | -0.02172 | -0.02172 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0021
0.05 | 2182.8252 | 2182.8252 | 2182.8252 | 2182.706 | 109.1413 | 109.1413 | -109.1413 | -109.1353 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.1 | 2193.6504 | 2193.6504 | 2193.6504 | 2193.412 | 219.365 | 219.365 | -219.365 | -219.3412 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.15 | 2225.5031 | 2225.5031 | 2225.5031 | 2223.479 | 333.8255 | 333.8255 | -333.8255 | -333.5218 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.2 | 2257.3559 | 2257.3559 | 2257.3559 | 2253.546 | 451.4712 | 451.4712 | -451.4712 | -450.7092 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.25 | 2308.5344 | 2308.5344 | 2308.5344 | 2301.1058 | 577.1336 | 577.1336 | -577.1336 | -575.2764 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.3 | 2359.713 | 2359.713 | 2359.713 | 2348.6655 | 707.9139 | 707.9139 | -707.9139 | -704.5997 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.35 | 2427.842 | 2427.842 | 2427.842 | 2411.0079 | 849.7447 | 849.7447 | -849.7447 | -843.8528 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.4 | 2495.9709 | 2495.9709 | 2495.9709 | 2473.3503 | 998.3884 | 998.3884 | -998.3884 | -989.3401 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.45 | 2578.4489 | 2578.4489 | 2578.4489 | 2545.1097 | 1160.302 | 1160.302 | -1160.302 | -1145.2994 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.5 | 2660.9269 | 2660.9269 | 2660.9269 | 2616.8692 | 1330.4635 | 1330.4635 | -1330.4635 | -1308.4346 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.51 | 2679.7944 | 2679.7944 | 2679.7944 | 2635.4512 | 1366.6951 | 1366.6951 | -1366.6951 | -1344.0801 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.52 | 2698.6619 | 2698.6619 | 2698.6619 | 2654.0332 | 1403.3042 | 1403.3042 | -1403.3042 | -1380.0972 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.53 | 2717.5293 | 2717.5293 | 2717.5293 | 2672.6152 | 1440.2906 | 1440.2906 | -1440.2906 | -1416.486 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.54 | 2736.3968 | 2736.3968 | 2736.3968 | 2691.1972 | 1477.6543 | 1477.6543 | -1477.6543 | -1453.2465 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.55 | 2755.2643 | 2755.2643 | 2755.2643 | 2709.7792 | 1515.3954 | 1515.3954 | -1515.3954 | -1490.3785 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.56 | 2774.1317 | 2774.1317 | 2774.1317 | 2728.3612 | 1553.5138 | 1553.5138 | -1553.5138 | -1527.8823 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.57 | 2792.9992 | 2792.9992 | 2792.9992 | 2746.9432 | 1592.0096 | 1592.0096 | -1592.0096 | -1565.7576 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.58 | 2811.8667 | 2811.8667 | 2811.8667 | 2765.5252 | 1630.8827 | 1630.8827 | -1630.8827 | -1604.0046 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.59 | 2830.7342 | 2830.7342 | 2830.7342 | 2784.1072 | 1670.1332 | 1670.1332 | -1670.1332 | -1642.6232 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.6 | 2849.6016 | 2849.6016 | 2849.6016 | 2802.6892 | 1709.761 | 1709.761 | -1709.761 | -1681.6135 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.61 | 2870.4022 | 2870.4022 | 2870.4022 | 2820.085 | 1750.9453 | 1750.9453 | -1750.9453 | -1720.2519 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.62 | 2891.2028 | 2891.2028 | 2891.2028 | 2837.4809 | 1792.5457 | 1792.5457 | -1792.5457 | -1759.2381 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.63 | 2912.0033 | 2912.0033 | 2912.0033 | 2854.8767 | 1834.5621 | 1834.5621 | -1834.5621 | -1798.5723 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.64 | 2932.8039 | 2932.8039 | 2932.8039 | 2872.2726 | 1876.9945 | 1876.9945 | -1876.9945 | -1838.2545 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.65 | 2953.6045 | 2953.6045 | 2953.6045 | 2889.6684 | 1919.8429 | 1919.8429 | -1919.8429 | -1878.2845 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.66 | 2974.405 | 2974.405 | 2974.405 | 2907.0643 | 1963.1073 | 1963.1073 | -1963.1073 | -1918.6624 | 2172.0022 | -2172.0022 | 2172.0022 | -2172.0022
0.67 | 2995.2056 | 2995.2056 | 2995.2056 | 2924.4601 | 2006.7878 | 2006.7878 | -2006.7878 | -1959.3883 | 2172.0022 | -2172.0022 | 2172.0022 | -2171.0054
0.68 | 3016.0062 | 3016.0062 | 3016.0062 | 2937.0909 | 2050.8842 | 2050.8842 | -2050.8842 | -1997.2218 | 2172.0022 | -2172.0022 | 2172.0022 | -2153.5106
0.69 | 3036.8067 | 3036.8067 | 3036.8067 | 2939.5234 | 2095.3967 | 2095.3967 | -2095.3967 | -2028.2711 | 2172.0022 | -2172.0022 | 2172.0022 | -2127.6545
0.7 | 3057.6073 | 3057.6073 | 3057.6073 | 2941.9558 | 2140.3251 | 2140.3251 | -2140.3251 | -2059.3691 | 2172.0022 | -2172.0022 | 2172.0022 | -2100.9767
0.71 | 3059.2843 | 3059.2843 | 3059.2843 | 2945.5114 | 2172.0918 | 2172.0918 | -2172.0918 | -2091.3131 | 2154.3531 | -2154.3531 | 2154.3531 | -2074.2341
0.72 | 3060.9612 | 3060.9612 | 3060.9612 | 2949.067 | 2203.8921 | 2203.8921 | -2203.8921 | -2123.3283 | 2124.2277 | -2124.2277 | 2124.2277 | -2046.576
0.73 | 3062.6382 | 3062.6382 | 3062.6382 | 2952.6226 | 2235.7259 | 2235.7259 | -2235.7259 | -2155.4145 | 2093.1513 | -2093.1513 | 2093.1513 | -2017.9615
0.74 | 3064.3151 | 3064.3151 | 3064.3151 | 2956.1782 | 2267.5932 | 2267.5932 | -2267.5932 | -2187.5719 | 2061.0794 | -2061.0794 | 2061.0794 | -1988.3458
0.75 | 3065.9921 | 3065.9921 | 3065.9921 | 2959.7338 | 2299.494 | 2299.494 | -2299.494 | -2219.8004 | 2027.9631 | -2027.9631 | 2027.9631 | -1957.6799
0.76 | 3067.669 | 3067.669 | 3067.669 | 2963.2894 | 2331.4284 | 2331.4284 | -2331.4284 | -2252.1 | 1993.7489 | -1993.7489 | 1993.7489 | -1925.9102
0.77 | 3069.346 | 3069.346 | 3069.346 | 2966.845 | 2363.3964 | 2363.3964 | -2363.3964 | -2284.4707 | 1958.3774 | -1958.3774 | 1958.3774 | -1892.9773
0.78 | 3071.0229 | 3071.0229 | 3071.0229 | 2970.4006 | 2395.3979 | 2395.3979 | -2395.3979 | -2316.9125 | 1921.7832 | -1921.7832 | 1921.7832 | -1858.8159
0.79 | 3072.6999 | 3072.6999 | 3072.6999 | 2973.9562 | 2427.4329 | 2427.4329 | -2427.4329 | -2349.4254 | 1883.8933 | -1883.8933 | 1883.8933 | -1823.3529
0.8 | 3074.3768 | 3074.3768 | 3074.3768 | 2977.5118 | 2459.5014 | 2459.5014 | -2459.5014 | -2382.0095 | 1844.6261 | -1844.6261 | 1844.6261 | -1786.5071
0.81 | 3074.3768 | 3074.3768 | 3074.3768 | 2983.0435 | 2490.2452 | 2490.2452 | -2490.2452 | -2416.2653 | 1802.9064 | -1802.9064 | 1802.9064 | -1749.3459
0.82 | 3074.3768 | 3074.3768 | 3074.3768 | 2988.5752 | 2520.989 | 2520.989 | -2520.989 | -2450.6317 | 1759.6611 | -1759.6611 | 1759.6611 | -1710.5514
0.83 | 3074.3768 | 3074.3768 | 3074.3768 | 2994.1069 | 2551.7328 | 2551.7328 | -2551.7328 | -2485.1087 | 1714.7748 | -1714.7748 | 1714.7748 | -1670.0032
0.84 | 3074.3768 | 3074.3768 | 3074.3768 | 2999.6386 | 2582.4765 | 2582.4765 | -2582.4765 | -2519.6964 | 1668.115 | -1668.115 | 1668.115 | -1627.5631
0.85 | 3074.3768 | 3074.3768 | 3074.3768 | 3005.1703 | 2613.2203 | 2613.2203 | -2613.2203 | -2554.3948 | 1619.5285 | -1619.5285 | 1619.5285 | -1583.0717
0.86 | 3074.3768 | 3074.3768 | 3074.3768 | 3010.702 | 2643.9641 | 2643.9641 | -2643.9641 | -2589.2037 | 1568.8361 | -1568.8361 | 1568.8361 | -1536.3433
0.87 | 3074.3768 | 3074.3768 | 3074.3768 | 3016.2337 | 2674.7078 | 2674.7078 | -2674.7078 | -2624.1233 | 1515.8268 | -1515.8268 | 1515.8268 | -1487.1592
0.88 | 3074.3768 | 3074.3768 | 3074.3768 | 3021.7654 | 2705.4516 | 2705.4516 | -2705.4516 | -2659.1535 | 1460.2481 | -1460.2481 | 1460.2481 | -1435.259
0.89 | 3074.3768 | 3074.3768 | 3074.3768 | 3027.2971 | 2736.1954 | 2736.1954 | -2736.1954 | -2694.2944 | 1401.7945 | -1401.7945 | 1401.7945 | -1380.328
0.9 | 3074.3768 | 3074.3768 | 3074.3768 | 3032.8288 | 2766.9391 | 2766.9391 | -2766.9391 | -2729.5459 | 1340.0898 | -1340.0898 | 1340.0898 | -1321.9794
0.91 | 3074.3768 | 3074.3768 | 3074.3768 | 3040.1652 | 2797.6829 | 2797.6829 | -2797.6829 | -2766.5503 | 1274.662 | -1274.662 | 1274.662 | -1260.4776
0.92 | 3074.3768 | 3074.3768 | 3074.3768 | 3047.5017 | 2828.4267 | 2828.4267 | -2828.4267 | -2803.7015 | 1204.9047 | -1204.9047 | 1204.9047 | -1194.3718
0.93 | 3074.3768 | 3074.3768 | 3074.3768 | 3054.8381 | 2859.1704 | 2859.1704 | -2859.1704 | -2840.9994 | 1130.0165 | -1130.0165 | 1130.0165 | -1122.8348
0.94 | 3074.3768 | 3074.3768 | 3074.3768 | 3062.1746 | 2889.9142 | 2889.9142 | -2889.9142 | -2878.4441 | 1048.8988 | -1048.8988 | 1048.8988 | -1044.7357
0.95 | 3074.3768 | 3074.3768 | 3074.3768 | 3069.511 | 2920.658 | 2920.658 | -2920.658 | -2916.0355 | 959.9739 | -959.9739 | 959.9739 | -958.4545
0.96 | 3074.5014 | 3074.5014 | 3074.5014 | 3074.5014 | 2951.5214 | 2951.5214 | -2951.5214 | -2951.5214 | 860.8604 | -860.8604 | 860.8604 | -860.8604
0.97 | 3074.6261 | 3074.6261 | 3074.6261 | 3074.6261 | 2982.3873 | 2982.3873 | -2982.3873 | -2982.3873 | 747.4567 | -747.4567 | 747.4567 | -747.4567
0.98 | 3074.7507 | 3074.7507 | 3074.7507 | 3074.7507 | 3013.2557 | 3013.2557 | -3013.2557 | -3013.2557 | 611.8677 | -611.8677 | 611.8677 | -611.8677
0.99 | 3074.8754 | 3074.8754 | 3074.8754 | 3074.8754 | 3044.1266 | 3044.1266 | -3044.1266 | -3044.1266 | 433.7645 | -433.7645 | 433.7645 | -433.7645
1 | 3075 | 3075 | 3075 | 3075 | 3075 | 3075 | -3075 | -3075 | 0 | 0 | 0 | 0
Dis-OE: Discharge Overexcited |  |  |  | Overexcited (OE): +Q, +PF, Leading PF, Injecting kVAR
Dis-UE: Discharge Underexcited |  |  |  | Underexcited (UE): -Q, -PF, Lagging PF, Absorbing kVAR
Cha-OE: Charge Overexcited
Cha-UE: Charge Underexcited