Horsham Solar Farm

Steady State Grid Impact Assessment

27th January 2023

| Document Information |  |
| --- | --- |
| File Ref: | 20230127 HORSF Steady State Report F0.docx |
| Version: | Version F0 |
| Distribution: | For distribution to Ausgrid as part of connection application |

COPYRIGHT This document is copyright. Other than for the purposes and subject to the conditions prescribed under the Copyright Act 1968 (Commonwealth), no part of it may in any form or by any means (electronic, mechanical, micro-copying, photocopying, recording or otherwise) be reproduced, stored in a retrieval system or transmitted without prior written permission.

DISCLAIMER This report has been prepared for a specific purpose stated within the introduction and is not to be used for any other purpose or by any other person or corporation. ESCO Pacific Holdings Pty Ltd accepts no responsibility for any loss or damage suffered howsoever arising to any person or corporation who may use or rely on this report in contravention of the terms of this disclaimer. Due consideration has been given to appropriate legislation and documentation available at the time of preparation of the report. As these elements are liable to change over time, the report should be considered current at the time of preparation only. The document relies on information supplied by subcontractors and findings obtained during the assessment process. While due care was taken during the report preparation, ESCO Pacific Holdings Pty Ltd accepts no responsibility for any omissions that may have occurred during the assessment process.

# Revision History

| Revision | Description | Author | Review | Approval | Date |
| --- | --- | --- | --- | --- | --- |
| F0 | For submission to AEMO | Mani S | Dao V | Mervin K | 27/01/2023 |

# Defined Terms

| Term | Definition |
| --- | --- |
| AC | Alternating Current |
| AVR | Automatic Voltage Regulator |
| DC | Direct Current |
| HV | High Voltage |
| kV | Kilovolt, equivalent to 103 volts |
| LV | Low voltage |
| MVA | Megavolt-ampere, equivalent to 106 volt ampere |
| MVAr | Megavolt-ampere reactive, equivalent to 106 volt-amperes reactive |
| MW | Megawatt, equivalent to 106 watts |
| OH | Overhead Conductor |
| OLTC | Onload Tap Changing/Changers |
| ONAN | Oil Natural Air Natural cooling method |
| OOS | Out of Service |
| PCS | Power Conversion System |
| PF | Power Factor |
| POC | Point of Connection |
| PSS®E | Power System Simulator for Engineering from SIEMENS |
| pu | Per Unit |
| SLD | Single Line Diagram |
| Tx | Transformer |
| UG | Underground Cable |
| UGOH | Underground to Overhead Connection |
| VC | Voltage Control |
| VDC | Voltage Drop Control |
| Vk | Impedance Voltage |
| V1 | Positive Sequence Voltage |
| VnLL | Nominal Line to Line Voltage |
| ZS | Zone Substation |

# Generators Nomenclature

| Generator Name | Nomenclature in the report |
| --- | --- |
| HORSF | Horsham Solar Farm |
| GLWWSF | Glenrowan West Solar Farm |
| GLWSF | Glenrown Solar Farm |
| STCKHWF | Stockyard Hill Wind Farm |
| VBB | Victorian Big Battery |
| MUR1WF | Murra Warra 1 Wind Farm |
| MUR2WF | Murra Warra 2 Wind Farm |
| YTPSF | Yatpool Solar Farm |
| YNDWF | Yendon Wind Farm |
| WTNSF | Winton Solar Farm |

# Executive Summary

ESCO Pacific Holdings Pty Ltd is proposing to connect Horsham Solar Farm (HORSF) into the AEMO network in Horsham Victoria. The proposed plant will have a maximum export capacity (active power) of 118.8 MWac at PoC. The Horsham Solar Farm will be directly connected to the existing 220kV busbar in the Horsham 220/66 kV Zone Substation.

This report forms a part of the HORSF connection application to the AEMO. This report aims to assess the steady state requirements for the proposed power plant. The studies were conducted in PSS®E v34.5.1 version using the data provided in the AEMO data pack [1] . This includes thermal loadings, voltage levels, generation change and loss of line voltage fluctuations, and short circuit calculations. The studies were set up so that the HORSF was operating in a voltage droop control with a droop of 3.9% on 46.926 MVAr base and a voltage setpoint of 1.02 pu at the PoC.

The aim of the report is to:

- Provide network modelling and study execution details.

- Demonstrate the compliance of HORSF to reactive power capability requirements

- Analyze the impacts of the proposed plant on the current network

The study results shows that the Horsham Solar Farm is able to meet the automatic access standard NER clause S5.2.5.1 for reactive power capability at 35°C; thus, providing and absorbing 46.926 MVAr at the PoC which is 0.395x118.8 MWac. At 50°C, due to 10% derating in the plant MVA there is small decrease in reactive power when generating full active power at 0.9pu POC voltage. So, a negotiated access standard is requested as per section 6.1.

Furthermore, there are no thermal constraints identified under system normal and the considered contingency conditions on the network with the addition of HORSF. Overall voltage fluctuations on the network due to change in generation (i.e., cloud cover and trip of generating units) and due to loss of line contingency are within 3% (for generation change) and 5% (for generator trip and loss of line contingency). The only exception occurs at the Kiamal 220kV bus (3KIAMAL_220A) when losing the Kiamal to Redcliff 220 kV line. For this case4, the existing voltage fluctuation is above 5% i.e., 5.047% and the addition of HORSF this voltage fluctuation increases to 5.595 %. Due to the small magnitude of this exacerbation i.e., 0.55% and the long distance between HORSF and 3KIAMAL_220A bus this is deemed acceptable. This exacerbation is not expected to impact system security and the limit is slightly exceeded with and without HORSF present. In fact, Horsham is not causing the fluctuation and under slightly different network conditions the plant would likely mitigate the fluctuation rather than exacerbate it, given it stabilizes the voltage at HOTS 220 kV. No further issues have been identified in the Horsham Solar Farm and BESS steady state analysis.

Overall, the inclusion of HORSF 118.8 MWac will enhance flexibility to system operators by providing reactive power capability of +46.926 MVAr/-46.926 MVAr. Also, the plants fast acting droop capability will allow to reduce voltage steps on the network.

Table of Contents

Revision History	2

Defined Terms	3

Generators Nomenclature	4

Executive Summary	5

1	Introduction	8

1.1	Project Details	8

1.2	Site Information	9

1.3	Connection Details	9

2	Model Construction	10

2.1	Input Data	10

2.2	Horsham Solar Farm Plant Model	11

2.3	Integration of the HORSF into the Network	13

3	Generators within proximity	15

4	Study Execution	16

4.1	Monitored Elements	16

4.2	Study requirements	18

4.3	HORSF Steady State Grid Impact Assessment Summary	21

5	HORSF Plant Control Strategy and Optimistaion	22

6	Simulation Results	23

6.1	Reactive Power Capability Curve	23

6.2	Voltage Levels	25

6.2.1	Summary of Findings	25

6.2.2	Plots	26

6.3	Line and Transformer Loadings	28

6.3.1	Summary of Findings	28

6.3.2	Plots	31

6.4	Voltage Fluctuations for Change of Generation	33

6.4.1	Summary of Findings	33

6.4.2	Plots	36

6.5	Voltage fluctuations due to loss of line contingencies	38

6.5.1	Summary of Findings	38

6.5.2	Plots	41

6.6	Fault Level Analysis	43

6.6.1	HighLoad	43

7	Conclusion	44

8	References	44

9	Appendices	45

9.1.1	Appendix 1	45

9.1.2	Appendix 2	46

9.1.3	Appendix 3	51

9.1.4	Appendix4	55

9.1.5	Appendix 5	60

9.1.6	Appendix 6	64

# Introduction

## Project Details

ESCO Pacific is proposing to develop Horsham Solar Farm with maximum active power output of 118.8 MWac in Horsham Victoria connecting to Ausnet’s network. This report presents the steady state analysis consisting of the following assessments:

- Reactive power capability

- Thermal loading assessment

- Load flow and voltage analysis under system normal and N-1 conditions

- Fault level calculation for three-phase faults and single phase to ground faults.

Figure 1 Proposed location of the Horsham Solar Farm connecting to existing 220 kV bus at the 220/66 kV Horsham ZS.

## Site Information

Table 1 Site Information

| Variable | Value |
| --- | --- |
| Lot/DP | Multiple Lots |
| Address | Horsham-Lubeck Road Riverside VIC 3401 |
| LGA | Horsham Rural City Council |

## Connection Details

Table 2 Connection Details

| Variable | Value |
| --- | --- |
| NSP | Ausnet |
| Supply Area | Horsham |
| Point of Connection Voltage | 220 kV |
| Feeder Name | N/A |
| Relevant Zone Substation | Horsham 220/66 kV Terminal Station |

# Model Construction

This chapter’s emphasis is on the input data required and the methodology used to construct the network model integrated with Horsham Solar Farm. Software used for the network modelling and the analysis is PSS®E v34.5.1.

## Input Data

The network models and the steady state studies are based upon the AEMO summer high and spring low cases together with data outlined in the table below.

Table 3 Input data references

| Variable | Value | Source |
| --- | --- | --- |
| Enquiry Response | Horsham Data Pack VIC runback schemes, fault levels, breaker clearing times. | AEMO |
| PSS®E Models | High: 20210124-180000-SystemNormal.sav Low: 20210328-110152-SystemNormal.sav | AEMO |
| RUGS | VIC RUGS as specified in section 3 | AEMO |
| Inverter Plant Model | SMA SC 4200 UP | SMA |

## Horsham Solar Farm Plant Model

To conduct the steady state studies the HORSF was modelled as one aggregated generator. The graphical representation of the solar plant is shown in Figure 3. The one aggregated generator has the combined capacity of inverter plant as follows:

- 1 x aggregated generator consisting of combined 151.2 MVA

- 1 x aggregated inverter transformer accommodating 151.2 MVA

- 33kV cable reticulation system modeled as an aggregated equivalent

- 1 x 170 MVA 220/33 kV power transformer

- 2 x 5 MVAr capacitor banks located on the 33kV buses

The aggregated load flow model is shown in figure below:

Figure 1 HORSF graphical representation in PSS®E

Table 4 Aggregated HORSF generator parameters

| Description | Value |
| --- | --- |
| Mbase | 151.2 MVA |
| Pmax | 118.8 MW |
| Pmin | 0 MW |
| Pgen | 119 |
| Qmax | 46.926 |
| Qmin | -46.926 |
| Base kV | 0.63 kV |
| R Source | 0 |
| X Source | 10000.0 |
| Control Mode | N/A |

Table 5 Inverter short circuit impedances

| Description | Value | Description | Value |
| --- | --- | --- | --- |
| Positive R | 0.12 pu | Zero R | 99999 pu |
| Sub transient X | 0.74 pu | Zero X | 99999 pu |
| Transient X | 0.74 pu | Reference Angle | 0 |
| Synchronous X | 0.88 pu | Grounding R | 0 |
| Negative R | 0.12 pu | Grounding X | 0 |
| Negative X | 0.88 pu |  |  |

Table 7 Equivalent 33/0.63 kV transformer data

| Description | Value | unit |
| --- | --- | --- |
| Transformer rating | 151.2 | MVA |
| Winding 1 nominal | 33 | kV |
| Winding 2 nominal | 0.63 | kV |
| Specified R | 0.0065 | pu |
| Specified X | 0.065 | pu |
| R-Zero | 0.004878 | pu |
| X-Zero | 0.034756 | pu |
| Vector group | Dyn1 | Text |
| HV – LV winding angle | 30 | ° |
| Tap change type | Off load | Text |
| Number of taps | 5 | Qty |
| Tap changer step size | 2.5 | % |
| R1 max | 1.1 | pu |
| R1 min | 0.9 | pu |
| Tap setting (HV:LV) | 1:1 | Text |

Table 8 Equivalent 33kV cable parameters

| Description | Value | unit |
| --- | --- | --- |
| BUS 334092 to 334096 |  |  |
| Specified R | 0.001732 | pu on 100 MVA base |
| Specified X | 0.002928 | pu on 100 MVA base |
| Specified B | 0.012514 | pu on 100 MVA base |
| R-Zero | 0.007515 | pu on 100 MVA base |
| X-Zero | 0.001222 | pu on 100 MVA base |
| B-Zero | 0.012514 | pu on 100 MVA base |

Table 9 Capacitor bank parameters

| Description | Value | unit |
| --- | --- | --- |
| Capacitor – 1 | 5 | MVAr |
| Capacitor - 2 | 5 | MVAr |

Table 10 220/33 kV Grid interface main transformer data

| Description | Value | unit |
| --- | --- | --- |
| Transformer rating | 170 | MVA |
| Winding 1 nominal | 220 | kV |
| Winding 2 nominal | 33 | kV |
| Specified R | 0.003529 | pu |
| Specified X | 0.168 | pu |
| Vector group | Ynd1 | Text |
| HV – LV winding angle | 30 | ° |
| Tap change type | On load | Text |
| Number of taps | 1 | Qty |
| Tap changer step size | 1.25 | % |
| R1 max | 1.1 | pu |
| R1 min | 0.9 | pu |
| Tap setting (HV:LV) | 1:1 | Text |

## Integration of the HORSF into the Network

The Horsham Solar Farm is connected directly to the existing 220 kV busbar at Horsham 220/ 66 kV Zone Substation. In the PSS®E model this happens on the bus number 334081 (3HORSHM_220B). The figure below shows the integration of HORSF at bus number 334081 i.e., Horsham ZS 220 kV terminal.

Figure 2 Integration of HORSF into the network model at Horsham 220 kV bus at Horsham 220/66 kV ZS

# Generators within proximity

The following committed generators are identified within HORSF proximity.

Table 11 Generators within Horsham Solar Farm proximity

| Name | Shor Name |
| --- | --- |
| Glenrowan West Solar Farm | GLWWSF |
| Glenrown Solar Farm | GLWSF |
| Stockyard Hill Wind Farm | STCKHWF |
| Victorian Big Battery | VBB |
| Murra Warra 1 Wind Farm | MUR1WF |
| Murra Warra 2 Wind Farm | MUR2WF |
| Yatpool Solar Farm | YTPSF |
| Yendon Wind Farm | YNDWF |
| Winton Solar Farm | WTNSF |

Each of them is added to the high and low load snapshots as per their RUG and the steady state analysis have been with the inclusion of these generators.

# Study Execution

This chapter outlines the steady state assessment criteria and the methodology employed by the proposed generator to fulfill the criteria.

## Monitored Elements

Following network elements were monitored during the steady state analysis

Table 12 Monitored Buses

| Bus Name | PSS®E Bus Number | Comments |
| --- | --- | --- |
| 3ARAR_T_220A | 306580 | ARART 220 kV |
| 3ARAR_T_220F | 306585 | ARART 220 kV |
| 3BULGTS_220A | 316580 | BULGANA 220 kV |
| HOTS 220 KV_POC | 334081 | HORSHAM 220 kV |
| 3KIAMAL_220A | 342280 | KIAMAL 220 kV |
| 3ARAR_T_220B | 306581 | ARART 220 kV |
| 3CROWLA_220A | 321580 | CROWNLANDS 220 KV |
| 3MURRAW_220A | 355880 | MURRA WARRA 220 kV |
| 3REDCLF_220A | 364080 | RED CLIFF 220 kV |
| 3BALRAT_220A | 309080 | BALARAT 220 kV |
| 3WAUBRA_220A | 384080 | WAUBRA 220 kV |

Table 13 Monitored Branches

| Branch Name | Branch from | Branch to | Branch id | Branch Code |
| --- | --- | --- | --- | --- |
| 3BALRAT_220A - 3WAUBRA_220A | 309080 | 384080 | 1 | 3BALRAT_220A - 3WAUBRA_220A |
| 3ARAR_T_220B - 3WAUBRA_220A | 306581 | 384080 | 1 | 3ARAR_T_220B - 3WAUBRA_220A |
| 3ARAR_T_220F - 3CROWLA_220A | 306585 | 321580 | 1 | 3ARAR_T_220F - 3CROWLA_220A |
| 3BULGTS_220A - 3CROWLA_220A | 316580 | 321580 | 1 | 3BULGTS_220A - 3CROWLA_220A |
| 3BULGTS_220A - HOTS 220 KV | 316580 | 334081 | 1 | 3BULGTS_220A - HOTS 220 KV |
| 3HORSHM__66A - HOTS 220 KV | 334030 | 334081 | 1 | 3HORSHM__66A - HOTS 220 KV |
| 3HORSHM__66A - HOTS 220 KV | 334030 | 334081 | 2 | 3HORSHM__66A - HOTS 220 KV |
| HOTS 220 KV - 3MURRAW_220A | 334081 | 355880 | 1 | HOTS 220 KV - 3MURRAW_220A |
| 3KIAMAL_220A -3MURRAW_220A | 342280 | 355880 | 1 | 3KIAMAL_220A - 3MURRAW_220A |
| 3KIAMAL_220A - 3REDCLF_220A | 342280 | 364080 | 1 | 3KIAMAL_220A - 3REDCLF_220A |

## Study requirements

The steady state consists of four key components, each of which illustrate the findings of the respective part of the study:

- Plant reactive power capability

  - This criterion is based on the reactive power requirement from the automatic access standard S5.2.5.1(a) i.e. that the proposed plant should be capable of supplying or absorbing the reactive power which is at least 0.395 of its intended active power value.

- Impact on thermal network capability for standard configuration and contingency events

  - This part of the steady state analysis investigates line loading and transformer loading under network normal and N-1 conditions, with and without the proposed generator. This reveals the pre-existing issues as well as issues caused by the inclusion of the proposed generator.

- Impact on network voltage capability for standard configuration and contingency events. This part further divided into three parts

  - The first part looks at Bus voltages under system normal conditions (i.e. no line outages or other contingencies. Adding generation to a bus or a line may shift the voltage levels at that bus or surrounding buses due to the impact it has on the power flows in the area. The normal operating band of the NEM is between 0.9 p.u. voltage and 1.1 p.u. voltage. The results presented in results section will highlight the changes in relevant bus voltages due to the addition of the newly proposed generator.

  - The second part of this assessment explores voltage fluctuations for a change in the generation output. This includes voltage fluctuations due to generation output variation considering a change from 100% output to 75%, 50% and 25% with all network transformer taps locked. This also includes voltage fluctuations due to trip of the proposed plant, considering a change from 100%, 75%, 50% and 25% output to no output (plant trip) with all the network transformer taps locked. This is quantified and compared against the Table6 IEC 61000.3.7:2012 (p.33) applicable thresholds.

  - The third part of this assessment focusses on voltage stability under credible contingencies. The voltage changes due to loss of line with fixed tap load flows on the network should not be worse than the system without the proposed plant.

- The last part of the Steady State analysis investigates fault current at buses of interest. These fault levels are required to not exceed planning levels. This item is unlikely to be problematic in most instances as the contribution from inverter-based resources behind transformer and cable impedances is generally normally small compared against existing headroom.

Following table provides the summary of different test scenarios performed on Horsham Solar Farm as per the above test types in accessing the steady state analysis. The Case Reference column in the table below corresponds to the cases/contingencies being studied, For instance

- Network Normal case reference refers to the network normal conditions case. The corresponding Voltage levels test type will consider voltage levels deviation with and without HORSF as well as voltage levels to be remain within 0.9 to 1.1pu.

- ARTS-CWTS (ARARAT to CROWNLANDS) 220kV line OOS refers to the contingency where ARARAT to CROWNLANDS 2200kV line is out of service. The Contingency test type will consider line loadings with and without HORSF while that contingency is in place. The voltage fluctuation will also be measured when the network is going from network normal to that contingency. This voltage fluctuations will be assessed against with and without HORSF in service. Furthermore, during these line contingencies inter trip schemes have been placed thus tripping the required committed generators as per the contingency. These inter trip schemes have been implemented as per the provided document 2g_Western Vic Generation Fast trip Schemes and Murraylink VFRB.docx [2]

- HORSF_GenChng 100% to 75% refers to the case where generation of HORSF is changed from 100% to 75%.

- HORSF_GenTrip 75% to 0% refers to the case where HORSF is tripped while generating at 75%. The Gen Change and Gen Trip will observe voltage fluctuations before and after the event and the plant itself is required for this test to be performed.

Table 14 Case Reference and the corresponding Test Types used in HORSF SS Analysis

| Case Reference | TestType |
| --- | --- |
| Network Normal | Voltage levels |
| ARTS-WBTS-BATS (ARARAT to WAUBRA to BALLARAT) 220kV line OOS | Contingency |
| ARTS-CWTS (ARARAT to CROWNLANDS) 220kV line OOS | Contingency |
| CWTS-BGTS-HOTS (CROWNLANDS to BULGANA to HORSHAM) 220kV line OOS | Contingency |
| HOTS-MRTS-KMTS (HORSHAM to MURRAWARRA to KIAMAL) 220kV line OOS | Contingency |
| KMTS-RCTS (KIAMAL to REDCLIFF) 220kV line OOS | Contingency |
| HOTS220 - HOTS66 kV Tx OOS | Contingency |
| HORSF_GenChng 118.8MW to 89.1MW (100% to 75%) | GenChange |
| HORSF_GenChng 118.8MW to 59.4MW (100% to 50%) | GenChange |
| HORSF_GenChng 118.8MW to 29.7MW (100% to 25%) | GenChange |
| HORSF_GenTrip 118.8MW to 0MW (100% to 0%) | GenTrip |
| HORSF_GenTrip 89.1MW to 0MW (75% to 0%) | GenTrip |
| HORSF_GenTrip 59.4MW to 0MW (50% to 0%) | GenTrip |
| Network Normal High Load | Fault Levels |

## HORSF Steady State Grid Impact Assessment Summary

The table below shows the summary of steady state analysis conducted on the HORSF. The HORSF has met the steady state criteria.

Table 15 HORSF steady state grid impact assessment summary

| Assessment | Assessment criteria | Notes | Assessment results |
| --- | --- | --- | --- |
| Generator reactive power capability | Automatic access standard | Tap changers enabled | Criterion met |
| Impact on thermal network capability for standard configuration and contingency events | ≤ 100% Thermal limit; or not exacerbated by given exacerbation value from NSP where already>100% | Tap changers enabled | Criterion met |
| Impact on network voltage capability for standard configuration and contingency events | - Voltage levels between 0.9 to 1.1pu - ≤ 3% voltage fluctuations GenChange - ≤ 5% voltage fluctuations GenTrip - ≤ 5% Voltage fluctuations due to loss of line contingencies Note: Existing out of bound voltage fluctuations are not be exacerbated by a given limit provided by the NSP. | Tap changers disabled | - Criterion met - Criterion met - Criterion met - Criterion met |
| Short circuit calculation studies | ≤ Provided fault level limits |  | Criterion met |

# HORSF Plant Control Strategy and Optimistaion

To assess the steady state studies of Horsham solar farm, the following PSS®E sav cases have been used. The raw snapshots were integrated with committed generators and the HORSF SMIB model. This results in creation of HORSF_high_genon.sav and HORSF_low_genon.sav. After that HORSF is deactivated, resulting in the creation of HORSF_high_genoff.sav and HORSF_low_genoff.sav.

Table 16 PSS®E sav cases used for steady state analysis

Sav cases

HORSF_high_genon.sav

HORSF_high_genoff.sav

HORSF_Low_genon.sav

HORSF_Low_genoff.sav

Initial assessment of HORSF operating at voltage setpoint of 1.02pu in a voltage droop control mode with a droop of 3.9% on 46.926 MVAr base shows compliance in steady state analysis. No further assessment was required, therefore Horsham solar farm is operated in the above settings.

# Simulation Results

## Reactive Power Capability Curve

Based on the reactive power requirement from the automatic access standard S5.2.5.1(a),  HORSF  is required to supply and absorb at least 46.926 MVAr at the connection point (CP) for a rated active power output of 118.8 MW.

The calculation for the required reactive power is given below:

𝑄𝑝𝑜𝑐 = ±0.395 × 𝑃𝑟𝑎𝑡𝑒𝑑,𝑃𝑂𝐶 = ±0.395 × 118.8.0 = ±46.926 𝑀𝑉𝐴𝑟

To assess the reactive power capability of HORSF, active power output at inverter terminal has been incrementally increased from its minimum to 118.8 MW; and at each level of the active power generation, reactive power has been changed till it reaches the maximum and minimum capacity of the plant. This process is repeated at different voltage level 0.9pu, 1.0pu and 1.1pu. The active power and reactive power were measured at the POC, which was used as an estimate of the reactive power capability of the aggregated plant.

It is important to note that the method used here has not taken the plant controller operation into consideration which has been addressed in dynamic analysis in the connection study i.e., PPC is disabled for this study.

Figures below shows that HORSF has sufficient leading and lagging reactive power capability at all levels of active power and it is able to comply with the automatic access standard S5.2.5.1(a) for 118.8 MW active power output at the CP at an ambient temperature of 35C.

Figure 3 HORSF reactive power capability at 35°C (AAS)

Figure 4 HORSF reactive power capability at  50°C (NAS)

There will be a 10% derating in the HORSF plant MVA at 50C. The plant capability at 50C is shown in figure above and it does not comply with automatic access standard at 50C with a full active power of 118.8 MW when POC voltage is 0.9pu. There are no issues at POC voltage of 1 and 1.1pu. Therefore, a negotiated access standard is required for HORSF S5251 at 50C. Taking the above figure into consideration, above results at 50C will not impact the studies much.

## Voltage Levels

The voltage levels at buses of interest have been analysed for system normal conditions (no contingencies) with Horsham Solar Farm in service and compared to the voltage levels prior to adding the HORSF. The normal operating voltage band of each considered bus is defined as 0.9 p.u. to 1.1 p.u.

### Summary of Findings

The results for each bus before and after the inclusion of Horsham Solar Farm are listed in the tables below. There are no issues observed in the voltage levels with the addition of HORSF into the network.

#### HighLoad

| Bus Name | Voltage Level(pu) GenOFF | Voltage Level(pu) GenON |
| --- | --- | --- |
| 3ARAR_T_220A | 1.026 | 1.018 |
| 3ARAR_T_220F | 1.026 | 1.018 |
| 3BULGTS_220A | 1.026 | 1.02 |
| HOTS 220 KV_POC | 1.028 | 1.028 |
| 3KIAMAL_220A | 1.024 | 1.022 |
| 3ARAR_T_220B | 1.026 | 1.018 |
| 3CROWLA_220A | 1.025 | 1.018 |
| 3MURRAW_220A | 1.04 | 1.04 |
| 3REDCLF_220A | 1.004 | 1.004 |
| 3BALRAT_220A | 1.038 | 1.033 |
| 3WAUBRA_220A | 1.031 | 1.024 |

#### LowLoad

| Bus Name | Voltage Level(pu) GenOFF | Voltage Level(pu) GenON |
| --- | --- | --- |
| 3ARAR_T_220A | 1.033 | 1.02 |
| 3ARAR_T_220F | 1.033 | 1.02 |
| 3BULGTS_220A | 1.027 | 1.015 |
| HOTS 220 KV_POC | 1.022 | 1.021 |
| 3KIAMAL_220A | 1.009 | 1.008 |
| 3ARAR_T_220B | 1.033 | 1.02 |
| 3CROWLA_220A | 1.03 | 1.017 |
| 3MURRAW_220A | 1.04 | 1.04 |
| 3REDCLF_220A | 0.998 | 0.998 |
| 3BALRAT_220A | 1.054 | 1.047 |
| 3WAUBRA_220A | 1.043 | 1.031 |

### Plots

The scatter plots show the absolute voltage level in the reference case(s) analysed in this study.

#### HighLoad

#### LowLoad

## Line and Transformer Loadings

Line and transformer loadings in the area around Horsham have been analysed under various conditions, including relevant N-1 scenarios. For each scenario, the analysis is conducted in two cases which are with and without the inclusion of HORSF by using the GenOn and GenOff cases created earlier.

### Summary of Findings

The maximum and minimum loading levels for each contingency or case reference including network normal before and after addition of Horsham Solar Farm are listed in the tables below. The Case Reference column in the table below represents contingency or network normal and the corresponding row represents the maximum and minimum loading branch. Full results are provided in  Appendix 2.

#### HighLoad

| Case Reference | Branch Name | Max Loading(%) GenOFF | Max Loading(%) GenON | Branch Name | Min Loading(%) GenOFF | Min Loading(%) GenON |
| --- | --- | --- | --- | --- | --- | --- |
| ARTS-CWTS (ARARAT to CROWNLANDS) 220kV line OOS | 3KIAMAL_220A - 3REDCLF_220A | 35.4 | 59.53 | 3BULGTS_220A - 3CROWLA_220A | 0.66 | 0.66 |
| ARTS-WBTS-BATS (ARARAT to WAUBRA to BALLARAT) 220kV line OOS | 3KIAMAL_220A - 3REDCLF_220A | 35.21 | 59.33 | 3ARAR_T_220F - 3CROWLA_220A | 0.0 | 0.0 |
| CWTS-BGTS-HOTS (CROWNLANDS to BULGANA to HORSHAM) 220kV line OOS | 3KIAMAL_220A - 3REDCLF_220A | 35.49 | 59.63 | 3ARAR_T_220F - 3CROWLA_220A | 6.32 | 6.28 |
| HOTS-MRTS-KMTS (HORSHAM to MURRAWARRA to KIAMAL) 220kV line OOS | 3BALRAT_220A - 3WAUBRA_220A | 12.49 | 33.85 | 3KIAMAL_220A - 3REDCLF_220A | 7.13 | 7.13 |
| HOTS220 - HOTS66 kV Tx OOS | 3BALRAT_220A - 3WAUBRA_220A | 60.54 | 74.47 | 3KIAMAL_220A - 3MURRAW_220A | 32.45 | 39.81 |
| KMTS-RCTS (KIAMAL to REDCLIFF) 220kV line OOS | 3BALRAT_220A - 3WAUBRA_220A | 51.79 | 71.58 | 3KIAMAL_220A - 3MURRAW_220A | 5.18 | 5.69 |
| Network Normal | 3BALRAT_220A - 3WAUBRA_220A | 60.04 | 73.88 | 3HORSHM__66A - HOTS 220 KV | 33.78 | 35.44 |

#### LowLoad

| Case Reference | Branch Name | Max Loading(%) GenOFF | Max Loading(%) GenON | Branch Name | Min Loading(%) GenOFF | Min Loading(%) GenON |
| --- | --- | --- | --- | --- | --- | --- |
| ARTS-CWTS (ARARAT to CROWNLANDS) 220kV line OOS | 3KIAMAL_220A - 3REDCLF_220A | 43.04 | 62.44 | 3BULGTS_220A - 3CROWLA_220A | 0.52 | 0.52 |
| ARTS-WBTS-BATS (ARARAT to WAUBRA to BALLARAT) 220kV line OOS | 3KIAMAL_220A - 3REDCLF_220A | 42.96 | 62.37 | 3ARAR_T_220F - 3CROWLA_220A | 0.0 | 0.0 |
| CWTS-BGTS-HOTS (CROWNLANDS to BULGANA to HORSHAM) 220kV line OOS | 3KIAMAL_220A - 3REDCLF_220A | 43.09 | 62.48 | 3ARAR_T_220F - 3CROWLA_220A | 1.11 | 1.12 |
| HOTS-MRTS-KMTS (HORSHAM to MURRAWARRA to KIAMAL) 220kV line OOS | 3BALRAT_220A - 3WAUBRA_220A | 9.38 | 26.27 | 3HORSHM__66A - HOTS 220 KV | 11.5 | 12.49 |
| HOTS220 - HOTS66 kV Tx OOS | 3BALRAT_220A - 3WAUBRA_220A | 70.63 | 84.28 | 3KIAMAL_220A - 3MURRAW_220A | 9.45 | 13.63 |
| KMTS-RCTS (KIAMAL to REDCLIFF) 220kV line OOS | 3BALRAT_220A - 3WAUBRA_220A | 52.09 | 70.22 | 3HORSHM__66A - HOTS 220 KV | 13.89 | 15.99 |
| Network Normal | 3BALRAT_220A - 3WAUBRA_220A | 70.35 | 83.97 | 3KIAMAL_220A - 3MURRAW_220A | 9.41 | 13.54 |

### Plots

The scatter plots show the results for the line loadings with and without HORSF in service in network normal conditions.

#### HighLoad

#### LowLoad

## Voltage Fluctuations for Change of Generation

This section explores the impact of a sudden loss of generation on the bus voltages at the buses of interest. The output of Horsham Solar Farm can suddenly change due to unexpected tripping of the plant or weather-related circumstances such as a change in cloud cover. A sudden change in the output of the plant must not cause a voltage disturbance larger than 3% due to loss of generation and larger than 5% due to trip of the plant.

### Summary of Findings

The maximum and minimum voltage fluctuation for each generation change case are listed in the tables below. The Case Reference column in the table below represents generation change and the corresponding row represents the maximum and minimum voltage fluctuation busbar. Full results are provided in Appendix 3. The results show that voltage fluctuations for change of generation are within the acceptable range.

#### HighLoad

| Case Reference | Bus Name | Max Volt Fluc(%) | Bus Name | Min Volt Fluc(%) |
| --- | --- | --- | --- | --- |
| HORSF_GenChng - 118.8MW to 29.7MW (100% to 25%) | 3ARAR_T_220A | 0.695 | HOTS 220 KV_POC | -0.011 |
| HORSF_GenChng - 118.8MW to 59.4MW (100% to 50%) | 3WAUBRA_220A | 0.516 | 3MURRAW_220A | 0.0 |
| HORSF_GenChng - 118.8MW to 89.1MW (100% to 75%) | 3WAUBRA_220A | 0.267 | 3MURRAW_220A | 0.0 |
| HORSF_GenTrip - 118.8MW to 0MW (100% to 0%) | 3ARAR_T_220A | 0.787 | 3MURRAW_220A | 0.0 |
| HORSF_GenTrip - 29.7MW to 0MW (25% to 0%) | 3BULGTS_220A | 0.124 | 3MURRAW_220A | 0.0 |
| HORSF_GenTrip - 59.4MW to 0MW (50% to 0%) | 3ARAR_T_220A | 0.316 | 3MURRAW_220A | 0.0 |
| HORSF_GenTrip - 89.1MW to 0MW (75% to 0%) | 3ARAR_T_220A | 0.543 | 3MURRAW_220A | 0.0 |

#### LowLoad

| Case Reference | Bus Name | Max Volt Fluc(%) | Bus Name | Min Volt Fluc(%) |
| --- | --- | --- | --- | --- |
| HORSF_GenChng - 118.8MW to 29.7MW (100% to 25%) | 3ARAR_T_220A | 1.274 | 3MURRAW_220A | 0.0 |
| HORSF_GenChng - 118.8MW to 59.4MW (100% to 50%) | 3ARAR_T_220A | 0.868 | 3MURRAW_220A | 0.0 |
| HORSF_GenChng - 118.8MW to 89.1MW (100% to 75%) | 3ARAR_T_220A | 0.441 | 3MURRAW_220A | 0.0 |
| HORSF_GenTrip - 118.8MW to 0MW (100% to 0%) | 3ARAR_T_220A | 1.698 | 3MURRAW_220A | 0.0 |
| HORSF_GenTrip - 29.7MW to 0MW (25% to 0%) | 3ARAR_T_220A | 0.392 | 3MURRAW_220A | 0.0 |
| HORSF_GenTrip - 59.4MW to 0MW (50% to 0%) | 3ARAR_T_220A | 0.798 | 3MURRAW_220A | 0.0 |
| HORSF_GenTrip - 89.1MW to 0MW (75% to 0%) | 3ARAR_T_220A | 1.227 | 3MURRAW_220A | 0.0 |

### Plots

The scatter plots shows the voltage profile of the network during loss of generation events prior and after connecting the proposed plant.

#### HighLoad

#### LowLoad

## Voltage fluctuations due to loss of line contingencies

This section explores voltage fluctuations at the buses of interest due to loss of line contingencies. These voltage fluctuations are than compared with the existing voltage fluctuations i.e. prior connecting the proposed plant. The voltage fluctuations should not be above 5% or should not exacerbate by a value provided by the NSP.

### Summary of Findings

The maximum and minimum voltage fluctuation for each bus under the given scenarios are listed in the tables below. Full results are provided in Appendix4.

The results show that with the inclusion of HORSF, the voltage fluctuations are within the acceptable range in most of the credible contingency scenarios except at the Kiamal 220kV bus (3KIAMAL_220A) due to loss of Kiamal to Redcliff 220 kV line. The existing voltage fluctuation is 5.047 % and with the addition of HORSF the voltage fluctuation exceeds to 5.595 %. Due to the small magnitude of this exacerbation i.e., 0.55% and the long distance between HORSF and 3KIAMAL_220A bus this is deemed acceptable. This exacerbation is not expected to impact system security and the limit is slightly exceeded with and without HORSF present. In fact, Horsham is not causing the fluctuation and under slightly different network conditions the plant would likely mitigate the fluctuation rather than exacerbate it, given it stabilizes the voltage at HOTS 220 kV.

There are no other voltage fluctuation issues.

Table 17 Voltage fluctuation above 5% in high load scenario

| Case Reference | Bus Name | Voltage Level(pu) GenON | Volt Fluc(%) GenON | Voltage Level(pu) GenOFF | Volt Fluc(%) GenOFF |
| --- | --- | --- | --- | --- | --- |
| KMTS-RCTS (KIAMAL to REDCLIFF) 220kV line OOS | 3KIAMAL_220A | 1.078 | 5.595 | 1.075 | 5.047 |

#### HighLoad

| Case Reference | Bus Name | Max Volt Fluc(%) GenON | Max Volt Fluc(%) GenOFF | Bus Name | Min Volt Fluc(%) GenON | Min Volt Fluc(%) GenOFF |
| --- | --- | --- | --- | --- | --- | --- |
| ARTS-CWTS (ARARAT to CROWNLANDS) 220kV line OOS | 3ARAR_T_220A | 3.238 | 2.548 | 3KIAMAL_220A | -0.063 | 0.257 |
| ARTS-WBTS-BATS (ARARAT to WAUBRA to BALLARAT) 220kV line OOS | 3ARAR_T_220A | 2.082 | 1.217 | 3KIAMAL_220A | -0.053 | 0.263 |
| CWTS-BGTS-HOTS (CROWNLANDS to BULGANA to HORSHAM) 220kV line OOS | 3ARAR_T_220A | 1.949 | 1.238 | 3KIAMAL_220A | -0.068 | 0.255 |
| HOTS-MRTS-KMTS (HORSHAM to MURRAWARRA to KIAMAL) 220kV line OOS | 3ARAR_T_220A | 1.661 | 0.968 | HOTS 220 KV_POC | -0.066 | -0.5 |
| HOTS220 - HOTS66 kV Tx OOS | 3MURRAW_220A | 0.0 | 0.0 | 3BULGTS_220A | -0.057 | -0.028 |
| KMTS-RCTS (KIAMAL to REDCLIFF) 220kV line OOS | 3KIAMAL_220A | 5.595 | 5.047 | 3MURRAW_220A | 0.0 | 0.0 |
| Network Normal | 3KIAMAL_220A | 0.0 | 0.0 | 3ARAR_T_220A | -0.001 | 0.0 |

#### LowLoad

| Case Reference | Bus Name | Max Volt Fluc(%) GenON | Max Volt Fluc(%) GenOFF | Bus Name | Min Volt Fluc(%) GenON | Min Volt Fluc(%) GenOFF |
| --- | --- | --- | --- | --- | --- | --- |
| ARTS-CWTS (ARARAT to CROWNLANDS) 220kV line OOS | 3ARAR_T_220A | 3.417 | 2.422 | 3MURRAW_220A | -3.0 | -3.0 |
| ARTS-WBTS-BATS (ARARAT to WAUBRA to BALLARAT) 220kV line OOS | 3BALRAT_220A | 1.789 | 1.377 | 3MURRAW_220A | -3.0 | -3.0 |
| CWTS-BGTS-HOTS (CROWNLANDS to BULGANA to HORSHAM) 220kV line OOS | 3CROWLA_220A | 3.099 | 2.148 | 3MURRAW_220A | -3.0 | -3.0 |
| HOTS-MRTS-KMTS (HORSHAM to MURRAWARRA to KIAMAL) 220kV line OOS | 3BULGTS_220A | 3.654 | 1.631 | 3KIAMAL_220A | -2.186 | -2.346 |
| HOTS220 - HOTS66 kV Tx OOS | 3MURRAW_220A | 0.0 | 0.0 | 3BULGTS_220A | -0.055 | -0.024 |
| KMTS-RCTS (KIAMAL to REDCLIFF) 220kV line OOS | 3WAUBRA_220A | 1.382 | 0.696 | 3MURRAW_220A | -3.0 | -3.0 |
| Network Normal | 3KIAMAL_220A | -0.0 | 0.0 | HOTS 220 KV_POC | -0.028 | 0.0 |

### Plots

The scatter plots shows the summary of voltage fluctuations due to loss of line contingencies.

#### HighLoad

#### LowLoad

## Fault Level Analysis

The fault levels were calculated using the IEC 60909 fault calculation function in PSS®E for both 3 phase and phase to ground faults. The short circuit current studies have been performed on the maximum load case. Following table shows the fault levels on the monitored buses.

### HighLoad

| Bus Name | Bus No | 1ph Fault (MVA) GenOff | 1ph Fault (MVA) GenON | 3ph Fault (MVA) GenOFF | 3ph Fault (MVA) GenON |
| --- | --- | --- | --- | --- | --- |
| 3ARAR_T_220A | 306580 | 1842.52 | 1905.96 | 2026.92 | 2165.86 |
| 3ARAR_T_220F | 306585 | 1842.52 | 1905.96 | 2026.92 | 2165.86 |
| 3BULGTS_220A | 316580 | 1478.27 | 1544.49 | 1811.74 | 1989.03 |
| HOTS 220 KV_POC | 334081 | 1508.79 | 1694.21 | 1714.31 | 2147.11 |
| 3KIAMAL_220A | 342280 | 1921 | 1946.56 | 2068.36 | 2119.36 |
| 3ARAR_T_220B | 306581 | 1842.52 | 1905.96 | 2026.92 | 2165.86 |
| 3CROWLA_220A | 321580 | 1678.18 | 1740.95 | 1936.51 | 2087.26 |
| 3MURRAW_220A | 355880 | 1287.3 | 1365.62 | 1861.07 | 2146.64 |
| 3REDCLF_220A | 364080 | 2633.95 | 2649.29 | 2013.96 | 2032.9 |
| 3BALRAT_220A | 309080 | 4761.56 | 4805.6 | 4750.17 | 4830.4 |
| 3WAUBRA_220A | 384080 | 2607.65 | 2656.54 | 2799.76 | 2901.11 |

# Conclusion

Steady state study has been caried out with consideration of various test scenarios for different assessments including voltage levels and thermal loading assessments, and the results show that no issues have been identified in these assessments. In addition, the inclusion of HORSF provides a reactive power support of +-46.926 MVA to enhance the stability and controllability of the existing network.

In summary, Horsham solar farm will improve the network with respect to voltage stability and the plant operation will be in voltage droop control mode with 3.9% droop on 46.926 MVAr and a voltage setpoint of 1.02pu.

# References

| [1] | AEMO, "Horsham Data Pack and VIC runback schemes, fault levels, breaker clearing times". |
| --- | --- |
| [2] | AEMO, 2g_Western Vic Generation Fast trip Schemes and Murraylink VFRB, VIC: AEMO, 2020. |

# Appendices

This section provides the detailed results where applicable for the assessments performed in this steady state analysis.

### Appendix 1

The voltage levels for all the monitored buses as per section 6.2

#### HighLoad

| Bus Name | Voltage Level(pu) GenOFF | Voltage Level(pu) GenON |
| --- | --- | --- |
| 3ARAR_T_220A | 1.026 | 1.018 |
| 3ARAR_T_220F | 1.026 | 1.018 |
| 3BULGTS_220A | 1.026 | 1.02 |
| HOTS 220 KV_POC | 1.028 | 1.028 |
| 3KIAMAL_220A | 1.024 | 1.022 |
| 3ARAR_T_220B | 1.026 | 1.018 |
| 3CROWLA_220A | 1.025 | 1.018 |
| 3MURRAW_220A | 1.04 | 1.04 |
| 3REDCLF_220A | 1.004 | 1.004 |
| 3BALRAT_220A | 1.038 | 1.033 |
| 3WAUBRA_220A | 1.031 | 1.024 |

#### LowLoad

| Bus Name | Voltage Level(pu) GenOFF | Voltage Level(pu) GenON |
| --- | --- | --- |
| 3ARAR_T_220A | 1.033 | 1.02 |
| 3ARAR_T_220F | 1.033 | 1.02 |
| 3BULGTS_220A | 1.027 | 1.015 |
| HOTS 220 KV_POC | 1.022 | 1.021 |
| 3KIAMAL_220A | 1.009 | 1.008 |
| 3ARAR_T_220B | 1.033 | 1.02 |
| 3CROWLA_220A | 1.03 | 1.017 |
| 3MURRAW_220A | 1.04 | 1.04 |
| 3REDCLF_220A | 0.998 | 0.998 |
| 3BALRAT_220A | 1.054 | 1.047 |
| 3WAUBRA_220A | 1.043 | 1.031 |

### Appendix 2

The thermal loadings for all the monitored branches in network normal and N-1 contingencies as per section 6.3.

#### HighLoad

|  |  | max |  |
| --- | --- | --- | --- |
| Case Reference | Branch Name | Loading(%) GenOFF | Loading(%) GenON |
| ARTS-CWTS (ARARAT to CROWNLANDS) 220kV line OOS | 3ARAR_T_220B - 3WAUBRA_220A | 9.98 | 9.98 |
|  | 3BALRAT_220A - 3WAUBRA_220A | 12.72 | 12.72 |
|  | 3BULGTS_220A - 3CROWLA_220A | 0.66 | 0.66 |
|  | 3BULGTS_220A - HOTS 220 KV | 0.66 | 0.66 |
|  | 3HORSHM__66A - HOTS 220 KV | 34.1 | 40.11 |
|  | 3KIAMAL_220A - 3MURRAW_220A | 25.34 | 45.86 |
|  | 3KIAMAL_220A - 3REDCLF_220A | 35.4 | 59.53 |
|  | HOTS 220 KV - 3MURRAW_220A | 23.27 | 12.95 |
| ARTS-WBTS-BATS (ARARAT to WAUBRA to BALLARAT) 220kV line OOS | 3ARAR_T_220F - 3CROWLA_220A | 0.0 | 0.0 |
|  | 3BULGTS_220A - 3CROWLA_220A | 1.01 | 1.01 |
|  | 3BULGTS_220A - HOTS 220 KV | 1.02 | 1.02 |
|  | 3HORSHM__66A - HOTS 220 KV | 34.39 | 40.46 |
|  | 3KIAMAL_220A - 3MURRAW_220A | 25.18 | 45.69 |
|  | 3KIAMAL_220A - 3REDCLF_220A | 35.21 | 59.33 |
|  | HOTS 220 KV - 3MURRAW_220A | 23.42 | 12.62 |
| CWTS-BGTS-HOTS (CROWNLANDS to BULGANA to HORSHAM) 220kV line OOS | 3ARAR_T_220B - 3WAUBRA_220A | 15.85 | 15.83 |
|  | 3ARAR_T_220F - 3CROWLA_220A | 6.32 | 6.28 |
|  | 3BALRAT_220A - 3WAUBRA_220A | 18.28 | 18.27 |
|  | 3HORSHM__66A - HOTS 220 KV | 33.97 | 39.95 |
|  | 3KIAMAL_220A - 3MURRAW_220A | 25.42 | 45.94 |
|  | 3KIAMAL_220A - 3REDCLF_220A | 35.49 | 59.63 |
|  | HOTS 220 KV - 3MURRAW_220A | 24.07 | 15.24 |
| HOTS-MRTS-KMTS (HORSHAM to MURRAWARRA to KIAMAL) 220kV line OOS | 3ARAR_T_220B - 3WAUBRA_220A | 10.5 | 31.02 |
|  | 3ARAR_T_220F - 3CROWLA_220A | 4.08 | 21.0 |
|  | 3BALRAT_220A - 3WAUBRA_220A | 12.49 | 33.85 |
|  | 3BULGTS_220A - 3CROWLA_220A | 6.02 | 15.67 |
|  | 3BULGTS_220A - HOTS 220 KV | 12.48 | 9.61 |
|  | 3HORSHM__66A - HOTS 220 KV | 29.55 | 31.25 |
|  | 3KIAMAL_220A - 3REDCLF_220A | 7.13 | 7.13 |
| HOTS220 - HOTS66 kV Tx OOS | 3ARAR_T_220B - 3WAUBRA_220A | 57.64 | 71.43 |
|  | 3ARAR_T_220F - 3CROWLA_220A | 47.49 | 61.24 |
|  | 3BALRAT_220A - 3WAUBRA_220A | 60.54 | 74.47 |
|  | 3BULGTS_220A - 3CROWLA_220A | 42.72 | 56.83 |
|  | 3BULGTS_220A - HOTS 220 KV | 36.54 | 50.79 |
|  | 3HORSHM__66A - HOTS 220 KV | 65.94 | 69.03 |
|  | 3KIAMAL_220A - 3MURRAW_220A | 32.45 | 39.81 |
|  | 3KIAMAL_220A - 3REDCLF_220A | 43.81 | 52.52 |
|  | HOTS 220 KV - 3MURRAW_220A | 75.0 | 64.91 |
| KMTS-RCTS (KIAMAL to REDCLIFF) 220kV line OOS | 3ARAR_T_220B - 3WAUBRA_220A | 48.57 | 68.68 |
|  | 3ARAR_T_220F - 3CROWLA_220A | 38.45 | 58.5 |
|  | 3BALRAT_220A - 3WAUBRA_220A | 51.79 | 71.58 |
|  | 3BULGTS_220A - 3CROWLA_220A | 33.55 | 54.01 |
|  | 3BULGTS_220A - HOTS 220 KV | 27.32 | 47.96 |
|  | 3HORSHM__66A - HOTS 220 KV | 33.03 | 35.29 |
|  | 3KIAMAL_220A - 3MURRAW_220A | 5.18 | 5.69 |
|  | HOTS 220 KV - 3MURRAW_220A | 61.58 | 61.56 |
| Network Normal | 3ARAR_T_220B - 3WAUBRA_220A | 57.07 | 70.87 |
|  | 3ARAR_T_220F - 3CROWLA_220A | 46.93 | 60.68 |
|  | 3BALRAT_220A - 3WAUBRA_220A | 60.04 | 73.88 |
|  | 3BULGTS_220A - 3CROWLA_220A | 42.15 | 56.25 |
|  | 3BULGTS_220A - HOTS 220 KV | 35.97 | 50.21 |
|  | 3HORSHM__66A - HOTS 220 KV | 33.89 | 35.55 |
|  | 3KIAMAL_220A - 3MURRAW_220A | 32.24 | 39.56 |
|  | 3KIAMAL_220A - 3REDCLF_220A | 43.56 | 52.23 |
|  | HOTS 220 KV - 3MURRAW_220A | 75.31 | 65.24 |

#### LowLoad

| Case Reference | Branch Name | Loading(%) GenOFF | Loading(%) GenON |
| --- | --- | --- | --- |
| ARTS-CWTS (ARARAT to CROWNLANDS) 220kV line OOS | 3ARAR_T_220B - 3WAUBRA_220A | 4.37 | 4.37 |
|  | 3BALRAT_220A - 3WAUBRA_220A | 6.51 | 6.52 |
|  | 3BULGTS_220A - 3CROWLA_220A | 0.52 | 0.52 |
|  | 3BULGTS_220A - HOTS 220 KV | 0.52 | 0.52 |
|  | 3HORSHM__66A - HOTS 220 KV | 26.14 | 33.03 |
|  | 3KIAMAL_220A - 3MURRAW_220A | 26.82 | 45.92 |
|  | 3KIAMAL_220A - 3REDCLF_220A | 43.04 | 62.44 |
|  | HOTS 220 KV - 3MURRAW_220A | 11.86 | 7.2 |
| ARTS-WBTS-BATS (ARARAT to WAUBRA to BALLARAT) 220kV line OOS | 3ARAR_T_220F - 3CROWLA_220A | 0.0 | 0.0 |
|  | 3BULGTS_220A - 3CROWLA_220A | 0.8 | 0.8 |
|  | 3BULGTS_220A - HOTS 220 KV | 0.8 | 0.81 |
|  | 3HORSHM__66A - HOTS 220 KV | 26.29 | 33.19 |
|  | 3KIAMAL_220A - 3MURRAW_220A | 26.74 | 45.85 |
|  | 3KIAMAL_220A - 3REDCLF_220A | 42.96 | 62.37 |
|  | HOTS 220 KV - 3MURRAW_220A | 11.96 | 7.14 |
| CWTS-BGTS-HOTS (CROWNLANDS to BULGANA to HORSHAM) 220kV line OOS | 3ARAR_T_220B - 3WAUBRA_220A | 5.37 | 5.38 |
|  | 3ARAR_T_220F - 3CROWLA_220A | 1.11 | 1.12 |
|  | 3BALRAT_220A - 3WAUBRA_220A | 7.33 | 7.35 |
|  | 3HORSHM__66A - HOTS 220 KV | 26.08 | 32.96 |
|  | 3KIAMAL_220A - 3MURRAW_220A | 26.86 | 45.96 |
|  | 3KIAMAL_220A - 3REDCLF_220A | 43.09 | 62.48 |
|  | HOTS 220 KV - 3MURRAW_220A | 11.62 | 7.35 |
| HOTS-MRTS-KMTS (HORSHAM to MURRAWARRA to KIAMAL) 220kV line OOS | 3ARAR_T_220B - 3WAUBRA_220A | 8.1 | 20.19 |
|  | 3ARAR_T_220F - 3CROWLA_220A | 4.54 | 16.73 |
|  | 3BALRAT_220A - 3WAUBRA_220A | 9.38 | 26.27 |
|  | 3BULGTS_220A - 3CROWLA_220A | 3.99 | 16.53 |
|  | 3BULGTS_220A - HOTS 220 KV | 6.14 | 17.08 |
|  | 3HORSHM__66A - HOTS 220 KV | 11.54 | 12.53 |
|  | 3KIAMAL_220A - 3REDCLF_220A | 17.26 | 17.08 |
| HOTS220 - HOTS66 kV Tx OOS | 3ARAR_T_220B - 3WAUBRA_220A | 57.96 | 68.95 |
|  | 3ARAR_T_220F - 3CROWLA_220A | 57.5 | 68.43 |
|  | 3BALRAT_220A - 3WAUBRA_220A | 70.63 | 84.28 |
|  | 3BULGTS_220A - 3CROWLA_220A | 57.04 | 68.04 |
|  | 3BULGTS_220A - HOTS 220 KV | 56.95 | 68.22 |
|  | 3HORSHM__66A - HOTS 220 KV | 31.29 | 34.55 |
|  | 3KIAMAL_220A - 3MURRAW_220A | 9.45 | 13.63 |
|  | 3KIAMAL_220A - 3REDCLF_220A | 20.23 | 27.21 |
|  | HOTS 220 KV - 3MURRAW_220A | 72.55 | 66.16 |
| KMTS-RCTS (KIAMAL to REDCLIFF) 220kV line OOS | 3ARAR_T_220B - 3WAUBRA_220A | 41.43 | 57.51 |
|  | 3ARAR_T_220F - 3CROWLA_220A | 40.92 | 57.15 |
|  | 3BALRAT_220A - 3WAUBRA_220A | 52.09 | 70.22 |
|  | 3BULGTS_220A - 3CROWLA_220A | 40.43 | 56.6 |
|  | 3BULGTS_220A - HOTS 220 KV | 40.47 | 56.98 |
|  | 3HORSHM__66A - HOTS 220 KV | 13.93 | 16.04 |
|  | 3KIAMAL_220A - 3MURRAW_220A | 17.21 | 17.04 |
|  | HOTS 220 KV - 3MURRAW_220A | 52.22 | 52.3 |
| Network Normal | 3ARAR_T_220B - 3WAUBRA_220A | 57.73 | 68.71 |
|  | 3ARAR_T_220F - 3CROWLA_220A | 57.28 | 68.19 |
|  | 3BALRAT_220A - 3WAUBRA_220A | 70.35 | 83.97 |
|  | 3BULGTS_220A - 3CROWLA_220A | 56.82 | 67.8 |
|  | 3BULGTS_220A - HOTS 220 KV | 56.73 | 67.98 |
|  | 3HORSHM__66A - HOTS 220 KV | 16.39 | 18.11 |
|  | 3KIAMAL_220A - 3MURRAW_220A | 9.41 | 13.54 |
|  | 3KIAMAL_220A - 3REDCLF_220A | 20.12 | 27.08 |
|  | HOTS 220 KV - 3MURRAW_220A | 72.65 | 66.28 |

### Appendix 3

The voltage fluctuations due to change in generation output on all the monitored buses as per section 6.4.

#### HighLoad

|  |  | max |  |  |
| --- | --- | --- | --- | --- |
| Case Reference | Bus Name | Volt Fluc(%) | Voltage Level(pu) After | Voltage Level(pu) Prior |
| HORSF_GenChng - 118.8MW to 29.7MW (100% to 25%) | 3ARAR_T_220A | 0.695 | 1.025 | 1.018 |
|  | 3ARAR_T_220B | 0.695 | 1.025 | 1.018 |
|  | 3ARAR_T_220F | 0.695 | 1.025 | 1.018 |
|  | 3BALRAT_220A | 0.481 | 1.038 | 1.033 |
|  | 3BULGTS_220A | 0.603 | 1.026 | 1.02 |
|  | 3CROWLA_220A | 0.654 | 1.025 | 1.018 |
|  | 3KIAMAL_220A | 0.263 | 1.025 | 1.022 |
|  | 3MURRAW_220A | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 1.004 | 1.004 |
|  | 3WAUBRA_220A | 0.686 | 1.031 | 1.024 |
|  | HOTS 220 KV_POC | -0.011 | 1.027 | 1.028 |
| HORSF_GenChng - 118.8MW to 59.4MW (100% to 50%) | 3ARAR_T_220A | 0.509 | 1.023 | 1.018 |
|  | 3ARAR_T_220B | 0.509 | 1.023 | 1.018 |
|  | 3ARAR_T_220F | 0.509 | 1.023 | 1.018 |
|  | 3BALRAT_220A | 0.358 | 1.037 | 1.033 |
|  | 3BULGTS_220A | 0.44 | 1.024 | 1.02 |
|  | 3CROWLA_220A | 0.478 | 1.023 | 1.018 |
|  | 3KIAMAL_220A | 0.18 | 1.024 | 1.022 |
|  | 3MURRAW_220A | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 1.004 | 1.004 |
|  | 3WAUBRA_220A | 0.516 | 1.029 | 1.024 |
|  | HOTS 220 KV_POC | 0.003 | 1.028 | 1.028 |
| HORSF_GenChng - 118.8MW to 89.1MW (100% to 75%) | 3ARAR_T_220A | 0.264 | 1.021 | 1.018 |
|  | 3ARAR_T_220B | 0.264 | 1.021 | 1.018 |
|  | 3ARAR_T_220F | 0.264 | 1.021 | 1.018 |
|  | 3BALRAT_220A | 0.185 | 1.035 | 1.033 |
|  | 3BULGTS_220A | 0.229 | 1.022 | 1.02 |
|  | 3CROWLA_220A | 0.248 | 1.021 | 1.018 |
|  | 3KIAMAL_220A | 0.093 | 1.023 | 1.022 |
|  | 3MURRAW_220A | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 1.004 | 1.004 |
|  | 3WAUBRA_220A | 0.267 | 1.027 | 1.024 |
|  | HOTS 220 KV_POC | 0.004 | 1.028 | 1.028 |
| HORSF_GenTrip - 118.8MW to 0MW (100% to 0%) | 3ARAR_T_220A | 0.787 | 1.026 | 1.018 |
|  | 3ARAR_T_220B | 0.787 | 1.026 | 1.018 |
|  | 3ARAR_T_220F | 0.787 | 1.026 | 1.018 |
|  | 3BALRAT_220A | 0.516 | 1.038 | 1.033 |
|  | 3BULGTS_220A | 0.718 | 1.027 | 1.02 |
|  | 3CROWLA_220A | 0.755 | 1.026 | 1.018 |
|  | 3KIAMAL_220A | 0.341 | 1.025 | 1.022 |
|  | 3MURRAW_220A | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 1.004 | 1.004 |
|  | 3WAUBRA_220A | 0.686 | 1.031 | 1.024 |
|  | HOTS 220 KV_POC | 0.05 | 1.028 | 1.028 |
| HORSF_GenTrip - 29.7MW to 0MW (25% to 0%) | 3ARAR_T_220A | 0.104 | 1.026 | 1.025 |
|  | 3ARAR_T_220B | 0.104 | 1.026 | 1.025 |
|  | 3ARAR_T_220F | 0.104 | 1.026 | 1.025 |
|  | 3BALRAT_220A | 0.045 | 1.038 | 1.037 |
|  | 3BULGTS_220A | 0.124 | 1.026 | 1.025 |
|  | 3CROWLA_220A | 0.111 | 1.026 | 1.024 |
|  | 3KIAMAL_220A | 0.078 | 1.025 | 1.024 |
|  | 3MURRAW_220A | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 1.004 | 1.004 |
|  | 3WAUBRA_220A | 0.016 | 1.031 | 1.031 |
|  | HOTS 220 KV_POC | 0.065 | 1.028 | 1.027 |
| HORSF_GenTrip - 59.4MW to 0MW (50% to 0%) | 3ARAR_T_220A | 0.316 | 1.026 | 1.023 |
|  | 3ARAR_T_220B | 0.316 | 1.026 | 1.023 |
|  | 3ARAR_T_220F | 0.316 | 1.026 | 1.023 |
|  | 3BALRAT_220A | 0.192 | 1.038 | 1.036 |
|  | 3BULGTS_220A | 0.306 | 1.026 | 1.023 |
|  | 3CROWLA_220A | 0.31 | 1.026 | 1.023 |
|  | 3KIAMAL_220A | 0.161 | 1.025 | 1.023 |
|  | 3MURRAW_220A | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 1.004 | 1.004 |
|  | 3WAUBRA_220A | 0.225 | 1.031 | 1.029 |
|  | HOTS 220 KV_POC | 0.055 | 1.028 | 1.027 |
| HORSF_GenTrip - 89.1MW to 0MW (75% to 0%) | 3ARAR_T_220A | 0.543 | 1.026 | 1.021 |
|  | 3ARAR_T_220B | 0.543 | 1.026 | 1.021 |
|  | 3ARAR_T_220F | 0.543 | 1.026 | 1.021 |
|  | 3BALRAT_220A | 0.349 | 1.038 | 1.035 |
|  | 3BULGTS_220A | 0.504 | 1.027 | 1.022 |
|  | 3CROWLA_220A | 0.524 | 1.026 | 1.021 |
|  | 3KIAMAL_220A | 0.248 | 1.025 | 1.023 |
|  | 3MURRAW_220A | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 1.004 | 1.004 |
|  | 3WAUBRA_220A | 0.448 | 1.031 | 1.026 |
|  | HOTS 220 KV_POC | 0.05 | 1.028 | 1.027 |

#### LowLoad

|  |  | max |  |  |
| --- | --- | --- | --- | --- |
| Case Reference | Bus Name | Volt Fluc(%) | Voltage Level(pu) After | Voltage Level(pu) Prior |
| HORSF_GenChng - 118.8MW to 29.7MW (100% to 25%) | 3ARAR_T_220A | 1.274 | 1.032 | 1.02 |
|  | 3ARAR_T_220B | 1.274 | 1.032 | 1.02 |
|  | 3ARAR_T_220F | 1.274 | 1.032 | 1.02 |
|  | 3BALRAT_220A | 0.735 | 1.054 | 1.047 |
|  | 3BULGTS_220A | 1.162 | 1.027 | 1.015 |
|  | 3CROWLA_220A | 1.252 | 1.03 | 1.017 |
|  | 3KIAMAL_220A | 0.102 | 1.009 | 1.008 |
|  | 3MURRAW_220A | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 0.998 | 0.998 |
|  | 3WAUBRA_220A | 1.142 | 1.042 | 1.031 |
|  | HOTS 220 KV_POC | 0.109 | 1.022 | 1.021 |
| HORSF_GenChng - 118.8MW to 59.4MW (100% to 50%) | 3ARAR_T_220A | 0.868 | 1.028 | 1.02 |
|  | 3ARAR_T_220B | 0.868 | 1.028 | 1.02 |
|  | 3ARAR_T_220F | 0.868 | 1.028 | 1.02 |
|  | 3BALRAT_220A | 0.501 | 1.052 | 1.047 |
|  | 3BULGTS_220A | 0.792 | 1.023 | 1.015 |
|  | 3CROWLA_220A | 0.854 | 1.026 | 1.017 |
|  | 3KIAMAL_220A | 0.072 | 1.009 | 1.008 |
|  | 3MURRAW_220A | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 0.998 | 0.998 |
|  | 3WAUBRA_220A | 0.779 | 1.038 | 1.031 |
|  | HOTS 220 KV_POC | 0.071 | 1.022 | 1.021 |
| HORSF_GenChng - 118.8MW to 89.1MW (100% to 75%) | 3ARAR_T_220A | 0.441 | 1.024 | 1.02 |
|  | 3ARAR_T_220B | 0.441 | 1.024 | 1.02 |
|  | 3ARAR_T_220F | 0.441 | 1.024 | 1.02 |
|  | 3BALRAT_220A | 0.257 | 1.049 | 1.047 |
|  | 3BULGTS_220A | 0.4 | 1.019 | 1.015 |
|  | 3CROWLA_220A | 0.432 | 1.022 | 1.017 |
|  | 3KIAMAL_220A | 0.038 | 1.009 | 1.008 |
|  | 3MURRAW_220A | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 0.998 | 0.998 |
|  | 3WAUBRA_220A | 0.397 | 1.035 | 1.031 |
|  | HOTS 220 KV_POC | 0.026 | 1.022 | 1.021 |
| HORSF_GenTrip - 118.8MW to 0MW (100% to 0%) | 3ARAR_T_220A | 1.698 | 1.037 | 1.02 |
|  | 3ARAR_T_220B | 1.698 | 1.037 | 1.02 |
|  | 3ARAR_T_220F | 1.698 | 1.037 | 1.02 |
|  | 3BALRAT_220A | 0.985 | 1.057 | 1.047 |
|  | 3BULGTS_220A | 1.558 | 1.031 | 1.015 |
|  | 3CROWLA_220A | 1.672 | 1.034 | 1.017 |
|  | 3KIAMAL_220A | 0.127 | 1.009 | 1.008 |
|  | 3MURRAW_220A | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 0.998 | 0.998 |
|  | 3WAUBRA_220A | 1.52 | 1.046 | 1.031 |
|  | HOTS 220 KV_POC | 0.195 | 1.023 | 1.021 |
| HORSF_GenTrip - 29.7MW to 0MW (25% to 0%) | 3ARAR_T_220A | 0.392 | 1.034 | 1.03 |
|  | 3ARAR_T_220B | 0.392 | 1.034 | 1.03 |
|  | 3ARAR_T_220F | 0.392 | 1.034 | 1.03 |
|  | 3BALRAT_220A | 0.227 | 1.055 | 1.053 |
|  | 3BULGTS_220A | 0.359 | 1.028 | 1.024 |
|  | 3CROWLA_220A | 0.386 | 1.031 | 1.027 |
|  | 3KIAMAL_220A | 0.025 | 1.009 | 1.009 |
|  | 3MURRAW_220A | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 0.998 | 0.998 |
|  | 3WAUBRA_220A | 0.351 | 1.043 | 1.04 |
|  | HOTS 220 KV_POC | 0.044 | 1.022 | 1.022 |
| HORSF_GenTrip - 59.4MW to 0MW (50% to 0%) | 3ARAR_T_220A | 0.798 | 1.035 | 1.027 |
|  | 3ARAR_T_220B | 0.798 | 1.035 | 1.027 |
|  | 3ARAR_T_220F | 0.798 | 1.035 | 1.027 |
|  | 3BALRAT_220A | 0.46 | 1.055 | 1.051 |
|  | 3BULGTS_220A | 0.731 | 1.029 | 1.022 |
|  | 3CROWLA_220A | 0.785 | 1.032 | 1.024 |
|  | 3KIAMAL_220A | 0.055 | 1.009 | 1.008 |
|  | 3MURRAW_220A | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 0.998 | 0.998 |
|  | 3WAUBRA_220A | 0.714 | 1.044 | 1.037 |
|  | HOTS 220 KV_POC | 0.084 | 1.023 | 1.022 |
| HORSF_GenTrip - 89.1MW to 0MW (75% to 0%) | 3ARAR_T_220A | 1.227 | 1.035 | 1.023 |
|  | 3ARAR_T_220B | 1.227 | 1.035 | 1.023 |
|  | 3ARAR_T_220F | 1.227 | 1.035 | 1.023 |
|  | 3BALRAT_220A | 0.71 | 1.056 | 1.049 |
|  | 3BULGTS_220A | 1.124 | 1.03 | 1.019 |
|  | 3CROWLA_220A | 1.207 | 1.033 | 1.021 |
|  | 3KIAMAL_220A | 0.089 | 1.009 | 1.008 |
|  | 3MURRAW_220A | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 0.998 | 0.998 |
|  | 3WAUBRA_220A | 1.099 | 1.045 | 1.034 |
|  | HOTS 220 KV_POC | 0.127 | 1.023 | 1.022 |

### Appendix4

The voltage fluctuations due to loss of line contingencies on all the monitored buses as per section 6.5.

#### HighLoad

|  |  | max |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Case Reference | Bus Name | Volt Fluc(%) GenOFF | Volt Fluc(%) GenON | Voltage Level(pu) GenOFF | Voltage Level(pu) GenON |
| ARTS-CWTS (ARARAT to CROWNLANDS) 220kV line OOS | 3ARAR_T_220A | 2.548 | 3.238 | 1.051 | 1.051 |
|  | 3ARAR_T_220B | 2.548 | 3.238 | 1.051 | 1.051 |
|  | 3ARAR_T_220F | 0.0 | 0.0 | 1.026 | 1.018 |
|  | 3BALRAT_220A | 1.16 | 1.582 | 1.049 | 1.049 |
|  | 3BULGTS_220A | 1.034 | 1.81 | 1.036 | 1.038 |
|  | 3CROWLA_220A | 1.119 | 1.949 | 1.037 | 1.038 |
|  | 3KIAMAL_220A | 0.257 | -0.063 | 1.027 | 1.021 |
|  | 3MURRAW_220A | 0.0 | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 0.0 | 1.004 | 1.004 |
|  | 3WAUBRA_220A | 1.988 | 2.612 | 1.051 | 1.05 |
|  | HOTS 220 KV_POC | 0.383 | 0.522 | 1.032 | 1.033 |
| ARTS-WBTS-BATS (ARARAT to WAUBRA to BALLARAT) 220kV line OOS | 3ARAR_T_220A | 1.217 | 2.082 | 1.038 | 1.039 |
|  | 3ARAR_T_220B | 0.0 | 0.0 | 1.026 | 1.018 |
|  | 3ARAR_T_220F | 1.217 | 2.082 | 1.038 | 1.039 |
|  | 3BALRAT_220A | 0.999 | 1.425 | 1.048 | 1.047 |
|  | 3BULGTS_220A | 1.141 | 1.912 | 1.038 | 1.039 |
|  | 3CROWLA_220A | 1.246 | 2.071 | 1.038 | 1.039 |
|  | 3KIAMAL_220A | 0.263 | -0.053 | 1.027 | 1.021 |
|  | 3MURRAW_220A | 0.0 | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 0.0 | 1.004 | 1.004 |
|  | 3WAUBRA_220A | 0.0 | 0.0 | 1.031 | 1.024 |
|  | HOTS 220 KV_POC | 0.404 | 0.538 | 1.032 | 1.033 |
| CWTS-BGTS-HOTS (CROWNLANDS to BULGANA to HORSHAM) 220kV line OOS | 3ARAR_T_220A | 1.238 | 1.949 | 1.038 | 1.038 |
|  | 3ARAR_T_220B | 1.238 | 1.949 | 1.038 | 1.038 |
|  | 3ARAR_T_220F | 1.238 | 1.949 | 1.038 | 1.038 |
|  | 3BALRAT_220A | 0.761 | 1.188 | 1.045 | 1.045 |
|  | 3BULGTS_220A | 0.0 | 0.0 | 1.026 | 1.02 |
|  | 3CROWLA_220A | 1.167 | 1.84 | 1.037 | 1.037 |
|  | 3KIAMAL_220A | 0.255 | -0.068 | 1.027 | 1.021 |
|  | 3MURRAW_220A | 0.0 | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 0.0 | 1.004 | 1.004 |
|  | 3WAUBRA_220A | 1.147 | 1.783 | 1.042 | 1.042 |
|  | HOTS 220 KV_POC | 0.156 | 0.324 | 1.029 | 1.031 |
| HOTS-MRTS-KMTS (HORSHAM to MURRAWARRA to KIAMAL) 220kV line OOS | 3ARAR_T_220A | 0.968 | 1.661 | 1.036 | 1.035 |
|  | 3ARAR_T_220B | 0.968 | 1.661 | 1.036 | 1.035 |
|  | 3ARAR_T_220F | 0.968 | 1.661 | 1.036 | 1.035 |
|  | 3BALRAT_220A | 0.684 | 1.052 | 1.045 | 1.044 |
|  | 3BULGTS_220A | 0.7 | 1.451 | 1.033 | 1.034 |
|  | 3CROWLA_220A | 0.866 | 1.571 | 1.034 | 1.034 |
|  | 3KIAMAL_220A | -0.257 | -0.019 | 1.022 | 1.022 |
|  | 3MURRAW_220A | 0.0 | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 0.0 | 1.004 | 1.004 |
|  | 3WAUBRA_220A | 0.992 | 1.512 | 1.041 | 1.039 |
|  | HOTS 220 KV_POC | -0.5 | -0.066 | 1.023 | 1.027 |
| HOTS220 - HOTS66 kV Tx OOS | 3ARAR_T_220A | -0.02 | -0.056 | 1.026 | 1.018 |
|  | 3ARAR_T_220B | -0.02 | -0.056 | 1.026 | 1.018 |
|  | 3ARAR_T_220F | -0.02 | -0.056 | 1.026 | 1.018 |
|  | 3BALRAT_220A | -0.005 | -0.022 | 1.038 | 1.033 |
|  | 3BULGTS_220A | -0.028 | -0.057 | 1.026 | 1.019 |
|  | 3CROWLA_220A | -0.022 | -0.055 | 1.025 | 1.018 |
|  | 3KIAMAL_220A | -0.009 | -0.012 | 1.024 | 1.022 |
|  | 3MURRAW_220A | 0.0 | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 0.0 | 1.004 | 1.004 |
|  | 3WAUBRA_220A | 0.0 | -0.046 | 1.031 | 1.023 |
|  | HOTS 220 KV_POC | -0.032 | -0.039 | 1.027 | 1.027 |
| KMTS-RCTS (KIAMAL to REDCLIFF) 220kV line OOS | 3ARAR_T_220A | 0.293 | 0.15 | 1.029 | 1.02 |
|  | 3ARAR_T_220B | 0.293 | 0.15 | 1.029 | 1.02 |
|  | 3ARAR_T_220F | 0.293 | 0.15 | 1.029 | 1.02 |
|  | 3BALRAT_220A | 0.098 | 0.041 | 1.039 | 1.033 |
|  | 3BULGTS_220A | 0.308 | 0.146 | 1.029 | 1.021 |
|  | 3CROWLA_220A | 0.296 | 0.147 | 1.028 | 1.02 |
|  | 3KIAMAL_220A | 5.047 | 5.595 | 1.075 | 1.078 |
|  | 3MURRAW_220A | 0.0 | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 0.0 | 1.004 | 1.004 |
|  | 3WAUBRA_220A | 0.161 | 0.121 | 1.032 | 1.025 |
|  | HOTS 220 KV_POC | 0.131 | 0.048 | 1.029 | 1.028 |
| Network Normal | 3ARAR_T_220A | 0.0 | -0.001 | 1.026 | 1.018 |
|  | 3ARAR_T_220B | 0.0 | -0.001 | 1.026 | 1.018 |
|  | 3ARAR_T_220F | 0.0 | -0.001 | 1.026 | 1.018 |
|  | 3BALRAT_220A | 0.0 | -0.0 | 1.038 | 1.033 |
|  | 3BULGTS_220A | 0.0 | -0.001 | 1.026 | 1.02 |
|  | 3CROWLA_220A | 0.0 | -0.001 | 1.025 | 1.018 |
|  | 3KIAMAL_220A | 0.0 | 0.0 | 1.024 | 1.022 |
|  | 3MURRAW_220A | 0.0 | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 0.0 | 1.004 | 1.004 |
|  | 3WAUBRA_220A | 0.0 | -0.0 | 1.031 | 1.024 |
|  | HOTS 220 KV_POC | 0.0 | -0.001 | 1.028 | 1.028 |

#### LowLoad

|  |  | max |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Case Reference | Bus Name | Volt Fluc(%) GenOFF | Volt Fluc(%) GenON | Voltage Level(pu) GenOFF | Voltage Level(pu) GenON |
| ARTS-CWTS (ARARAT to CROWNLANDS) 220kV line OOS | 3ARAR_T_220A | 2.422 | 3.417 | 1.057 | 1.054 |
|  | 3ARAR_T_220B | 2.422 | 3.417 | 1.057 | 1.054 |
|  | 3ARAR_T_220F | 0.0 | 0.0 | 1.033 | 1.02 |
|  | 3BALRAT_220A | 1.106 | 1.512 | 1.065 | 1.062 |
|  | 3BULGTS_220A | -1.218 | 0.242 | 1.015 | 1.018 |
|  | 3CROWLA_220A | -1.505 | 0.088 | 1.015 | 1.018 |
|  | 3KIAMAL_220A | -1.755 | -2.889 | 0.991 | 0.979 |
|  | 3MURRAW_220A | -3.0 | -3.0 | 1.01 | 1.01 |
|  | 3REDCLF_220A | 0.0 | 0.0 | 0.998 | 0.998 |
|  | 3WAUBRA_220A | 1.883 | 2.761 | 1.061 | 1.058 |
|  | HOTS 220 KV_POC | -1.198 | -0.816 | 1.01 | 1.013 |
| ARTS-WBTS-BATS (ARARAT to WAUBRA to BALLARAT) 220kV line OOS | 3ARAR_T_220A | -1.644 | -0.016 | 1.016 | 1.019 |
|  | 3ARAR_T_220B | 0.0 | 0.0 | 1.033 | 1.02 |
|  | 3ARAR_T_220F | -1.644 | -0.016 | 1.016 | 1.019 |
|  | 3BALRAT_220A | 1.377 | 1.789 | 1.068 | 1.065 |
|  | 3BULGTS_220A | -1.113 | 0.343 | 1.016 | 1.019 |
|  | 3CROWLA_220A | -1.38 | 0.21 | 1.016 | 1.019 |
|  | 3KIAMAL_220A | -1.751 | -2.884 | 0.991 | 0.979 |
|  | 3MURRAW_220A | -3.0 | -3.0 | 1.01 | 1.01 |
|  | 3REDCLF_220A | 0.0 | 0.0 | 0.998 | 0.998 |
|  | 3WAUBRA_220A | 0.0 | 0.0 | 1.043 | 1.031 |
|  | HOTS 220 KV_POC | -1.177 | -0.798 | 1.01 | 1.013 |
| CWTS-BGTS-HOTS (CROWNLANDS to BULGANA to HORSHAM) 220kV line OOS | 3ARAR_T_220A | 1.925 | 2.915 | 1.052 | 1.049 |
|  | 3ARAR_T_220B | 1.925 | 2.915 | 1.052 | 1.049 |
|  | 3ARAR_T_220F | 1.925 | 2.915 | 1.052 | 1.049 |
|  | 3BALRAT_220A | 0.967 | 1.37 | 1.064 | 1.061 |
|  | 3BULGTS_220A | 0.0 | 0.0 | 1.027 | 1.015 |
|  | 3CROWLA_220A | 2.148 | 3.099 | 1.052 | 1.048 |
|  | 3KIAMAL_220A | -1.757 | -2.893 | 0.991 | 0.979 |
|  | 3MURRAW_220A | -3.0 | -3.0 | 1.01 | 1.01 |
|  | 3REDCLF_220A | 0.0 | 0.0 | 0.998 | 0.998 |
|  | 3WAUBRA_220A | 1.575 | 2.449 | 1.058 | 1.055 |
|  | HOTS 220 KV_POC | -1.42 | -1.01 | 1.008 | 1.011 |
| HOTS-MRTS-KMTS (HORSHAM to MURRAWARRA to KIAMAL) 220kV line OOS | 3ARAR_T_220A | 1.496 | 3.444 | 1.048 | 1.054 |
|  | 3ARAR_T_220B | 1.496 | 3.444 | 1.048 | 1.054 |
|  | 3ARAR_T_220F | 1.496 | 3.444 | 1.048 | 1.054 |
|  | 3BALRAT_220A | 1.635 | 2.52 | 1.071 | 1.072 |
|  | 3BULGTS_220A | 1.631 | 3.654 | 1.043 | 1.052 |
|  | 3CROWLA_220A | 1.587 | 3.581 | 1.046 | 1.053 |
|  | 3KIAMAL_220A | -2.346 | -2.186 | 0.985 | 0.986 |
|  | 3MURRAW_220A | 0.0 | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 0.0 | 0.998 | 0.998 |
|  | 3WAUBRA_220A | 1.728 | 3.263 | 1.06 | 1.063 |
|  | HOTS 220 KV_POC | 0.003 | 1.402 | 1.022 | 1.035 |
| HOTS220 - HOTS66 kV Tx OOS | 3ARAR_T_220A | -0.025 | -0.053 | 1.033 | 1.019 |
|  | 3ARAR_T_220B | -0.025 | -0.053 | 1.033 | 1.019 |
|  | 3ARAR_T_220F | -0.025 | -0.053 | 1.033 | 1.019 |
|  | 3BALRAT_220A | -0.01 | -0.018 | 1.054 | 1.047 |
|  | 3BULGTS_220A | -0.024 | -0.055 | 1.027 | 1.015 |
|  | 3CROWLA_220A | -0.025 | -0.054 | 1.03 | 1.017 |
|  | 3KIAMAL_220A | -0.001 | -0.003 | 1.009 | 1.008 |
|  | 3MURRAW_220A | 0.0 | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 0.0 | 0.998 | 0.998 |
|  | 3WAUBRA_220A | -0.021 | -0.039 | 1.042 | 1.03 |
|  | HOTS 220 KV_POC | -0.002 | -0.034 | 1.022 | 1.021 |
| KMTS-RCTS (KIAMAL to REDCLIFF) 220kV line OOS | 3ARAR_T_220A | 0.718 | 1.286 | 1.04 | 1.032 |
|  | 3ARAR_T_220B | 0.718 | 1.286 | 1.04 | 1.032 |
|  | 3ARAR_T_220F | 0.718 | 1.286 | 1.04 | 1.032 |
|  | 3BALRAT_220A | 0.784 | 1.085 | 1.062 | 1.058 |
|  | 3BULGTS_220A | 0.538 | 0.97 | 1.032 | 1.025 |
|  | 3CROWLA_220A | 0.678 | 1.198 | 1.037 | 1.029 |
|  | 3KIAMAL_220A | -1.673 | -1.425 | 0.992 | 0.994 |
|  | 3MURRAW_220A | -3.0 | -3.0 | 1.01 | 1.01 |
|  | 3REDCLF_220A | 0.0 | 0.0 | 0.998 | 0.998 |
|  | 3WAUBRA_220A | 0.696 | 1.382 | 1.05 | 1.044 |
|  | HOTS 220 KV_POC | -0.96 | -0.842 | 1.012 | 1.013 |
| Network Normal | 3ARAR_T_220A | 0.0 | -0.017 | 1.033 | 1.019 |
|  | 3ARAR_T_220B | 0.0 | -0.017 | 1.033 | 1.019 |
|  | 3ARAR_T_220F | 0.0 | -0.017 | 1.033 | 1.019 |
|  | 3BALRAT_220A | 0.0 | -0.005 | 1.054 | 1.047 |
|  | 3BULGTS_220A | 0.0 | -0.021 | 1.027 | 1.015 |
|  | 3CROWLA_220A | 0.0 | -0.018 | 1.03 | 1.017 |
|  | 3KIAMAL_220A | 0.0 | -0.0 | 1.009 | 1.008 |
|  | 3MURRAW_220A | 0.0 | 0.0 | 1.04 | 1.04 |
|  | 3REDCLF_220A | 0.0 | 0.0 | 0.998 | 0.998 |
|  | 3WAUBRA_220A | 0.0 | -0.011 | 1.043 | 1.03 |
|  | HOTS 220 KV_POC | 0.0 | -0.028 | 1.022 | 1.021 |

### Appendix 5

#### HORSF high load gen on

#### HORSF high load gen off

#### HORSF low load gen on

#### HORSF low load gen off

### Appendix 6

118.8 MW at the PoC, this needs to be adjusted where generation change is required.

Max Qmax and Qmin at the PoC is ±46.926 MVAr and this is taken into consideration when simulating the load flow as per the HORSF voltage droop characteristics.

Voltage droop control mode is implemented using PSS®E python API.